## Slide 1: ERCOT Frequency Events March 2026 ERCOT Operations Planning PDCWG Meeting Apr 15, 2026

## Slide 2: 3/11/2026 8:20:47 (Non-FME)
Notes: The unit tripped for ~612 MW while experiencing a run back
Starting Frequency: 59.982 Hz
Minimum Frequency: 59.950 Hz
A-C Time : 3 seconds
Recovery Time(back to deadband): 2 minutes 58 seconds
ECRS Released: 0 MW
Trip Reason: Unknown at this time
Contextual Information: A total of 318 MW of regulation Up and a manual offset of 350 MW was deployed during the event.
Reason for no selection: C point is 59.950

## Slide 3: Questions/Comments?