## Slide 1: ERCOT Frequency Control Report March 2026 PDCWG | April 15th , 2026 ERCOT Operations Planning April 14, 2026
Outline:
Frequency Control
  CPS1, BAAL, RMS1
Frequency Profile
Time Error
BAAL-003 Performance
ERCOT Energy Statistics
ERCOT System Inertia

## Slide 2: Summary of March 2026
CPS1: 185.31%
Current CPS1 12-Month Rolling Average: 179.26%
0 BAAL Exceedance(s)
0 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2024
2024 BAAL-003 FRM Performance: -1127.76
2026 RMS1 Statistics
  Mean: 11.46 mHz
  Min: 09.47 mHz
  Max 14.75 mHz
Energy Statistics
  Total Energy: 37,911,606 MWh
  Wind Energy: 13,331,081 MWh
  Percent Energy from Wind: 35.16%
  Solar Energy: 6,729,093 MWh
  Percent Energy from Solar: 17.75%
Minimum System Inertia
  Mean: 157,243 MW*s
  Max: 211,645 MW*s on March 8th
  Min: 114,642 MW*s on March 14th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Mar-26 CPS1 (%): 185.31
Notes: CPS1 Score is 185.31%
Scores Below 100%: No instances of CPS1 Score under 100%

## Slide 5: BAAL Exceedances & Violations
There were 0 BAAL exceedance(s) in March.

## Slide 6: 15-Minute Average CPS1%
Mar-26 CPS1 (%): 185.31
Notes: CPS1 score is above 170% for all 15-minute intervals.

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average 179.26%
Notes: 12 month rolling average CPS1 score is 179.26 which is continuing the increasing trend of CPS1 scores.

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Daily RMS1 frequency by year.
2026 RMS1 Statistics
  Mean: 11.46 mHz
  Min: 09.47 mHz
  Max 14.75 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month
Notes: A More granular look at last 15 years of RMS1 by month
11.46 mHz on avg for March 2026

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Same data with 10 years shown instead of 15

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison
Notes: Comparison of frequency profile between March 2025 and 2026. Compared to last year, there are slightly less instances of frequency hovering around the dead bands.

## Slide 13: Frequency Profile Comparison
Notes: Comparison of frequency profile between March 2024 and 2026. Like the previous slide, there are less instances of frequency hovering around the dead bands.

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error
Notes: We see low time error accumulation throughout the month of March.

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2024 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2024 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO = -471.0, FRM median = -913.56, FRM average = -992.
OP2022: FRO = -412.0, FRM median = -1060.40, FRM average = -1153.4
OP2023: FRO = -463.0, FRM median = -1130.21, FRM average = -1302.7
OP2024: FRO = -395.0, FRM median = -1127.76, FRM average = -1264.3
OP2025: FRO = -455.0,

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 37,911,606 MWh

## Slide 22: Total Energy from Wind Generation
Notes:   13,331,081 MWH

## Slide 23: % Energy from Wind Generation
Notes: 35.16% of total energy was provided by wind generation

## Slide 24: Total Energy From Solar Generation
Notes: 6,729,093 MWh

## Slide 25: % Energy from Solar Generation
Notes: 17.75% of total energy was provided by solar generation

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia in March 2026 = 114,642 MW*s on March 14th
Historical Overall Minimum was 109,029 MW*s on 3/22/2021
March Data:
Mean: 157,243 MW*s
Max: 211,645 MW*s on March 8th
Min: 114,642 MW*s on March 14th

## Slide 28: Total Inertia 2016-2026
Date and Time | 2016 4/10 2:00 AM | 2017 10/27 4:00 AM | 2018 11/03 3:30 AM | 2019 3/27 1:00 AM | 2020 05/01 2:00 AM | 2021 03/22 1:00 AM | 2022 03/21 2:00 AM | 2023 04/18 3:00 AM | 2024 03/29 4:00 AM | 2025 03/18 12:00 PM | 2026* 03/14 12:00 PM
Min synch. Inertia (GW*s) | 143 | 130 | 128.8 | 134.5 | 131.1 | 116.6 | 115.0 | 124.3 | 129.9 | 118.3 | 114.7
System load at minimum synch. Inertia (MW) | 27,831 | 28,425 | 28,397 | 29,883 | 30,679 | 31,767 | 33,784 | 35,578 | 37,039 | 49,130 | 48,013
Non-synch. Gen. in % of System Load | 47 | 54 | 53 | 50 | 57 | 66 | 65 | 61 | 68 | 74 | 81
FFR Award | N/A | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 134 | 298 | 430
Critical Inertia (GW*s) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 93 | 92 | 87
Red circles denote inertia at max IRR penetration (= IRR Gen/Total Gen)

## Slide 29: Questions/Comments?