## Slide 1: ERCOT Batch Study Process for Large Load Interconnections in support of NPRR1325 Discussion
April 15, 2026
Protocol Revision Subcommittee
1

## Slide 2: Agenda
Large Load Interconnection 101
What is a Batch process
What is the transitional Batch Zero process
Current Key Issues
CLR and BYOG
Path to June Board

## Slide 3: NERC and ERCOT Requirements Relevant to Large Load Interconnection
Role in LLI
Purpose
Facility interconnection studies
Establishes requirements for the Transmission Planner and Planning Coordinator to study the impact of interconnecting a new facility to the bulk electric system
Requires the applicable entities to perform steady-state, stability, and short-circuit studies to confirm the interconnection does not degrade system reliability. The load developer must supply accurate load models and parameters
NERC FAC-002
Transmission planning performance requirements
Defines steady-state performance requirements for the transmission system under a range of contingency categories (P0-P7), from no contingency to extreme events
Sets forth the transmission reliability criteria for the bulk electric system
NERC TPL-001
Transmission planning criteria
Defines ERCOT’s regional transmission planning criteria, performance requirements, and study methodology- including how new large loads must be modeled and assessed within the ERCOT grid
Sets forth ERCOT’s reliability criteria that is additive to the NERC criteria, and requires network upgrades when deficiencies are identified
ERCOT Planning Guide §4
Large load interconnection process
Establishes the procedural and technical framework specifically for interconnecting large loads (≥ 75 MW) to the ERCOT transmission system, from application through commercial operation
The primary ERCOT procedural roadmap for large loads. Covers the Large Load Interconnection Requests (LLIR) process, required study agreements, deposit milestones, phased study process, and commercial terms for cost responsibility of network upgrades
ERCOT Planning Guide §9
Key takeaway: NERC Reliability Standards and ERCOT Planning Guide requirements govern the reliability assessment of new Large Loads

## Slide 4: Evolution of Large Load Interconnection in ERCOT: from ad hoc to batch-based planning
.
2022–2025: Interim ERCOT-led
2025: PGRR115 – Unified but sequential
2026: PGRR145 – Batch Zero (transition)
Pre-2022: Decentralized, TDSP-led
Future: Ongoing batch process (TBD)
  Large loads worked directly with TDSPs; no ERCOT-wide coordination
  Limited need for system-level assessment
  ERCOT introduced interim interconnection process1
  Focused on near-term loads (~2 years)
  Longer-term impacts handled through transmission planning (RTP/RPG)
  Single interconnection study process (LLIS) for all large loads
  Applied regardless of energization timeline
  One-time, system-wide batch study to address backlog
  Aligns interconnection with coordinated transmission planning
  Target: June Board endorsement, Summer 2026 start
  Regular batch studies with defined entry criteria
  Fully integrated with transmission planning (RTP/RPG)
  Growing demand created risk that system-wide reliability impacts were not fully evaluated
  Multiple pathways and fragmented studies led to no single view of system impact
  High volume of requests drove frequent restudies and increasing uncertainty
  Objective of stabilizing the pipeline and enabling transition to a scalable process
  Scalable, predictable, system-wide planning framework
1. March 2022 Market Notice

## Slide 5: Large Load Interconnection requests: historical data
Number of large load requests and requested load amount by quarter, MW and #
Key Takeaways
Explosive growth in large load requests: after relatively low and stable activity through 2023–early 2024, requests surged sharply starting in late 2024 and accelerated further in 2025–2026
2026 sets a new peak: latest quarter (~200 requests) represents an order-of-magnitude increase vs. historical levels, signaling unprecedented pressure on the system
Note: Large Loads are defined as ≥75 MW in ERCOT

## Slide 6: Large Load Interconnection requests: projected demand
Chart: 
 | 5778 | 5778 | 5778 | 5778 | 5778 | 5778
 | 935 | 2748 | 2941 | 2941 | 3241 | 3241
 | 30 | 3181 | 10739 | 15923 | 19040 | 21343
 | 0 | 6478 | 30539 | 51315 | 61966 | 86605
 | 0 | 25253 | 101702 | 177879 | 238188 | 293651
2025
2026
2027
2028
2029
2030
6,743
43,438
151,699
253,836
328,213
410,618
No Studies Submitted
Under ERCOT Review
Planning Studies Approved
A2E but not operational
Observed Energized
Project Status
No Studies Submitted
Under ERCOT Review
Planning Studies Approved
A2E but not operational
Observed Energized
Total (MW)
0
0
30
935
5,778
6,743
25,253
6,478
3,181
2,748
5,778
43,438
101,702
30,539
10,739
2,941
5,778
151,699
177,879
51,315
15,923
2,941
5,778
253,836
238,188
61,966
19,040
3,241
5,778
328,213
293,651
86,605
21,343
3,241
5,778
410,618
Data Center
Other
Crypto
Industrials
Data Center/Crypto
Hydrogen
Load by year and project status, MW
Key Takeaways
Massive pipeline of demand (~410 GW by 2030): ERCOT is facing unprecedented load growth, with demand increasing ~6x 2025 to 2030
Pipeline is largely immature: ~70% of projected load has no studies submitted, indicating high uncertainty and speculative demand
Data centers dominate demand the surge is driven by hyperscale data centers, with other segments remaining marginal
2030 load by segment, %
Note: as of March 26, 2026
Chart: 
 | 87.6 | 6.3 | 3.8 | 1.3 | 0.6 | 0.3
1%
1%
0%

## Slide 7: Transition to a batch process is enabled by structured stakeholder engagement and governance
Broad-based stakeholder input for initial design
Iterative refinement through stakeholder workshops
Formal ERCOT governance and approval
Extensive stakeholder outreach (interviews, workshops, surveys, public comments) to identify key issues in the current process and inform the initial design of Batch Zero PGRR145
Vetting and refinement of initial proposal through stakeholder workshops, testing key elements and incorporating stakeholder feedback to ensure a robust and implementable design
Progression through ERCOT governance (PRS, ROS, TAC, Board) and PUCT review, ensuring alignment, technical validation, and approval for implementation

## Slide 8: PUCT rulemakings under SB6 are reshaping how large loads are planned, interconnected, and paid for
Source: PUCT Project Nos. 58479, 58480, 58481, 58484; SB6 Implementation Docket (Project No. 58317)
SB6 establishes the overarching policy framework to ensure large load growth is integrated reliably, cost-responsibly, and transparently – under which these rulemakings define the mechanisms for forecasting, interconnection, and cost allocation
Description
Why it matters for LLIS..
No. 58480 – Large Load Forecasting Criteria
Establishes standardized requirements for how large load forecasts are developed and incorporated into ERCOT planning processes
Determines which loads are considered “real” vs. speculative in studies
Directly impacts planning assumptions and transmission sizing
Reduces risk of over-forecasting (stranded or misallocated infrastructure)
No. 58481 – Large Load Interconnection Standards
Defines requirements for interconnecting large loads, including financial commitments, study requirements, and reliability criteria
No. 58479 – Co-location / Net Metering
Rulemaking governing arrangements where large loads are co-located with existing generation resources
No. 58484 – Transmission Cost Recovery
Evaluates how transmission costs (including those driven by large loads) are recovered and allocated across customers
Sets entry criteria for studies
Introduces financial commitment as a filter
Drives standardization of the interconnection process, addressing inconsistency across TDSPs
Core enabler of batch process design and eligibility
Protects system from impact of loss of existing generation due to a new net metering arrangement
Requires ERCOT study after load interconnection studies
ERCOT may recommend and the PUCT may adopt certain operating conditions
Determines who pays for transmission upgrades
Critical to avoiding cost socialization to only residential and commercial ratepayers
Relevant PUCT Projects
Rulemaking stage
Rule effective
Public comment period
Rule effective
Project initiation
Detailed next

## Slide 9: Related PUCT Activities
Source: PUCT Project No. 58480 (final rule) and Project No. 58481 – Proposal for Publication of 16 TAC §25.194 (filed March 12, 2026)
  After 2026, only Large Loads that have executed an interconnection agreement that satisfies the requirements in PUC Project 58481 will be included in the Large Load forecast. These requirements will be reflected in future revision requests.
  Establishes alternative gating criteria for Large Loads to be included in the 2026 Large Load Forecast, which is used in planning assessments until new cases are constructed in 2027 using new rule criteria.
PUC Project 58481, proposed to be 16 TAC § 25.194, Large Load Interconnection Standards (Proposal for Publication published on March 12, 2026)
  Intermediate Agreement Requirements:
    Site control (updated)
    Financial Security ($50,000/MW in current PFP; subject to final rule)
    Disclosures
    Option to pay for significant equipment or services
  Interconnection Agreement Requirements:
    Site control (updated)
    Financial security
    Interconnection fee ($50,000/MW, non-refundable)
    CIAC
    Reallocation
    Withdrawal Consequences
    Refund Eligibility and Timing
  After the PUCT adopts a final rule, ERCOT will file a revision request to align Section 9.7 with the requirements in the final rule.
PUC Project 58480, 16 TAC § 25.370, Large Load Forecasting Rule (Adopted & Effective March 1, 2026)

## Slide 10: Incorporating PUC Project 58481 into Batch Zero: Two Implementation Pathways
2026
2027
Q2
Q3
Q4
Q1
Case building
  Batch Zero Study
  Illustrative publication date of Project No. 58481
Deferred launch of Batch Zero
No need for re-alignment if adopted 58481 rule is different from published draft
Case building
Batch Zero Study
Potential re-alignment needed if adopted 58481 rule is different from published draft
Early launch of Batch Zero
Project 58481 will define readiness and financial commitment standards for Large Loads. ERCOT must determine how to align Batch Zero timing with this rulemaking
Context
  Description: embed the PUCT proposal for publication (Project No. 58481) concepts directly into the PGRR language and update the PGRR with the published PFP once available
  Implications
  Enables earlier Batch Zero launch
  Uses proposed draft for intermediate agreement and interconnection agreement criteria
  Risk of misalignment if final rule differs from draft
  Description: draft PGRR to reference the final adopted 16 TAC §25.194 and begin Batch Zero a defined period (e.g., X days) after the rule becomes effective
  Implications
  Batch Zero will be aligned with final PUC rule
  May delay Batch Zero start depending on rule adoption timeline
Illustrative timeline
Option 1: Replicate the Draft 58481 PFP in the PGRR (proceed in parallel)
Option 2: Tie PGRR to Final Adopted 58481 Rule (sequential alignment)
Option
Description and implications
Current PGRR145 option

## Slide 11: Agenda
Large Load Interconnection 101
What is a Batch process
What is the transitional Batch Zero process
Current Key Issues
CLR and BYOG
Path to June Board

## Slide 12: The batch study process increases outcome certainty and transparency while limiting restudy risk
.
ERCOT action
Non-ERCOT action
Communication point
From the existing single study process…
…to the new batch study process
RPG, QSA
Energization
Batch study: ERCOT compiles applications, studies together as a batch, and allocates load
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
C
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
Single study
Single study (invalidating prior results)
Initial approval
Single study (invalidating prior results)
Initial approval
RPG, QSA
Energization
B
Single study (invalidating prior results)
Single study (invalidating prior results)
Initial approval
Initial approval
Initial approval
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
A
A
A
A
A
C
Frequent restudies required If another project impacts the same transmission zone, all previous studies are invalidated and impacted projects which haven’t yet energized must be restudied
Batching process Every ~6 months, all submitted requests are clustered and studied together; allocated capacity coming out of the study is “reserved” to prevent restudies
B
Restudy loop In the absence of capacity reservation, projects can be repeatedly pulled into restudies as new requests enter the system, delaying approvals and potentially extending timelines by years
Transparent communications Along with the new batch study process, ERCOT is redesigning the study communication process to have clearly defined touchpoints and transparent information handovers

## Slide 13: A Batch Study delivers three key outputs to enable investment certainty and system reliability
Batch Study
Annual MW allocation per request
Clear, year-by-year MW allocation (2028–2033) for each project based on system reliability constraints, formalized through the Load Commissioning Plan (LCP)
Financial commitment requirements
Transparency on financial obligations, including interconnection costs, upgrade-related costs, and required financial commitments (e.g., CIAC, security)
Actionable transmission plan
Identification of system constraints and the transmission upgrades required to serve additional load, translating study results into a coordinated, buildable plan
How SB6 objectives are enabled
System reliability: Actionable transmission plan aligns load growth with system capability and enables timely development of required upgrades to protect the grid
Economic development: MW allocation and cost visibility provide the certainty developers need to proceed with investments

## Slide 14: Agenda
Large Load Interconnection 101
What is a Batch process
What is the transitional Batch Zero process
Current Key Issues
CLR and BYOG
Path to June Board

## Slide 15: Batch Zero is a bridge between existing and new processes
PGRR115
PGRR145/ Batch Zero
PGRR(TBD) Batch Study Process
Batch Zero bridges the current and future processes by reassessing existing requests under a consistent, system-wide view and studying them together
It introduces coordinated studies, clear eligibility criteria, and produces phased load allocations/an actionable transmission plan
It ensures projects can continue progressing while establishing the foundation for the future batch process and avoiding a transition “grey zone”
Under PGRR115, projects are studied one-by-one, with each new request potentially triggering restudies and changing assumptions
This fragmented approach limits coordination and creates backlog, delays, and uncertainty on available capacity
The future process studies projects in batches, enabling a system-wide view with consistent assumptions and direct linkage to transmission planning
This creates a more scalable, transparent, and predictable interconnection framework
Today
Transition
Future

## Slide 16: Two-step revision plan: enable Batch Zero now and establish the enduring batch framework
Enable a Batch Zero 2026 launch
2026
Q1
Q2
Q3
Q4
Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
Jun Board
Dec Board
1
2
Establish an ongoing batch process
Target Jun Board
To be published (TBD)
BYOG for Batch Zero
Published 3/4
Target Jun Board
PGRR145/NPRR1325 (Batch Zero framework)
Target Jun Board
To be published 4/8 (TBD)
CLR for Batch Zero
Target Dec Board
Publishing date TBD
PGRR/NPRR (Batch Study framework)
Target Dec Board
Publishing date TBD
CLR enhancement Revision Requests
BYOG enhancement Revision Requests
Target Dec Board
Publishing date TBD

## Slide 17: PGRR145 defines Batch Zero as a structured process from screening to actionable transmission plan
Inclusion criteria Which LL projects are included in Batch Zero
Batch Zero Study System-wide assessment
Commitment Gate Which LL projects stay in
Refinement Study Right-sizing the plan
Transmission Plan to RPG Actionable output
Eligibility rules to determine which projects are included in Batch Zero and how they are treated
Single ERCOT-led, system-wide study to assess reliability and allocate load
Formal commitment gate to convert allocated load into firm, financeable demand
Refinement step to update the plan based only on committed projects
Translation of study results into a single actionable transmission plan
Batch Zero PGRR145 Building Blocks
1. Load Commissioning Plan | 2. Per NPRR1325
Detailed next
  Formal classification of projects (base load, studied, excluded)
  Eligibility thresholds and milestones (agreements, readiness)
  Validation and ordering of existing studies
  Single system-wide interconnection study
  Allocation of load by year via LCPs1
  Identification of initial transmission upgrade set and financial commitment requirement for each LL project
  Execution of interconnection agreements and financial commitments
  Acceptance of ERCOT-defined MW allocation and timeline (LCP)
  Automatic removal of non-committed projects
  Re-study limited to committed projects only
  Determination of which upgrades are still required, modified, or removed
  Updated cost estimates and evaluation of alternatives
  No reassessment of financial commitment
  Bundled transmission plan submission to RPG2
  Inclusion of cost estimates, need justification, and alternatives
  Direct path from study results to implementation

## Slide 18: Batch Zero duration reflects the need to assess reliability across scenarios and develop transmission solutions
Chart: 
 | 100 | 100 | 450 | 600 | 600 | 1000
Year 1
Year 2
Year 3
Year 4
Year 5
Year 6
MW allocation
Determine year-by-year deliverable MW (2028–2032) based on system capability
1
MW allocation
~
~
500MW
500MW
500MW
500MW
Original 750MW line
Constraint identified (1,000MW >750MW)
Assess reliability under multiple system conditions1 (summer peak, low renewable/no-solar, maintenance outages) and contingencies2 (N-1, G-1+N-1, X-1+N-1, N-1-1)
2
Reliability testing
~
~
500MW
500MW
500MW
500MW
New 750MW line
Constraint resolved (500MW>750MW)
Original 750MW line
Identify and iterate on transmission solutions with TSPs to resolve limiting conditions
3
Upgrade identification
Description
Illustrative example
Batch Study activity
Multi-year analysis required: year-by-year allocation requires sequential simulations across planning horizon
Extensive reliability testing: multiple system conditions and contingency scenarios expand study scope
Iterative deliverability assessment: MW allocation must be tested and adjusted based on system limits under each condition
Transmission solutions are not predefined: upgrades must be identified, validated, and refined with TSPs
Drivers of Batch study timeline
Unconstrained transmission line
Constrained transmission line
1. System conditions represent different operating environments used in planning studies (e.g., peak demand, low renewable output such as no-solar conditions, and planned maintenance outages) to reflect how the system performs under varying real-world scenarios | 2. Contingencies represent unexpected failures of system elements and test reliability under stress (e.g., N-1: single element outage; G-1+N-1: generator outage combined with another contingency; X-1+N-1: extreme event followed by a contingency; N-1-1: sequential outages)
~
Generator
Load

## Slide 19: Batch Zero categorizes loads based on readiness, defining MW certainty and timing
Chart: 
 | 1000 | 1000
Chart: 
 | 1000 | 0
Request
Allocation
Chart: 
 | 1000 | 500
TBD
Batch Zero cluster
Illustrative allocation, MW
Eligibility criteria
Description
Base Load
  Achieved initial energization or demonstrated near-term readiness
  Complete and valid interconnection studies
  Executed interconnection agreement
  Demonstrated site readiness and equipment procurement
Included as base load with MW effectively locked in, not subject to further study or reallocation
Studied Load
  Does not meet base load criteria
  Has executed an intermediate agreement
  Meets data submission and study requirements by deadlines
Included in Batch Zero, with MW allocation determined through system-wide study based on system capability and reliability constraints
Excluded Load
  Does not meet base load or study eligibility criteria
  Fails to provide required information by deadlines
  Next allocation opportunity: Batch 1 (expected March 2027)
Excluded from Batch Zero, receives no MW allocation, and must wait for a future batch
Illustrative

## Slide 20: Proposed Batch inclusion and treatment depend on timing of study completion and milestone achievement
3/4/26
7/10/26
3/1/27
LLIS studies are deemed complete and valid*
LLIS studies may be deemed complete and valid*
* LLI projects must also meet Planning Guide Section 9.5
LLIS studies no longer accepted; if not in Batch Zero, wait for Batch 1
If not in Batch 1, wait for Batch 2
Batch Zero
Batch 1
LLIS (“PGRR115”)

## Slide 21: Agenda
Large Load Interconnection 101
What is a Batch process
What is the transitional Batch Zero process
Current Key Issues
CLR and BYOG
Path to June Board

## Slide 22: Key Issues for Batch Zero
In comments submitted on PGRR145 and in ERCOT’s Batch Study workshops, stakeholders have raised several issues that ERCOT plans to present to the PUCT at the April 17 Open Meeting: Interchange - Documents
Study validity
Financial commitment and site control
Use of 2026 RTP inclusion as an alternative to financial commitment and site control requirements
Alternative requirements for projects with near term energization
Approaches to verifying development activity for near-term projects

## Slide 23: Two approaches to allocating future MWs: early certainty vs. alignment with transmission development
Chart: 
 | 100 | 100 | 450 | 600 | 600 | 1000
Year 1
Year 2
Year 3
Year 4
Year 5
Year 6
Chart: 
 | 100 | 100 | 450 | 600 | 600 | 600
 | 400
Year 1
Year 2
Year 3
Year 4
Year 5
TBD
Year 6
Automatically set at requested peak Demand
TBD: studied in next batch and allocated based on available capacity
Example: 1,000 MW data center requiring full capacity by Year 6
PGRR145 Approach
Alternative approach to address TSP comments
Illustrative allocation, MW
Request studied in Batch Zero: initial MWs allocated based on system capability; transmission constraints and required upgrades identified
Request studied in Batch Zero: initial MWs allocated based on system capability; transmission constraints and required upgrades identified
Years 1-5
  Provides certainty by guaranteeing full MWs by Year 6
  Creates a potential step-change in MWs between Years 5 and 6, with limited time to develop required transmission
  Full MW allocation is aligned with identified transmission upgrades
  Requires financial commitment for partial MWs without clear visibility on timing or certainty of full MW delivery
Considerations
Full MW automatically allocated based on Batch Zero results; transmission solutions further defined in the 2027 RTP
Full MW not committed in Batch Zero; additional MWs studied and allocated through a subsequent (~12-month) Batch 1 process
Year 6

## Slide 24: Agenda
Large Load Interconnection 101
What is a Batch process
What is the transitional Batch Zero process
Current Key Issues
CLR and BYOG
Path to June Board

## Slide 25: Potential frameworks under consideration and refinement for addressing CLR and BYOG (1/2)
  Large Load participates as a Provisional Controllable Load Resource (PCLR), where a portion of load is firm (LPC) and the remaining load is flexible and subject to dispatch
  The PCLR framework enables Load to consume more energy in unconstrained hours of the day ahead of full transmission build-out, with firm MW defined in the Batch Zero study and non-firm MW managed through SCED
Description
Details
  Split between firm and flexible load defined through the Load Commissioning Plan (LCP) (LPC = firm MW; remaining load operates as PCLR)
  PCLR participates as dispatchable demand and must follow SCED basepoints within its operating range
  Full requested load is studied in Batch Zero, with transmission upgrades identified to transition PCLR to firm service over time
Provisional Controllable Load Resource (CLR)
Point of interconnection
Load
Illustrative scheme
Expected PGRR publishing date: Apr 8
PRELIMINARY

## Slide 26: Potential frameworks under consideration and refinement for addressing CLR and BYOG (2/2)
Description
BYOG Batch Self-Limiting Facility (SLF)
  Site operates with a fixed transmission withdrawal limit determined through batch study
  Generation mix may include thermal resources, renewables, and batteries
  A fixed transmission withdrawal limit is established (e.g., 100 MW grid import limit) determined in the batch study
  The load and generation owners must coordinate operations to ensure grid imports never exceed the limit
  Transmission upgrades may be required if identified by the batch study to meet reliability criteria
Limited withdrawal
~
~
~
Point of interconnection
Load
Generator
~
Illustrative scheme
Details
Expected PGRR publishing date: TBD
PRELIMINARY

## Slide 27: Agenda
Large Load Interconnection 101
What is a Batch process
What is the transitional Batch Zero process
Current Key Issues
CLR and BYOG
Path to June Board

## Slide 28: Batch Zero Revision Request Timeline
Forums
ROS (Reliability and Operations Subcommittee)
2026
Q1
Q2
Q3
Feb
Mar
Apr
May
Jun
Jul
Workshop #2 Feb 12
Workshop #4 Mar 10
Workshop #5 Mar 24
Workshop #6 Mar 30
PRS Update 3/11
ROS Vote 5/7
Board Vote 6/1
3/4 ERCOT files Batch Zero Revision Request(s)
7/10 Target effective date of protocols
Consideration of Batch Zero NPRR 1325 and PGRR 145
LLWG Feb 19
Workshop #3 Feb 26
TAC Vote 5/19-20
Target Board approval date
Board Meeting 4/20
ROS Update 4/2
Monthly TAC updates
Workshop #7 Apr 9
Special PRS 4/22
Regular TAC 4/29
Special TAC 5/13
PRS Vote 5/6
Monthly LLWG updates
4/9 ERCOT files draft comments to the PGRR for CLR, followed by NPRRs for both CLR and BYOG (TBD)
ROS Update (special) 4/14
ROS Update 3/5
ROS Update (special) 4/23
PRS (Protocols Review Subcommittee)
Workshops and working groups
TAC
ERCOT Board
Objective
Align stakeholders on direction/scope following Commission decision
Define the scope, boundaries, and intended role of Batch Zero
File NPRR 1325 for Workshops and PRS review
Endorse NPRR 1325 for advancement to TAC
File PGRR 145 for Workshops and ROS review
Endorse PGRR 145 for advancement to TAC
Review/endorse combined NPRR/PGRR package for Board approval
Close outstanding design and drafting issues, incorporate vetted stakeholder feedback, and finalize Revision Request language for committee approval
Preview structure/governing concepts of Batch Zero PGRR before filing
Note that TAC leadership is involved in considering options to ensure successful review and approval
Regular PRS 4/15

## Slide 29: CLR and BYOG frameworks are being integrated into Batch Zero filing, forming a first comprehensive design with further refinement over time
PCLR comments
PCLR comments
PCLR comments
BYOG comments
PCLR comments
BYOG comments
March 4: ERCOT files PGRR145 and NPRR1325
March 17 and April 4: targeted ERCOT comments to incorporate stakeholder feedback
Establishes foundational framework for Batch Zero execution and LLI processing
April 13: PCLR introduced as modular enhancement via comments to PGRR145 / NPRR1325
Enables early shaping of controllable load pathway without delaying core filing
April (TBD): BYOG introduced as modular enhancement via comments to PGRR145 / NPRR1325
Enables integration of generation-backed load pathway without delaying core filing
Path of PGRR145 and NPRR1325 towards governance approval
Key takeaways
Modular approach enables speed without locking design: core framework advanced while PCLR and BYOG are developed in parallel
Convergence toward June Board: PGRR145/NPRR1325, PCLR, and BYOG converge into a complete, minimum viable package for decision-making
Minimum viable, not final design: PCLR and BYOG are introduced as initial concepts, with further refinement expected post June Board
Source: ERCOT discussion
1
2
3
Core Batch Zero framework established
PCLR framework integration
BYOG framework integration
Detailed next
PGRR145
PGRR145
PGRR145
NPRR1325
NPRR1325
NPRR1325

## Slide 30: PCLR introduces a flexible pathway within Batch Zero, requiring targeted updates across PGRR sections
PGRR145 reference section
Section 9.2 – Applicability, Eligibility, and Submission Requirements
Section 9.3 – Batch Zero Interconnection Study Methodology
Section 9.4 – Batch Zero Results and Commitment Requirements
Section 9.5 – Refinement Study and Transmission Planning
Section 9.6 – Energization and Operational Requirements
How PCLRs impact/integrate PGRR145 sections
Expand applicability to include PCLR as a distinct pathway, alongside Base Load and Studied Load
Introduce LPC-based modeling and enhanced data requirements for controllable load evaluation
Update LCP to reflect flexible load ranges (LPC to max) and non-linear energization profiles
Model PCLRs at LPC for reliability, decoupling operational and requested demand
Apply binary allocation logic: approve full load if LPC is supportable, otherwise allocate zero
Enable conditional approval of full demand, contingent on operational controllability
Introduce dual commitment structure, requiring interconnection agreement plus PCLR operational commitment
Require signed LPC commitments and notarized forms
Link study results to binding operational constraints and qualification requirements
Plan transmission for full requested load, despite near-term operation at LPC levels
Decouple planning horizon (full load) from operational reality (constrained load)
Allow staged energization, with initial operation capped at LPC until full qualification
Enforce dispatchability and LPC limits, requiring ERCOT approval before exceeding initial thresholds
Source: PGRR145- 38- 4/4/2026 ERCOT Comments; PGRR145 PCLR Comments

## Slide 31: PCLR enables dispatchable, price-responsive load, requiring targeted NPRR updates across pricing, dispatch, and commitment layers
Source: NPRR1325 (March 4, 2026); NPRR1325 Revised Protocol Language (PCLR comments)
NPRR1325 reference section
Section 2 – Definitions, acronyms and abbreviations
How PCLRs impact/integrate NPRR1325 sections
Introduce PCLR as a new controllable load construct, extending CLR into planning/operations
Define eligibility, LPC constraints, and operational limitations
Establish standardized terminology to enable consistent integration across Protocols
Section 3.2.5 – Publication of resource and load information
Publish CLR/PCLR energy bid curves and dispatch behavior
Include PCLR-adjusted bids, reflecting constraint-driven modifications
Provide visibility into real-time demand response to congestion
Section 4.4.9.4 – Mitigated offer cap/floor
Extend mitigation framework to incorporate PCLR participation alongside generation/ESRs
Align traditional offer caps with demand-side bid controls to ensure mitigation treatment
Ensure consistent price formation across supply and flexible demand resources
Section 6.5.7.3 – Security Constrained Economic Dispatch (SCED)
Integrate PCLRs into SCED as dispatchable, price-responsive load resources
Apply Adjusted Bid Caps within the two-step SCED process
Use Energy Bid Curves (instead of static load) to represent flexible demand
Enable real-time congestion management via demand response while maintaining reliability
Section 23 (Form W) – PCLR registration and commitment
Establish formal PCLR registration mechanism (Part A election, Part B commitment)
Require LPC commitments by year, tied to study outcomes
Enforce notarized forms and binding operational obligations
Link planning outcomes to dispatch compliance and ongoing qualification requirements
Section 4.4.9.4.4 – Adjusted Bid Caps (ABC)
Introduce dynamic bid capping for PCLRs based on constraint shadow prices
Use shift factors to determine each PCLR’s contribution to congestion
Enable targeted demand response while preventing over-response and price distortion
New section introduced

## Slide 32: Batch Zero Revision Request Timeline
Forums
ROS (Reliability and Operations Subcommittee)
2026
Q1
Q2
Q3
Feb
Mar
Apr
May
Jun
Jul
Workshop #2 Feb 12
Workshop #4 Mar 10
Workshop #5 Mar 24
Workshop #6 Mar 30
PRS Update 3/11
ROS Vote 5/7
Board Vote 6/1
3/4 ERCOT files Batch Zero Revision Request(s)
7/10 Target effective date of protocols
Consideration of Batch Zero NPRR 1325 and PGRR 145
LLWG Feb 19
Workshop #3 Feb 26
TAC Vote 5/19-20
Target Board approval date
Board Meeting 4/20
ROS Update 4/2
Monthly TAC updates
Workshop #7 Apr 9
Special PRS 4/22
Regular TAC 4/29
Special TAC 5/13
PRS Vote 5/6
Monthly LLWG updates
4/9 ERCOT files draft comments to the PGRR for CLR, followed by NPRRs for both CLR and BYOG (TBD)
ROS Update (special) 4/14
ROS Update 3/5
ROS Update (special) 4/23
PRS (Protocols Review Subcommittee)
Workshops and working groups
TAC
ERCOT Board
Objective
Align stakeholders on direction/scope following Commission decision
Define the scope, boundaries, and intended role of Batch Zero
File NPRR 1325 for Workshops and PRS review
Endorse NPRR 1325 for advancement to TAC
File PGRR 145 for Workshops and ROS review
Endorse PGRR 145 for advancement to TAC
Review/endorse combined NPRR/PGRR package for Board approval
Close outstanding design and drafting issues, incorporate vetted stakeholder feedback, and finalize Revision Request language for committee approval
Preview structure/governing concepts of Batch Zero PGRR before filing
Note that TAC leadership is involved in considering options to ensure successful review and approval
Regular PRS 4/15