## Slide 1
Large Load Interconnection Batch Study for Special ROS
April 23, 2026
Updated v2: Sections 4 & 5 populated

## Slide 2: Agenda
Timeline and governance recap
Update on timeline and key workshop dates
Outline PRS/ROS/TAC pathways to June Board with key submission dates
1
7
BYOG discussion
Further discussion of BYOG approach
Advance discussion on BYOG framework for Batch Zero
CLR discussion
Review revision language for CLR filed on April 17
3
6
Market Comments filed
Review stakeholder comments received
Batch Zero Concepts
Detailed review of Batch Zero Concepts
5
Feedback from PUCT and ERCOT comments
Review feedback received from PUCT on April 17 Open Meeting
Review updated ERCOT comments to PGRR145 filed on April 23
4
2
Year 6 allocation approach
Review alternative approach for dealing with year 6 allocation and discuss advantages and disadvantages

## Slide 3: Agenda
Timeline and governance recap
Year 6 allocation approach
CLR Discussion
Feedback from PUCT and ERCOT comments
Batch Zero Concepts
Stakeholder Feedback
BYOG Discussion
3

## Slide 4: Batch Zero Revision Request Timeline
Forums
ROS (Reliability and Operations Subcommittee)
2026
Q1
Q2
Q3
Feb
Mar
Apr
May
Jun
Jul
Workshop #2 Feb 12
Workshop #4 Mar 10
Workshop #5 Mar 24
Workshop #6 Mar 30
PRS Update 3/11
ROS Vote 5/7
Board Vote 6/1
3/4 ERCOT files Batch Zero Revision Request(s)
7/10 Target effective date of protocols
Consideration of Batch Zero NPRR 1325 and PGRR 145
LLWG Feb 19
Workshop #3 Feb 26
TAC Vote 5/19-20
Target Board approval date
Board Meeting 4/20
ROS Update 4/2
Monthly TAC updates
Workshop #7 Apr 9
Special PRS 4/22
Regular TAC 4/29
Special TAC 5/13
PRS Vote 5/6
Monthly LLWG updates
4/17 ERCOT filed comments to PGRR145 and NPRR1325 for CLR, followed by BYOG (TBD)
ROS Update (special) 4/14
ROS Update 3/5
ROS Update (special) 4/23
PRS (Protocols Review Subcommittee)
Workshops and working groups
TAC
ERCOT Board
Objective
Align stakeholders on direction/scope following Commission decision
Define the scope, boundaries, and intended role of Batch Zero
File NPRR 1325 for Workshops and PRS review
Endorse NPRR 1325 for advancement to TAC
File PGRR 145 for Workshops and ROS review
Endorse PGRR 145 for advancement to TAC
Review/endorse combined NPRR/PGRR package for Board approval
Close outstanding design and drafting issues, incorporate vetted stakeholder feedback, and finalize Revision Request language for committee approval
Preview structure/governing concepts of Batch Zero PGRR before filing
Note that TAC leadership is involved in considering options to ensure successful review and approval
Source: ERCOT discussions
Regular PRS 4/15

## Slide 5: Revision Request Process Flow
Comments may be filed between each step of the process
Comments for NPRR1325 may be submitted using the Comments Form found here
Comments for PGRR145 may be submitted using the Comments Form found here.
Submit to RevisionRequest@ercot.com
NPRR Comments
PGRR Comments
Large Load Interconnection Workshops
NPRR/PGRR
Review
BOARD
PUCT
TAC
ROS
PGRR Language/IA Review
PRS
NPRR Language/IA Review

## Slide 6: Related PUCT Activities
PUC Project 58480, 16 TAC § 25.370, Large Load Forecasting Rule (Adopted & Effective March 1, 2026)
  After 2026, only Large Loads that have executed an interconnection agreement that satisfies the requirements in PUC Project 58481 will be included in the Large Load forecast. These requirements will be reflected in future revision requests.
  Establishes alternative gating criteria for Large Loads to be included in the 2026 Large Load Forecast, which is used in planning assessments until new cases are constructed in 2027 using new rule criteria.
Source: PUCT Project No. 58480 (final rule) and Project No. 58481 – Proposal for Publication of 16 TAC §25.194 (filed March 12, 2026)
PUC Project 58481, proposed to be 16 TAC § 25.194, Large Load Interconnection Standards (Proposal for Publication published on March 12, 2026)
  Intermediate Agreement Requirements:
    Site control (updated)
    Financial Security ($50,000/MW in current PFP; subject to final rule)
    Disclosures
    Option to pay for significant equipment or services
  Interconnection Agreement Requirements:
    Site control (updated)
    Financial security
    Interconnection fee ($50,000/MW, non-refundable)
    CIAC
    Reallocation
    Withdrawal Consequences
    Refund Eligibility and Timing
  After the PUCT adopts a final rule, ERCOT will file a revision request to align Section 9.7 with the requirements in the final rule.

## Slide 7: Reminder of Scope and Priorities for Workshops
March 4 filings completed for Batch Zero: ERCOT filed the Batch Zero PGRR145 and related NPRR1325 on March 4, initiating the formal governance process and aligning with the May PRS/ROS/TAC sequence and June 1 Board target reflected in the critical path timeline
  March 17 ERCOT comments filed
  April 4 ERCOT comments filed: incorporated stakeholder feedback (received by March 20), including targeted clarifications and refinements
  April 23 ERCOT comments filed: updated proposal to align with PUCT April 17 Open Meeting guidance, including a shift to maturity- and commitment-based eligibility criteria, simplification of agreement/financial frameworks, introduction of net metering pathways, and refinements to allocation logic/Batch Zero study design
ERCOT progressing CLR and BYOG design through parallel comment tracks: Batch Zero comments may include or exclude CLR/BYOG elements, with ERCOT Market Rules managing versioning
  CLR status: April 17 comments filed, formally introducing and detailing PCLR framework (e.g., modular construct, operational treatment, linkage to future market implementation)
  BYOG Status: Concepts in progress, targeting filing comments for end of April
Long-term Batch Process revisions: out of scope for the current filing but soon after June 1. ERCOT will incorporate lessons learned from Batch Zero to inform future revision requests and the design of a durable, repeatable batch study process

## Slide 8: Agenda
Timeline and governance recap
Year 6 allocation approach
CLR Discussion
Feedback from PUCT and ERCOT comments
Batch Zero Concepts
Stakeholder Feedback
BYOG Discussion

## Slide 9: Year 6 allocation design choice: recap
Year 6 allocation remains a key design challenge for Batch Zero: process must balance early visibility for developers with alignment to actual transmission readiness, avoiding both over-commitment and lack of certainty
Two main approaches have been considered to date, each with clear trade-offs
  Current PGRR145 approach: allocates full MWs by Year 6 upfront, providing clarity but risking a step-change not supported by transmission development timelines
  “Rollover” approach: defers full MW allocation to a subsequent batch, ensuring realism but creating customer uncertainty and requiring commitment without clear visibility on full delivery
A third approach (“bookend” allocation) emerges as a more balanced solution:
  Description: focus the study on key years (2, 4, 6) to enable a 6-month Batch Zero while providing a full Year 1–6 capacity trajectory and anchoring Year 6 allocation to identified transmission solutions
  Enabler: early TSP involvement to define transmission solutions in parallel with the study
  Advantages: combines customer certainty (clear ramp) with transmission realism, enables an actionable 6-year plan within timeline, and reduces complexity and rework

## Slide 10: Existing approaches to Year 6 allocation present clear trade-offs between certainty and realism
PGRR145 Approach
“Rollover” approach to subsequent batch
Example: 1,000 MW data center requiring full capacity by Year 6
Years 1-5
Request studied in Batch Zero: initial MWs allocated based on system capability; transmission constraints and required upgrades identified
Request studied in Batch Zero: initial MWs allocated based on system capability; transmission constraints and required upgrades identified
Considerations
Provides certainty by guaranteeing full MWs by Year 6
Creates a potential step-change in MWs between Years 5 and 6, with limited time to develop required transmission
Full MW allocation is aligned with identified transmission upgrades
Requires financial commitment for partial MWs without clear visibility on timing or certainty of full MW delivery
Year 6
Full MW automatically allocated based on Batch Zero results; transmission solutions further defined in the 2027 RTP
Full MW not committed in Batch Zero; additional MWs studied and allocated through a subsequent Batch 1 process
Chart: 
 | 100 | 100 | 450 | 600 | 600 | 1000
Year 1
Year 2
Year 3
Year 4
Year 5
Year 6
Illustrative ramp schedule, MW
Chart: 
 | 100 | 100 | 450 | 600 | 600 | 600
 | 400
Year 1
Year 2
Year 3
Year 4
Year 5
TBD
Year 6
Automatically set at requested peak Demand
TBD: additional MWs studied in next batch and allocated based on available capacity

## Slide 11: “Bookend” allocation approach: resolving trade-off between early certainty and transmission alignment
Example: 1,000 MW data center requiring full capacity by Year 6
Chart: 
 | 100 | 300 | 300 | 500 | 500 | 1000
Year 1
Year 2
Year 3
Year 4
Year 5
Year 6
Illustrative ramp schedule and allocation methodology by year, MW
Key highlights
Not studied: based on existing system capacity (no upgrades)
Fully studied (all cases)
Not studied: conservative assumption equal to Year 2
Fully studied (all cases)
Not studied: conservative assumption equal to Year 4
Fully studied (all cases)
Studied
Not studied
Approach shifts from a fully prescriptive multi-year study to a targeted “bookend” approach to balance feasibility and value while reducing computational burden
Objectives:
  Preserve decision-quality outputs while making the study executable within a 6-month Batch Zero timeline
  Balance customer visibility with transmission realism
Process flow:
  Batch study produces Year 1–6 allocation trajectory and required transmission upgrades
  Customers use outputs to assess viability and commit
  Refinement removes non-committed load and refines projects and costs
  Output is a coherent, actionable transmission plan
Enablers
Early TSP involvement at study kickoff, with a shared Year 6 system case
Parallel development of transmission solutions and cost estimates
Centralized ERCOT coordination, consolidating TSP inputs into a single plan
Advantages
Delivers an actionable 6-year transmission plan within Batch Zero timeline, avoiding reliance on future cycles
Provides full Year 1–6 visibility for customer decisions
Reduces complexity and rework

## Slide 12: Agenda
Timeline and governance recap
Year 6 allocation approach
CLR Discussion
Feedback from PUCT and ERCOT comments
Batch Zero Concepts
Stakeholder Feedback
BYOG Discussion

## Slide 13: Overview of Provisional Controllable Load Resource (PCLR)
  Large Load participates as a Provisional Controllable Load Resource (PCLR), where a portion of load is firm (LPC) and the remaining load is flexible and subject to dispatch
  The PCLR framework enables Load to consume more energy in unconstrained hours of the day ahead of full transmission build-out, with firm MW defined in the Batch Zero study and non-firm MW managed through SCED
Description
Details
  Split between firm and flexible load defined through the Load Commissioning Plan (LCP) (LPC = firm MW; remaining load operates as PCLR)
  PCLR participates as dispatchable demand and must follow SCED basepoints within its operating range
  Full requested load is studied in Batch Zero, with transmission upgrades identified to transition PCLR to firm service over time
Provisional Controllable Load Resource (PCLR)
Point of interconnection
Load
Illustrative scheme

## Slide 14: Provisional CLRs – Definition1
New Resource Type: ‘Provisional CLR’
A Large Load electing to operate as a CLR post-Batch Zero, with LPC defined in study and commitment via Form
What’s different?
PCLR load bids can be ‘capped’ to mitigate transmission constraints identified in SCED
PCLR bids are capped dynamically (“last-in-line/just-in-time”) in each run of SCED to a price that will just allow SCED to resolve a constraint
PCLRs are not eligible to provide Ancillary Services
Submits CLR Energy Bid Curve  bid-to-buy prices between Low Power Consumption (LPC) and Maximum Power Consumption (MPC) – same as any other CLR
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.2.2.1, 9.3.2.1, 9.4.1, 9.5.3, and 9.6.1 (Provisional Controllable Load Resource design, study treatment, and operations)

## Slide 15: Provisional CLRs – Structure of Revision Requests1
Will consist of a comments to existing PGRR145 and companion NPRR1325
Modular structure adds to PGRR145 and NPRR1325
  Example – Section 9.2.2.1, Additional Information Required for Provisional Controllable Load Resources (PCLRs) compliments Section 9.2.2 as written in PGRR145
This structure will allow the PCLR concepts to move forward in parallel with PGRR145 and NPRR1325 if possible, without interfering with the core Batch Zero language
Language related to PCLR approval to energize and PCLR bid capping in SCED is intended to remain grey-boxed until implementation of NPRR1188 and until system changes for the bid capping are in place
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 16: PCLR Language – Foundational Concepts1
Allocation in Batch Zero
Registration Requirements
Ensure Real-Time Dispatch
Load is assessed through the Batch Zero process in the same manner as load requesting firm service for steady state and at full consumption for stability
The level of firm load that can be reliably served becomes the maximum Low Power Consumption (LPC) value for the PCLR in real-time (instead of a hard limit)
The remaining requested load amount is approved contingent on qualification as a PCLR
Intention to register as a PCLR must be declared prior to the start of Batch Zero
Once allocated in Batch Zero, the load must register and qualify as PCLR before it may consume above initial limits
Load must remain registered as a PCLR until an exit date identified in Batch Zero
Obligation to remain a PCLR transfers to subsequent owners of the Large Load
Like traditional CLRs, PCLRs must follow SCED basepoints when consuming energy2
Dynamic bid capping logic is added to ensure the PCLR will be dispatched rather than allowing the constraint to violate
1. Design and NPRR/PGRR language still under internal review and may change prior to filing | 2. On implementation of NPRR1188

## Slide 17: Provisional Controllable Load Resources (PCLRs) in Batch Zero1
ERCOT validates completion of all steps prior to granting Approval to Energize
8
QSE establishes required ICCP telemetry points
7
RE coordinates with ERCOT to establish metering and submit CLR parameters via RIOO
6
ILLE registers with ERCOT as a Resource Entity (RE) and designates a QSE
5
ERCOT studies the full load amount in the Batch Zero Refinement Study
4
ILLE submits updated Declaration to accept allocation amounts2
3
ERCOT studies PCLR in Batch Zero
2
Submission of Declaration and required information to ERCOT
(by July 24)
1
Must be done before non-firm load may energize
May be done in parallel with QSA
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
2. Failure to submit Form W removes project from the refinement story
Detailed next

## Slide 18: Post–Batch Zero, ILLE must elect path via Form W to retain position and proceed
Context
After Batch Zero results, each ILLE receives allocated LPC (firm) and MPC (total) values
To proceed, ILLE must submit Form W Part B election by deadline
Failure to elect leads to project being removed from Refinement study and loses queue position
Description
Option
Accept ERCOT-defined LPC and MPC values without modification
Maintains ability to consume above LPC, subject to PCLR qualification, dispatch, and bid capping
Accept PCLR as is
1
Elect to proceed as PCLR but reduce LPC and/or MPC below awarded levels
Provides flexibility while aligning with project readiness or infrastructure constraints
Accept PCLR with reduced values
2
Withdraw from PCLR and accept LPC values as firm load (with optional reduction), eliminating ability to exceed LPC
Withdraw PCLR, retain firm load
3
Withdraw from process
Decline participation and exit Batch Zero entirely
Project is removed from Refinement Study and must re-enter through a future process
4
Form W Part B election is binding and determines eligibility for Refinement Study and eventual energization. Failure to submit Form W Part B results in removal from Batch Zero

## Slide 19: Provision CLR (PCLR) – Dynamic Bid Capping Process
PUBLIC
1
SCED₋₁ (Previous Run)
After each SCED run, generate a fresh list of transmission constraints whose Shadow Price ≥ 90% of Max Shadow Price:
Constraint₁₂₃
Constraint₂₃₄
Constraint₃₄₅
Constraint₄₅₆
⚡ Shadow price threshold triggered
Match
2
SCEDcurrent (Before Step 2)
Compare the matching list against all active constraints in the current SCED run:
Constraint₂₃₄
Constraint₄₅₆
Constraint₆₇₈
Constraint₇₈₉
✔ 2 constraints match — evaluate PCLRs
Cap
3
SCED Step 2 (Bid Capped)
−0.02
Shift Factor Rule
Only PCLRs with a Shift Factor ≤ −0.02 on a matching constraint are eligible for bid capping
CAP
Bid Cap Applied
The PCLR's Energy Bid Curve is capped at the Adjusted Bid Cap (ABC) value before Step 2 executes
✓
Adjusted Bid Cap Formula:
ABC = Step 1 System Lambda − max ( MaxShadowPrice × ShiftFactor ) − $0.01 / MWh
Only applied where PCLR Shift Factor ≤ −0.02 | Constraint must appear in prior-run trigger list | No standard market mitigation applies to Energy Bid Curves

## Slide 20: CLR and BYOG frameworks are being integrated into Batch Zero filing, forming a first comprehensive design with further refinement over time
PCLR comments
PCLR comments
PCLR comments
BYOG comments
PCLR comments
BYOG comments
March 4: ERCOT files PGRR145 and NPRR1325
March 17 and April 4: targeted ERCOT comments to incorporate stakeholder feedback
Establishes foundational framework for Batch Zero execution and LLI processing
April 17: PCLR introduced as modular enhancement via comments to PGRR145/ NPRR1325
Enables early shaping of controllable load pathway without delaying core filing
April (TBD): BYOG introduced as modular enhancement via comments to PGRR145 / NPRR1325
Enables integration of generation-backed load pathway without delaying core filing
Path of PGRR145 and NPRR1325 towards governance approval
Key takeaways
Modular approach enables speed without locking design: core framework advanced while PCLR and BYOG are developed in parallel
Convergence toward June Board: PGRR145/NPRR1325, PCLR, and BYOG converge into a complete, minimum viable package for decision-making
Minimum viable, not final design: PCLR and BYOG are introduced as initial concepts, with further refinement expected post June Board
Source: ERCOT discussion
1
2
3
Core Batch Zero framework established
PCLR framework integration
BYOG framework integration
Detailed next
PGRR145
PGRR145
PGRR145
NPRR1325
NPRR1325
NPRR1325

## Slide 21: PCLR introduces a controllable-load pathway within Batch Zero, enabling staged interconnection while preserving full transmission planning
PGRR145 reference section
Section 9.2 – Applicability, Eligibility, and Submission Requirements
Section 9.3 – Batch Zero Interconnection Study Methodology
Section 9.4 – Batch Zero Results and Commitment Requirements
Section 9.5 – Refinement Study and Transmission Planning
Section 9.6 – Energization and Operational Requirements
How PCLRs impact/integrate PGRR145 sections
Expand applicability to include PCLR as a distinct pathway, alongside Base Load and Studied Load
Introduce enhanced data and modeling requirements for controllable loads
Define LPC (firm, reliable level) and MPC (conditional full demand), enabling flexible load ranges
Decouple planning vs. reliability modeling: plan system for full requested load (MPC), assess reliability at LPC (constrained level)
Establish LPC as the maximum reliably serviceable load in each study year
Enable two-tier outcomes: firm allocation at LPC, and conditional approval of additional demand (MPC)
Introduce dual commitment structure: interconnection Agreement (infrastructure) and PCLR operational commitment (Form W)
Require formal election of PCLR pathway, including ability to accept, modify, or decline LPC/MPC structure
Link study results to binding operational limits and qualification requirements
Plan transmission for full requested demand (MPC) to avoid underbuilding
Decouple long-term system design from near-term operations
Maintain LPC as the planning input for committed PCLRs in refinement
Enable staged energization, with initial operation limited to LPC
Require PCLR qualification (registration, telemetry, testing) before exceeding LPC
Enforce dispatchability and ERCOT control, with operations capped until full approval
Source: 145PGRR-45 ERCOT Comments 041726

## Slide 22: PCLR enables dispatchable, price-responsive load by integrating large load into ERCOT market operations and SCED
Source: 1325NPRR-05 ERCOT Comments 041726
NPRR1325 reference section
Section 2 – Definitions, acronyms and abbreviations
How PCLRs impact and integrate NPRR1325 sections
Introduce PCLR as a new controllable load construct, extending CLR into large-load interconnection
Define LPC (firm level) and MPC (conditional level) and associated operational constraints
Establish standardized terminology linking planning, dispatch, and compliance
Section 3.2.5 – Publication of resource and load information
Represent demand as price-responsive curves (LPC to MPC) instead of static load
Publish aggregate demand curves from Energy Bid Curves reflecting flexible consumption
Provide visibility into real-time demand response capability in SCED
Section 4.4.9.4 and 4.4.9.4.4 – Mitigation and Adjusted Bid Caps (ABC)
Extend mitigation framework to include dispatchable load alongside generation and ESRs
Introduce constraint-driven bid capping (ABC) for PCLRs: triggered by binding constraints (≥90% shadow price) and applied based on PCLR shift factor contribution to congestion
Align demand-side participation with efficient and consistent price formation
Section 6.5.7.11 – PCLR ramp rate requirements
Define minimum controllability requirements (10–20%/min ramp rates)
Establish performance monitoring and compliance thresholds
Enable ERCOT to enforce dispatch responsiveness and reliability performance
Section 23 (Form W) – PCLR registration and commitment
Establish formal PCLR registration mechanism (Part A election, Part B commitment)
Bind LPC/MPC outcomes from planning to operational obligations
Require continuous qualification, dispatch compliance, and telemetry
Define exit conditions, de-registration, and enforcement mechanisms
Section 6.5.7.3 – Security Constrained Economic Dispatch (SCED)
Integrate PCLRs into SCED as dispatchable, price-responsive resources
Implement two-step SCED process: Step 1 (reference prices without constraints) and Step 2: constrained dispatch with PCLR bid capping (ABC)
Use Energy Bid Curves (vs. fixed load) to represent flexible demand
Enable real-time congestion management via demand response while maintaining reliability
New section introduced

## Slide 23: Provisional CLRs – Declaration of Intent and Batch Treatment

## Slide 24: Commitment process (1/3)

## Slide 25: Commitment process (2/3)

## Slide 26: Commitment process (3/3)

## Slide 27: PCLR in Refinement Process

## Slide 28: PCLR Energization Requirements

## Slide 29: Agenda
Timeline and governance recap
Year 6 allocation approach
CLR Discussion
Feedback from PUCT and ERCOT comments
Batch Zero Concepts
Stakeholder Feedback
BYOG Discussion

## Slide 30: Feedback from April 17 PUCT Open Meeting
During the April 17 PUCT Open Meeting, the Commission provided guidance on ERCOT’s proposed approach to key Batch Zero design questions, signaling agreement with ERCOT’s recommendations
For areas where ERCOT did not provide explicit recommendations, the Commission directed that the Staff Memo should fill the gaps and guide the final framework
Additional feedback and discussion points:
  Need for a minimum allocation threshold for Batch Zero, with a range of ~100–200 MW considered
  $50k/MW financial security was clarified as a one-time requirement that becomes non-refundable at the interconnection agreement stage
  Commissioners emphasized that the financial security framework should balance ratepayer protection with enabling real project development, with differentiation by project maturity
  Discussion on what constitutes sufficient evidence of project maturity, with long-lead equipment viewed as a stronger signal than early-stage permitting
  Commission debated the appropriate level of verification for development activity, weighing stronger evidence against potential process delays
  Net metering and co-located load arrangements submitted before March 4 were generally considered eligible for inclusion as base load, subject to conditions and modeling considerations
  A ~60-day commitment window after Batch Zero was discussed as a reasonable baseline to balance financing needs and process speed
ERCOT incorporated the guidance received from the PUCT in the PGRR145 Comments filed on April 23
Source: April 17 PUCT Open Meeting
Detailed next

## Slide 31: Key updates in April 23 PGRR145 ERCOT comments, including implementation of PUCT guidance (1/2)
Aligned Batch Zero eligibility with PUCT guidance (April 17 OM): removed energization-date-driven criteria and introduced a structured framework based on project maturity, site control, financial commitment, and disclosure requirements
Shifted from agreement-based eligibility to broader readiness criteria: replaced reliance on executed Interconnection/ Intermediate Agreements with a more flexible set of readiness signals (e.g., equipment orders, NTP, power contracts, financial security, site control)
Introduced explicit treatment for additional load categories: added pathways for Permian Basin projects and net metering (PURA 39.169) loads, clarifying how these are included and modeled in Batch Zero
Consolidated and tightened “Load to be Studied” eligibility: merged previously separate pathways and imposed minimum requirements (site control, financial security, disclosures), creating a more consistent entry threshold
Simplified financial and contractual framework: removed detailed Intermediate Agreement / Interconnection Agreement constructs and replaced Section 9.7 with disclosure-only requirements, deferring key elements to PUCT rulemaking
Enhanced protection and grandfathering of legacy projects: explicitly deemed interim-process studies and agreements as satisfying legacy LLIS requirements, reducing risk of re-evaluation for advanced projects
Source: PGRR145 ERCOT Comments, April 23
Link to PGRR145 Comments from ERCOT April 23

## Slide 32: Key updates in April 23 PGRR145 ERCOT comments, including implementation of PUCT guidance (2/2)
Strengthened project readiness verification: introduced ERCOT authority to perform site readiness checks and require supporting evidence from developers
Refined modeling logic for base load and studied load: clarified how demand is derived across years, including explicit treatment of study-based limits, transmission timing (TPIT), and special cases (e.g., net metering loads)
Introduced minimum allocation and monotonicity rules in study results: ensured allocations do not increase and then decrease over time, and set minimum thresholds (e.g., 200 MW) below which projects may receive zero allocation
Added mechanisms to operationalize partial allocations: created explicit rules to handle low allocation outcomes and ensure consistent treatment across studied loads
Linked Batch Zero timelines to PUCT rulemaking: replaced fixed commitment deadlines with references to PUCT Rule 25.194, increasing regulatory alignment but introducing external dependency
Increased clarity and rigor in study execution: expanded requirements for short-circuit analysis, identified affected TSPs in outputs, and clarified that refinement does not change financial obligations
Improved transparency and governance of the process: added protections for submitted information, clarified roles, and formalized stakeholder-informed elements (e.g., allocation rules, study outputs)
Source: PGRR145 ERCOT Comments, April 23
Link to PGRR145 Comments from ERCOT April 23

## Slide 33: New Requirements Added in April 23 PGRR Update
Source: PGRR145 ERCOT Comments, April 23
Stronger and standardized site control requirements. Narrowed to two acceptable forms only:
  Executed lease (≥5 years): signed lease covering the full project site with a term extending ≥5 years beyond reaching full contracted peak demand
  Ownership (deed): legal title to the land (via deed) covering all parcels required for the planned facilities
Unified financial commitment framework. Consolidates prior approaches into a single structure:
  If upgrade costs known, post full required security
  If no upgrades are needed, no security required
  If costs are unknown, default security level equal to $50k/MW
Key new requirements introduced
  New end-use (tenant) requirement: projects must demonstrate confirmed end-use demand
    Either ILLE is the end-use customer, or
    ILLE has a signed contract with an end-use customer
  New power supply requirement: projects must demonstrate secured power supply sufficient to meet the Load Commissioning Plan (LCP)

## Slide 34: Agenda
Timeline and governance recap
Year 6 allocation approach
CLR Discussion
Feedback from PUCT and ERCOT comments
Batch Zero Concepts
Stakeholder Feedback
BYOG Discussion
34

## Slide 35: Batch Zero Overview – Two Phases
Study Inputs
Batch Zero Study
Batch Zero Refinement
ILLE Commitment Period
Transmission Plan to RPG
~6 months
~3 months
  Steady state study and dynamic stability screening
  Identify planning criteria violations
  Present study scope and methodology to RPG for stakeholder input
  Work iteratively with TSPs to determine amount of load that can be reliably served in each year and, where feasible, upgrades needed to serve full load request
Work iteratively with TSPs to
  Re-evaluate transmission upgrades based on committed loads only (remove withdrawn projects)
  Review cost estimates and alternative upgrade options
  Develop a transmission plan to serve committed loads
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.3.1–9.3.2, 9.4, and 9.5 (Study process, commitment, and refinement)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 36: Batch Zero Study Scope Overview
  Study horizon: 2028–2032 (Years 1–5), load amounts not reliably served within 2028-2032 will be set equal to requested load in 2033 (Year 6)
  What ERCOT studies (per year): ERCOT builds study cases based on planning models and approved study methodology and runs reliability assessment across:
    Summer peak load (high load system stress)
    Summer, no solar (sunset, net peak load)
    Fall peak (used to assess maintenance outage conditions consistent with ERCOT Planning Guide criteria)
  Reliability assessment coverage:
    Evaluate planning criteria violations triggered by adding the Batch Zero loads (across scenarios/contingencies ERCOT selects)
    Determine the amount of load that can be served reliably for each load and each year; allocations must be non-decreasing year-over-year (i.e., deliverable load that can be served without violating planning criteria)
    For non-PCLR loads, if allocated Demand is below 200 MW (or requested Demand if lower), allocation is set to zero for that year
    ERCOT shall determine reliably served peak Demand for each year within the 2028–2032 study scope
  Generation assumptions: if additional generation is needed to serve the modeled load, ERCOT models generation additions consistent with applicable planning methodologies
  Transparency: ERCOT posts study cases and contingencies (interconnection and refinement) used for Batch Zero on the MIS Secure Area once available
Scope details
Key Design Considerations
  One consistent, system-wide reliability study: ERCOT evaluates all Batch Zero-eligible Large Loads using a common set of assumptions, criteria, and cases to identify system limitations and needed upgrades
  Clear, year-by-year outcomes: for each assessed Large Load, the study determines the maximum peak MW that can be reliably served each year (2028–2033) and the transmission upgrades needed to increase service toward the requested level
  Stakeholder input on methodology: ERCOT presents study scope and approach to RPG for comment prior to execution
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.3.1 and 9.3.2 (Batch Zero Study Scope and Methodology)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 37: Batch Zero Study Methodology and Study Elements
Study elements and methodology
Key Design Considerations
  Study must be repeatable and explainable: ERCOT uses transparent study inputs (posted cases), consistent criteria, and a clear link from violations to upgrades to year-by-year reliably served MW
  Actionable coordination: the process enables rapid, iterative ERCOT–TSP alignment on transmission improvements while the study is underway
  Prepare system-wide study cases (ERCOT)
    Develop annual cases for 2028–2032 based on ERCOT planning models and study methodology
    Add Batch Zero-eligible Large Loads per the inclusion criteria and model treatment rules
    Post cases to MIS Secure once available
  System-wide reliability assessment (ERCOT)
    Study scenarios and contingencies ERCOT determines are needed to evaluate reliability impacts
    For each assessed LL, identify planning criteria violations associated with the proposed addition
    Determine the amount of peak load that can be reliably served each year
  Stability screening assessment (ERCOT)
    Perform the stability component of the Batch Zero study
    Perform stability screening as part of the Batch Zero study to assess system reliability impacts
  Identify transmission improvements (ERCOT and impacted TSPs)
    Once violations are identified, ERCOT initiates communication with relevant TSPs
    TSPs provide upgrade recommendations; ERCOT and TSPs iterate through the study period until needed upgrades are identified with ERCOT retaining final determination authority
    Results translate into upgrades resolving violations/enabling higher reliably served MW over time
  Supporting prerequisites (TDSPs/TSPs, as applicable)
    Inputs (pre-study): Interconnecting DSPs/TSPs submit required project data and information prior to study initiation (Section 9.2.2)
    Refinement activities (post-study): Short-circuit analysis performed by the Interconnecting TSP during the refinement phase (Section 9.5.2)
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.2.2, 9.3.1, 9.3.2, and 9.5.2
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 38: Outputs, Deliverables, and Timeline
Process and outputs
  Core timeline
    By July 10, 2026: ILLEs meet eligibility / milestone requirements
    By July 24, 2026: TSPs/DSPs submit complete project information to ERCOT
    By August 7, 2026: ERCOT confirms Batch Zero inclusion and classification of each load
    January 29, 2027: ERCOT issues the Batch Zero Study Report, provides Load Commissioning Plans (LCPs) to ILLEs (via TSPs/DSPs) and notifies TSPs of Batch Zero results
    April 1, 2027 or per P.U.C. Rule 25.194 timelines: TDSPs notify ERCOT which Large Loads have met commitment requirements
    July 1, 2027: ERCOT completes the Batch Zero Refinement Study and delivers the Batch Zero Transmission Plan to RPG
  Primary outputs
    Batch Zero Study Report (summary of reliability impacts, identified planning criteria violations, and proposed transmission upgrades)
    Load Commissioning Plan (LCP) per Large Load
      Maximum reliably served peak MW for each year, subject to non-decreasing allocation rules (2028–2033)
        Loads not reliably served receive full requested allocation for year 2033
    Estimated security requirements and CIAC obligations required to inform ILLE commitment decisions
    Confidential TSP package: detailed upgrade list and associated Large Loads (as applicable)
  Refinement and RPG handoff
    Only Large Loads that meet commitment milestones remain in scope, loads that do not meet commitment are removed from Batch Zero
    MW allocations for Large Loads that meet commitment criteria by the deadline are not adjusted during the Refinement Study
    ERCOT re-evaluates whether previously identified upgrades are still needed/modified/no longer required
    Final Batch Zero Transmission Plan is delivered into the RPG process
  Actionable outcomes: each Large Load receives a year-by-year Load Commissioning Plan (LCP) and estimated security requirements to support commitment decisions. TSPs receive
  Clear commitment gate to planning certainty: only Large Loads that meet commitment milestones move into the Refinement Study and transmission plan delivered to RPG
Key Design Considerations
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.3.1, 9.4, and 9.5 (Timeline, Outputs, and Refinement Process)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 39: Batch Zero process flow chart for studied load
Submit intermediate agreement requirements
Sign intermediate agreement and Send Batch Info to ERCOT
Build Cases and Post on MIS Secure
Perform Batch Steady State Study
Perform transmission improvement analysis
Perform supporting studies (as applicable, including refinement phase)
Post cases and results on MIS Secure and Communicate Results
Submit interconnection agreement requirements
Sign interconnection agreement
Perform Refinement Transmission Plan Study
Provide Cost Estimates and supporting inputs
Submit Refinement Transmission Plan Study for RPG Review
Resolve RPG Comments and Seek BOD endorsement, when necessary
ERCOT
T(D)SP
Developer (Interconnecting Large Load Entity – ILLE)
Perform Batch Stability Screening Study
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.3.1, 9.4, and 9.5 (Timeline, Outputs, and Refinement Process)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 40: Proposed Batch Zero Timeline
1
2
3
4
5
6
7
8
9
9
2026
2027
Aug
Sep
Oct
Nov
Jul
Dec
Feb
Mar
Apr
May
Jun
Jul
Aug
Jan
Sep
RPG Comment Period (3 weeks)
RPG Study Mode (4-weeks, if required)
TAC (August 2027)
Board (September 2027)
2026 RTP
Final Report (2 weeks)
2027 RTP
Batch Zero (Study years 2028-2032)
Stability Screening Study (14 weeks)
Steady State Analysis (15 weeks)
Developer Commitment Deadline
FAC-002 Stability
Batch Refinement Study (13 weeks)
Case Build (13 weeks)
Batch Refinement Study:
ERCOT: determine which transmission improvements identified in the Batch study are still required based on which loads met the commitment requirements
TSPs: provide cost estimates and refinement of transmission improvement projects and alternatives
ERCOT: refine and confirm transmission improvements for RPG submission
ERCOT: prepare final report and submit to RPG
Steady State and Stability Analyses:
ERCOT: identification of criteria violations
ERCOT and TSPs: identification of transmission improvement projects and alternatives to resolve violations
TSPs: determination of transmission improvement feasibility and schedule
TSPs: provide transmission improvement cost estimates
ERCOT: determine transmission improvements for study purposes
ERCOT: determine reliably served MW for each load
ERCOT: create load request to transmission improvement mapping

## Slide 41: Case Build
1
Details
Key Design Considerations
  Standardized ERCOT intake and deadline
  Clear eligibility and inclusion rules for Batch Zero
  Defined modeling treatment at entry
  Transparent study case development (posted to MIS Secure)
  For Batch Zero, the interconnecting TDSP submits required project information and any required attestations demonstrating required commitment criteria (e.g., site readiness activities, long-lead equipment orders, notice to proceed, power supply arrangements) (per Section 9.2.1.1(e)–(f)) by the applicable deadlines (July 10 for ILLE milestones, July 24 for TDSP submission to ERCOT), including DSP/TSP attestation of end-use customer arrangements, where applicable
  ERCOT applies the Batch Zero eligibility criteria to determine which Large Loads are included and whether they are treated as base load not subject to further evaluation or load subject to reliability assessment and allocation including ERCOTs determination of whether existing interconnection studies are valid, with certain studies deemed complete and valid without further review under Section 9.2.1.4(3) (e.g., studies associated with RPG-endorsed projects or completed legacy interconnection processes per Section 9.2.1.4)
  Projects that do not meet the criteria or fail to submit required information by the deadline are excluded from Batch Zero and evaluated in a future process
  ERCOT develops the 2028–2032 study cases based on planning models and approved study methodology, and posts those cases to the MIS Secure area to provide transparency into study assumptions
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.2.1–9.2.2 (Eligibility, Submission, and Study Validation)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 42
Details
Key Design Considerations
  ERCOT performs a singular, system-wide steady-state study for all Large Loads included in Batch Zero using SSWG derived base cases appropriate for the study horizon
  ERCOT studies all scenarios and contingencies necessary to assess reliability with applicable NERC Reliability Standards, ERCOT Protocols, the Planning Guide, and Operating Guides
  As soon as violations are identified, ERCOT begins collaborative, iterative process working with TSPs to identify feasible transmission upgrades with ERCOT making final determinations to serve the Large Loads
  For each Large Load subject to assessment, ERCOT documents planning criteria violations and determines the amount of peak Demand that may be reliably served for each year of the 2028–2032 study period. The amount of load that may be reliably served for 2033 will be set to the requested amount for load not reliably served in 2028–2032
  Single, system-wide ERCOT study
  Reliability-based contingency analysis
  Identification of planning criteria violations
  Determine the amount of peak demand that may be served reliably for each year, with allocations adjusted to be non-decreasing year-over-year and including the rule that allocations below 200 MW (or requested demand, if lower) are set to zero for that year
Steady State Analysis
2
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.3.1–9.3.2 (Batch Zero Study Scope and Methodology)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 43
Details
Key Design Considerations
  Maintain sufficient stability margin
  Mitigation of identified instability
  Coordination with TSPs
  If stability screening criteria violation is identified, ERCOT and the applicable TSP(s) investigates mitigation measures, including transmission improvements, and incorporates stability screening results into the determination of the amount of peak Demand that may be served reliably for each year reflected in the Load Commissioning Plan
Stability Screening Study
3
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.3.1 and 9.3.2 (Batch Zero Interconnection Study and Methodology)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 44
Details
Key Design Considerations
  Actionable study outcome
  Clear MW allocations by year
  Identification of required upgrades
  Security visibility
  ERCOT produces the Batch Zero Report summarizing study results and identified transmission upgrades
  For each assessed Large Load, ERCOT updates the originally provided Load Commissioning Plan reflecting the amount of peak Demand that can be reliably served each year and the upgrades required to support each level of Demand. The amount of load that may be reliably served for 2033 will be set equal to requested MW for load not achievable in earlier years
  ERCOT includes estimated security requirements in the Batch Zero Report based on TSP cost inputs; TSPs finalize financial security and CIAC obligations in the Interconnection Agreement
  Execution of an Interconnection Agreement (per PUCT Rule 25.194), as confirmed via DSP attestation, is required for the ILLE to accept allocated MW amounts and schedule
Final Report
4
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.4 and 9.3.1 (Batch Zero Report, ILLE Commitment, and timeline)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 45
Details
Key Design Considerations
  Clear commitment gate
  TDSP attestation as trigger
  Removal of non-committed projects
  Planning certainty before refinement
  To accept the allocated MW and schedule documented in the LCP, the ILLE must execute a binding Interconnection Agreement by the commitment deadline. The Interconnection Agreement must meet applicable requirements (e.g., PUCT Rule 25.194), including financial security and CIAC obligations; required disclosures are separately attested per Section 9.7
  The interconnecting DSP must submit formal attestation to ERCOT confirming that the ILLE has executed the Interconnection Agreement by the deadline. This attestation serves as verification that the load has satisfied the commitment requirement for inclusion in the Batch Zero Refinement Study
  Large Loads that do not satisfy the commitment requirement by the deadline are deemed withdrawn from the Batch Zero process and are excluded from the Refinement Study and resulting Transmission Plan
  MW allocations for Large Loads that meet the commitment requirement by the deadline are preserved and are not adjusted during the Refinement Study once commitment requirements are met. The Refinement Study may modify recommended transmission facility improvements but does not revisit committed MW amounts
Developer Commitment Deadline
5
Reference: Batch Zero PGRR145 (April 23, 2026), Section 9.4 (ILLE Commitment and Refinement eligibility)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 46
Details
Key Design Considerations
  Removal of non-committed loads
  Re-evaluation of identified upgrades
  Right-sizing of transmission scope
  Preparation of Transmission Plan for RPG
  Immediately following the commitment deadline, ERCOT updates the Batch Zero study to include only those Large Loads that met commitment requirements
  ERCOT evaluates whether the remaining loads continue to result in planning criteria violations and whether previously identified transmission upgrades are still needed, need modification, or are no longer required
  ERCOT works iteratively with relevant TSPs during this period and develops the final Transmission Plan to be delivered to RPG
  The Refinement Study may modify recommended transmission improvements but does not adjust MW allocations for Large Loads that met commitment criteria
  The Refinement Study results in a final report and recommended Transmission Facility improvements submitted for RPG Project Review
Batch Refinement Study
6
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.5 (Batch Zero Refinement Study and Transmission Plan)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 47
update (highlight changes)
Details
Key Design Considerations
  Stakeholder review and transparency
  Time-bound comment process
  Preservation of governance pathway
  ERCOT submits the final Batch Zero Refinement report, including recommended Transmission Facility improvements, for RPG Project Review in accordance with ERCOT Protocol Section 3.11.4
  Stakeholders have an opportunity to submit comments within a defined review period. RPG review focuses on the recommended Transmission Facility improvements identified in the Refinement Study and the associated technical assumptions
  MW allocations for committed Large Loads are not adjusted during the Refinement Study and are not subject to change through the RPG review process
RPG Comment Period
7
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.5 and ERCOT Protocol Section 3.11.4 (RPG Project Review Process)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 48
Details
Key Design Considerations
  Targeted additional evaluation if necessary
  Focused response to material concerns
  If needed, ERCOT may perform targeted additional analysis to address issues raised during RPG review, any additional study is limited to recommended Transmission Facility improvements and does not reopen MW allocations for committed Large Loads
  This step is intended to provide focused technical clarification rather than a full annual RTP-level re-evaluation
  The scope of additional analysis during RPG review is limited to evaluation of recommended Transmission Facility improvements identified in the Refinement Study
RPG Study Mode
8
XXX Changes/Clarification vs. Apr 14th ROS
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.5 and ERCOT Protocol Section 3.11.4 (RPG Project Review Process)

## Slide 49
Details
Key Design Considerations
  Formal governance review
  Recommendation pathway
  Final approval authority
  ERCOT independent review and approval of recommended projects
  Following completion of RPG review and any additional study, if applicable, the Batch Transmission Plan proceeds to TAC for review and comment in accordance with ERCOT governance procedures
  If required under ERCOT governance procedures, the ERCOT Board considers and acts on the recommended Transmission Plan resulting from the Batch Zero process. Board action applies to recommended Transmission Facility improvements identified in the Refinement Study
  MW allocations for Large Loads that meet commitment criteria are not adjusted during the Refinement Study and are not part of the Transmission Plan approval considered by TAC or the ERCOT Board, if applicable
  Approval reflects ERCOT’s independent technical review, TSP coordination, and stakeholder input through the RPG process
TAC and Board
9
XXX Changes/Clarification vs. Apr 14th ROS
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.5 and ERCOT Protocol Section 3.11.4 (RPG Project Review Process)

## Slide 50: Fundamental Principles for ERCOT's Proposed Batch Zero Criteria
Senate Bill 6 and PUC Gating Rules: Utilize (and align with) the gating criteria reflected in Project No. 58481 rulemaking (subject to final PUCT direction) to determine which large loads should be confirmed firm and which should be included to be studied in Batch Zero
Pre-Transition Processes: Respect to the extent feasible already granted approvals, including approval to energize and approved studies
Large Load Near-Term Energizations: Assess development activity for large loads that declare 2026 or 2027 energization to evaluate schedule feasibility
ERCOT’s Reliability Responsibility: Ensure all Large Loads confirmed to be firm in Batch Zero have been studied to show that the load can be served reliably
ERCOT–TSP Coordination: Incorporate structured consultation with Transmission Service Providers in study validation and transmission planning decisions

## Slide 51: Eligibility flowchart: how to assess if a load is included for Batch Zero?
1. Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.1(a)–(b) | 2. PGRR145 (April 23, 2026), Section 9.2.1.1(c), (d), and (g) | 3. Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.1(e)–(f) and Section 9.2.1.4 | 4. Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.2(1) | 5. Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.1(2) | 6. Batch Zero PGRR145 (April 23, 2026), Sections 9.2.1.2 and 9.3.2 (Studied Load Eligibility and MW Allocation through Batch Zero Study) | 7. Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.3
Has the load achieved Initial Energization as of July 10, 2026?1
Large Load request
Included in Batch Zero as a base load5
Not included in Batch Zero7
Studied in Batch Zero and will receive load allocation amounts6
Yes
No
Does the load meet baseload eligibility criteria under Section 9.2.1.1, including either pre-qualified pathways (e.g., QSA/IVRT, Permian Basin, net metering) or study-based criteria (i.e., complete and valid interconnection studies and required commitment criteria – financial security, site control etc.)?²
Has the load executed an Intermediate Agreement (or Interconnection Agreement) and meets eligibility criteria under Section 9.2.1.2?4
Does the load meet eligibility criteria for inclusion as studied load under Section 9.2.1.2 (e.g., site control, financial security, and required disclosures)?3
Yes
No
1
2
4
X
Reference tracker
No
No
Yes
Yes
3
5

## Slide 52: Deep-dive: “Included as base load” (1/6)
If your Large Load by June 1, 2026 | Treatment in Transitional Process | MW Allocation
Is Operational or Approved to Energize | Included as base load | Loads operational before ERCOT’s interim LLI process will be allocated the MWs modeled in the 2025 RTP Loads operational after ERCOT’s interim LLI process will be allocated the lesser of: MWs modeled in the 2025 RTP less the difference between: The planned MW by December 1, 2025, and the maximum consumed by June 1, 2026 MWs included in their Load Commissioning Plan, if applicable, less the difference between: The planned MW by December 1, 2025, and the maximum consumed by June 1, 2026 MWs in an updated ramp schedule as provided to the DSP by June 1, 2026 Loads not yet operational will be allocated the lesser of: MWs that can be reliably served as indicated in their interconnection studies MWs included in their interconnection agreement and reflected in their financial security
MW Allocation
If your Large Load
  Achieved Initial Energization before March 25, 2022; or
  Achieved Initial Energization between March 25, 2022, and July 10, 2026
Treatment in Transitional Process
  Included as base load and not subject to further reliability assessment
  Large Loads that achieved Initial Energization before March 25, 2022, shall be modeled at the level of peak Demand reported to ERCOT as part of development of the 2026 RTP
  Large Loads that achieved Initial Energization between March 25, 2022, and July 10, 2026, shall be modeled at the lesser of:
    The level of peak Demand reported to ERCOT as part of development of the 2026 RTP; or
    The level of peak Demand indicated in the most recent Load Commissioning Plan (if applicable) provided to ERCOT on or before July 24, 2026
1
Reference: Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.1(1)(a)–(b) and 9.2.1.1(2)(a)–(b)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 53: Deep-dive: “Included as base load” (2/6)
If your Large Load
  Has NOT achieved Initial Energization as of July 10, 2026 AND meets development readiness criteria under Section 9.2.1.1(1)(e), including:
    Complete and valid interconnection studies
    Site control demonstrated
    Financial security posted (as determined by TSP/DSP; or $50k/MW if upgrade cost unknown)
    CIAC / interconnection costs paid or secured
    Demonstrated development readiness (e.g., NTP issued, long-lead equipment ordered)
    Power supply arrangements in place
    DSP/TSP attestation that required disclosures (Section 9.7) are satisfied
Treatment in Transitional Process
  Included as base load and not subject to further reliability assessment
MW Allocation
  Large Loads meeting base load eligibility criteria that are not yet operational will be modeled at the lesser of:
    The level of peak Demand that can be served reliably as indicated in complete and valid existing studies; or
    The level of peak Demand specified in executed agreements or commitments
1
Reference: Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.1(1)(e) and 9.2.1.1(2)(c)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 54: Deep-dive: “Included as base load” (3/6)
If your Large Load
  Has NOT achieved Initial Energization as of July 10, 2026 AND meets end-use customer commitment criteria, including:
    Complete and valid interconnection studies
    Site control demonstrated
    Financial security posted (as determined by TSP/DSP; or $50k/MW if upgrade cost unknown)
    CIAC / interconnection costs paid or secured
    Confirmed end-use demand (direct customer or contracted off-taker)
    DSP/TSP attestation that required disclosures (Section 9.7) are satisfied
Treatment in Transitional Process
  Included as base load and not subject to further reliability assessment
MW Allocation
  Large Loads meeting base load eligibility criteria that are not yet operational will be modeled at the lesser of:
    The level of peak Demand that can be served reliably as indicated in complete and valid existing studies; or
    The level of peak Demand specified in executed agreements or commitments
1
Reference: Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.1(1)(f) and 9.2.1.1(2)(c)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 55: Deep-dive: “Included as base load” (4/6)
If your Large Load
  Was included in and contributed to transmission needs identified in the Permian Basin Reliability Plan (PBRP)
Treatment in Transitional Process
  Included as base load and not subject to further reliability assessment
MW Allocation
  Large Loads included in and contributing to transmission needs identified in the Permian Basin Reliability Plan (PBRP) are modeled at the level of peak Demand reflected in the PBRP study and associated planning assumptions
  The modeled Demand reflects the values included in the approved PBRP study and associated planning assumptions
1
Reference: Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.1(1)(d) and 9.2.1.1(2)(b)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 56: Deep-dive: “Included as base load” (5/6)
If your Large Load
  Is associated with an SB6 net metering application filed on or before March 4, 2026 and meets disclosure requirements (Section 9.7), as attested by the DSP
Treatment in Transitional Process
  Included as base load and not subject to further reliability assessment
MW Allocation
  Large Loads associated with SB6 net-metering applications filed on or before March 4, 2026 are modeled at the level of peak Demand specified in the associated PURA §39.169 proceeding
  The modeled Demand reflects the values submitted and reviewed through the PUCT process
1
Reference: Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.1(1)(g) and 9.2.1.1(2)(d)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 57: Deep-dive: “Included as base load” (6/6)
If your Large Load
  Met qualification requirements for inclusion in the Quarterly Stability Assessment (QSA) on or before May 1, 2026; OR
  Was included in an interim voltage ride-through (IVRT) assessment on or before May 1, 2026
Treatment in Transitional Process
  Included as base load and not subject to further reliability assessment
MW Allocation
  Modeled at the level of peak Demand defined in the 2026 RTP or the most recent Load Commissioning Plan (LCP), whichever is lower
1
Reference: Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.1(1)(c) and 9.2.1.1(2)(b)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 58
If your Large Load
Treatment in Transitional Process
MW Allocation
  Meets one of the following study conditions:
    Meets certain base load eligibility criteria but does not satisfy all required conditions;
    Has existing interconnection studies deemed invalid under Section 9.2.1.4;
    Has received ERCOT approval of a steady state or stability study as described in Section 9.8 and 9.9
  AND meets eligibility requirements under Section 9.2.1.2, including:
    Site control demonstrated
    Financial security posted (as determined by TSP/DSP; or $50k/MW if upgrade cost unknown)
    Required disclosures submitted (Section 9.7, attested by DSP)
    DSP notarized attestation confirming requirements are met
  Studied in Batch Zero
  To be determined during Batch Zero study and reflected in the Load Commissioning Plan (LCP)
Deep-dive: “Studied in Batch Zero”
2
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.2.1.2 and 9.2.1.4
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 59
  ERCOT, in consultation with the Interconnecting DSP or TSP, determines the completeness and validity of existing interconnection studies in accordance with Section 9.2.1.4
    Studies that met the required criteria on or before March 4, 2026 are deemed to be complete and valid without further review under Section 9.2.1.4(3)
  ERCOT uses the evaluation of existing studies to determine whether a Large Load has valid studies for purposes of eligibility under Sections 9.2.1.1 or 9.2.1.2
  Loads included in the 2024 Permian Basin Reliability Plan Study are treated as having complete and valid studies for purposes of Base Load eligibility (Section 9.2.1.1(1)(d))
Complete and valid existing studies
Interconnection Studies – Treatment of complete and valid existing studies
3
Reference: Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.4 (Evaluation of Existing Interconnection Studies)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 60
Key takeaways
Step 1: Date ordered list
Step 2: Sequential Evaluation
RPG A – Loads 1&2 (Apr 15, 2026)
RPG C – Loads 1, 2, 3 (Jun 10, 2026)
LLIS – Load 2 (May 3, 2026)
LLIS – Load 1 (Apr 28, 2026)
LLIS – Load 3 (Jun 22, 2026)
RPG B – Load 1 (May 3, 2026)
LLIS – Load 4 (Jul 8, 2026)
Process for evaluating study validity for loads that qualify after March 4
Loads with a milestone date1 on or before March 4, 2026 that meet the criteria in Section 9.2.1.4(3) are considered to have valid studies with no additional evaluation
ERCOT orders remaining loads sequentially by milestone date to evaluate legacy interconnection studies
  If two loads share the same date, ERCOT applies pathway-based tie-breakers (e.g., RPG-based loads prioritized over LLIS, then submission timing)
Milestone date depends on interconnection pathway:
  RPG loads - date of RPG endorsement
  LLIS loads - date legacy PG 9.4 and 9.5 satisfied
Earlier loads are validated first; subsequent ones remain valid only if previously validated loads are either outside the study area or included in the study
1
1. Milestone date reflects the date the load meets the applicable criteria under Section 9.2.1.4 (e.g., RPG endorsement date or date legacy LLIS and interconnection agreement requirements are satisfied)
RPG A – Loads 1&2 (Apr 15, 2026)
RPG C – Loads 1, 2, 3 (Jun 10, 2026)
LLIS – Load 2 (May 3, 2026)
LLIS – Load 1 (Apr 28, 2026)
LLIS – Load 3 (Jun 22, 2026)
RPG B – Load 1 (May 3, 2026)
LLIS – Load 4 (Jul 8, 2026)
1
✔
✔
✔
✔
✔
LLIS – Load 2 (May 3, 2026)
✘
LLIS – Load 3 (Jun 22, 2026)
✘
RPG
LLIS
Source
ERCOT sequentially evaluates legacy interconnection studies based on timing to determine eligibility for treatment as base load
3
Reference: Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.4 (Evaluation of Existing Interconnection Studies)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 61
If your Large Load
Treatment in Transitional Process
MW Allocation
  Does not meet eligibility criteria under Section 9.2.1.1 (base load) or Section 9.2.1.2 (studied load)
  Not included in Batch Zero
  No MW allocation in Batch Zero
  May seek inclusion in a future batch process if eligibility criteria are met
  Fails to provide required information under Section 9.2.2 on or before the required submission deadline (July 10, 2026; T(D)SP notification by July 24, 2026)
Deep-dive: “Not included in Batch Zero”
4
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.2.1.3 and 9.2.2 (Load Not Included in Batch Zero and Submission Requirements)
XXX Changes/Clarification vs. Apr 14th ROS

## Slide 62
For Large Loads that have not achieved Initial Energization as of July 10, 2026 and qualify for inclusion as base load under Sections 9.2.1.1(1)(e) or (f), the following requirements apply:
Development readiness pathway (Section 9.2.1.1(1)(e)): Large Loads must demonstrate complete and valid studies and physical development progress, evidenced by:
  Complete and valid interconnection studies (per Section 9.2.1.4)
  Interconnecting DSP submits notarized attestation to ERCOT that Section 9.7 disclosure requirements are satisfied (by July 24, 2026)
  Interconnecting DSP/TSP informs ERCOT that the ILLE has attested that:
    Site preparation and construction activities have commenced sufficient to meet the requested Initial Energization date
    All equipment with ≥18-month lead time has been ordered
    A Notice to Proceed (NTP) has been issued for interconnection facilities
    A contract for power sufficient to meet the Load Commissioning Plan (LCP) is in place
  Interconnecting DSP/TSP informs ERCOT that the ILLE has posted financial security for required system upgrades (or $50k/MW fallback if unknown)
  Interconnecting DSP/TSP informs ERCOT that the ILLE has paid or secured CIAC for interconnection facilities
  Interconnecting DSP/TSP confirms that site control has been demonstrated
End-use customer commitment pathway (Section 9.2.1.1(1)(f)): Large Loads must demonstrate complete and valid studies and commercial commitment, evidenced by:
  Complete and valid interconnection studies (per Section 9.2.1.4)
  Interconnecting DSP submits notarized attestation to ERCOT that Section 9.7 disclosure requirements are satisfied (by July 24, 2026)
  Interconnecting DSP/TSP informs ERCOT that the ILLE has attested that the ILLE is the end-use customer or has a signed contract with an end-use customer for service at the interconnection location
  Interconnecting DSP/TSP informs ERCOT that the ILLE has posted financial security for required system upgrades (or $50k/MW fallback if unknown)
  Interconnecting DSP/TSP informs ERCOT that the ILLE has paid or secured CIAC for interconnection facilities
  Interconnecting DSP/TSP confirms that site control has been demonstrated
Demonstrated Development Activity
5
Reference: Batch Zero PGRR145 (April 23, 2026), Section 9.2.1.1(1)(e)–(f) (Baseload Eligibility – Study-Based Categories)
XXX Changes/Clarification vs. Apr 14th ROS
NOTE: These requirements apply only to study-based base load categories. Loads qualifying via QSA/IVRT (Section 9.2.1.1(1)(c)) or Permian Basin Reliability Plan (Section 9.2.1.1(1)(d)) are not subject to additional development readiness or commercial commitment requirements

## Slide 63: Agenda
Timeline and governance recap
Year 6 allocation approach
CLR Discussion
Feedback from PUCT and ERCOT comments
Batch Zero Concepts
Stakeholder Feedback
BYOG Discussion
63

## Slide 64: Comments Filed after April 9th, 2026
Source: ERCOT PGRR145 “Key Documents” section
Date
Company
1. Agentic, Reliant, Eolic, Enchanted Rock, and Cholla filed comments together on Apr 21
Author
April 17th
Kevin Marquardt
April 17th / April 21st
Bill Barnes1
April 21st
Paul Townsend / Michele Richmond
April 21st
Samuel Brandin1
April 21st
Shannon Caraway1
April 21st
Monica Batra-Shrader1
April 21st
Gideon Powell1
April 23nd
Jim Lee
April 23nd
Haynes Strade
April 23nd
Grant Huber

## Slide 65: Agenda
Timeline and governance recap
Year 6 allocation approach
CLR Discussion
Feedback from PUCT and ERCOT comments
Batch Zero Concepts
Stakeholder Feedback
BYOG Discussion

## Slide 66: A Bring Your Own Generation (BYOG) approach should help stakeholders to solve some of the issues raised with the LLI process
Interconnecting Large Load Entities (ILLEs) can co-develop or contract with co-located generation to:
Secure their own path to energization, independent of grid constraints
Align load ramp with generation availability
Reduce reliance on uncertain transmission upgrades
Intent of BYOG
Potential benefits
  For the ILLEs
  Greater certainty on energization timing and scale
  Ability to bypass grid-driven delays and curtailment risk
  For the generators
  Direct, contracted demand from day one
  Improved bankability vs. merchant exposure
  Clear role in solving interconnection bottlenecks
  For the system
  Accelerates capacity build where it is needed most
  Reduces congestion and transmission pressure
  Improves resource adequacy through demand-linked generation

## Slide 67: A coordinated load–generation study framework is required to enable a viable BYOG construct
Generation Interconnection (Normal GINR process – Planning Guide Section 5)
Large Load Interconnection (PGRR145 process – Planning Guide Section 9)
BYOG agreement
Detailed next
Monitoring and compliance
Establishing metering, telemetry, and real-time compliance mechanisms to ensure the facility continuously operates within its defined limits
Operations
Specifying the facility operating envelope (net import/export limits at POI) and dispatch/curtailment behavior for co-located load, generation, and storage
Study treatment
Defining an integrated study approach where load and generation are modeled as a single facility with consistent assumptions across planning and reliability analyses
Registration
Setting the registration model and load commitment requirements, aligning timing, scale, and obligations across generation and load interconnection processes

## Slide 68: Study treatment should separate generation, load allocation and transmission planning while capturing full facility impact
Generation interconnection study
Studies generation independently under standard GINR assumptions to determine interconnection requirements and export capability
Batch Study
Evaluates load as grid-supplied only (co-located generation not counted) to determine firm load allocation based on system capability
Transmission planning study
Models load and generation together as a single facility to assess full system impact under N-1 (single-contingency) conditions (e.g., generator or transmission outages) and drives upgrades based on worst-case conditions
New discussion topic

## Slide 69: Co-located load and generation are governed by three separate ERCOT evaluation processes
Illustrative scheme
ERCOT lens
Description
Output
Batch Study (Load Interconnection)
Evaluates large load interconnections to determine the maximum import (withdrawal) capability under steady state conditions from the ERCOT grid, independent of on-site generation
Withdrawal limits1 and initial load allocation (subject to stability limits from Gen+Load studies)
Source: ERCOT discussions
1. Import (withdrawal) limit applies to total site demand, including co-located load and any storage charging | 2. Where generation and load share a POI, ERCOT/TSP studies may evaluate both independent and combined configurations; combined cases are particularly relevant for stability and system modeling
Focus
1,000MW
~
~
600MW
600MW
ERCOT Grid
1,000MW
~
~
600MW
600MW
1,000MW
~
~
600MW
600MW
Generation Interconnection
Assesses generation to determine export capability and interconnection requirements; co-located load is included in the study when it materially affects system performance (e.g., stability, voltage, operations)2
Maximum export (injection) limits, stability constraints, and interconnection requirements
ERCOT Grid
ERCOT Grid
1,000MW
~
~
600MW
600MW
Transmission planning
Identifies system constraints and determines network upgrades required to reliably support the combined load and generation under normal planning assumptions (e.g., N-1/G-1)
Required transmission upgrades and validation of SLF-exit (full load) conditions for reliable operation in the long-term (post-BYOG) configuration
ERCOT Grid
Final allowable load is determined by withdrawal limits (Batch Study) and may be further constrained by stability limits (Gen+Load studies) Example: Batch study sets a withdrawal limit of 100 MW. Stability studies identify a maximum stable load of 500 MW. Final allowable load = 500 MW, with up to 100 MW from the grid and the remainder supplied by on-site generation. If no stability constraint is identified, load can reach the full 1,000 MW using on-site generation

## Slide 70: PUN with Self-Limited Withdrawal (BYOG) – Operational Model
Interim operation (pre-transmission): BYOG agreement in place
Post-transmission operation: BYOG agreement exited
ERCOT Grid
1,000MW
~
~
600MW
600MW
New 400 MW transmission line
Export (injection): determined by SCED based on available surplus generation and dispatched at the resource level via COP/telemetry
Import (withdrawal): determined through batch study as a maximum withdrawal from the ERCOT grid, independent of co-located generation; total load cannot exceed identified stability limits
Operations: facility operates as a PUN with self-limited withdrawal
  Load is primarily served by on-site generation and must reduce load to remain within the withdrawal limit if generation is unavailable, within defined operational response times (e.g., cycles to seconds)
  Injection is governed by standard generation interconnection limits and SCED dispatch
SLF agreement dissolved and normal operations
Transmission upgrades: determined through ERCOT transmission planning studies, which evaluate the combined load and generation under standard reliability criteria (e.g., N-1 / G-1) to identify required network upgrades
Import and export: governed by standard interconnection limits and system constraints (no BYOG-specific caps); fully dispatchable through SCED subject to study results
Operations: transitions to standard ERCOT operation
  Generation and load treated as independent resources
  No self-limiting withdrawal requirement
  Full participation in market dispatch and planning
Source: ERCOT discussions
ERCOT Grid
1,000MW
~
~
600MW
600MW
Import: max withdrawal limit (Batch study)
Export: available export (SCED dispatch)

## Slide 71: Sequential BYOG interconnection timeline across Batch, Generation, and Transmission planning processes
Source: ERCOT discussions
Batch Study
Generation study
Transmission Planning
LLIS (meeting PG 9.4 and 9.5)
Jan 2027
Mar 2027
Developer commitment period (60 days)
BYOG declaration executed to identify load–generation pairing for studies (pre- PG 6.9 milestone of generation)
July 2026
Case building
Batch Study allocation
~
~
Focus on load only
Upgrade identification
Focus on load and gen
Refinement study
Focus on load and gen
Gen FIS studies
Includes load FIS studies as applicable
(includes load for stability/operability assessment)
Focus on gen only
Focus on load and gen
PRELIMINARY

## Slide 72: Appendix

## Slide 73: Co-located generation enables net export while serving large load under defined operating limits
PUN / SLF
Interconnection model
At steady state (full gen + load)
  COP/ SCED sees 500MW of excess to dispatch
  Reactive support obligation is based on total installed generation capacity at the POI (e.g., full 1000 MW), not net export
  Seen as:
    LSL = 0
    HSL = 500
  at POI or resource
1000 MW – 500 MW = 500 MW
of excess generation
~
~
~
1000 MW CC Generation in model with telemetry
500 MW Large Load Interconnection

## Slide 74: Load energization is limited by withdrawal limits and further enabled by co-located generation
1,000MW
~
~
500MW
500MW
ERCOT Grid
Jan 1: Load built first, energization is allowed up to withdrawal limit
Jun 1: Load increases beyond the withdrawal limit as gen comes online
Dec 1: Full generation online, full load energization
Key takeaways
Load infrastructure is completed ahead of generation
Load is allowed to energize up to the withdrawal limit (e.g., 100 MW)
Load beyond the withdrawal limit requires on-site generation
First generation unit reaches COD
Load can increase above the withdrawal limit as generation becomes available (up to withdrawal + generation, subject to stability limits)
Total load is limited by available generation plus the withdrawal limit (and stability limits)
Second CT reaches COD, completing generation build-out
Load can now fully energize to planned capacity
Facility transitions to steady-state operation
Source: ERCOT discussions
Jan 1
Dec 1
Jun 1
≤100
Load energization is limited by the withdrawal limit; generation availability enables additional load beyond that level
Energization is staged, not binary: load ramps in line with generation commissioning
At all times (including contingencies), load ≤ (available generation + withdrawal limit), subject to stability limits
This sequencing must be explicitly defined in agreements and Planning Guide language
1,000MW
~
~
500MW
500MW
ERCOT Grid
Jan 1
Dec 1
Jun 1
≤600
1,000MW
~
~
500MW
500MW
ERCOT Grid
Jan 1
Dec 1
Jun 1
≤1100
xxx
xxx
Commercial Operation Date
Allowed load energization, MW
Online (available)
100MW withdrawal limit
100MW withdrawal limit
100MW withdrawal limit
ILLUSTRATIVE

## Slide 75: Clarifications on example configurations and their classification as PCLR and/or BYOG
ERCOT Grid
ERCOT Grid
Source: ERCOT discussions
Load and battery, always grid-synchronized
Load and unsynchronized on-site generation
Configuration
  Large load directly connected to ERCOT grid
  Co-located battery electrically synchronous with the grid (AC-coupled or DC behind inverter)
  No ability to island or disconnect from grid in real time
Description
  Load is fully dependent on grid supply at all times
  Battery has no ability to respond to dispatch instructions independently of grid availability
Classification: not a PCLR, might be a BYOG
Configuration
  Large load directly connected to ERCOT grid
  On-site generators not synchronized to grid
  Transfer scheme allows fast disconnection from grid and switching to on-site supply
Description
  Under normal conditions, load consumes from grid
  Under constraint / dispatch, Load can rapidly disconnect from grid and Switch to on-site generation (or curtail)
Classification: PCLR if meeting dispatch instructions (SCED basepoints) and ramping down/up within required timelines
ESR
~
~
~
Generator
Load
Point of interconnection
Switch
~
~
~