## Slide 1: Oncor Electric Delivery Company LLC (Oncor) – Paris Switch to Monticello Switch 345-kV Line Rebuild Project (25RPG026) Prabhu Gnanam Director, Grid Planning Technical Advisory Committee Meeting April 29, 2026

## Slide 2: Overview
Oncor submitted the Paris Switch to Monticello Switch 345-kV Line Rebuild Project (25RPG026) for Reginal Planning Group (RPG) review in July 2025.
  This Tier 1 Oncor proposed project submission was estimated to cost $231.75 million and will not require a Convenience and Necessity (CCN).
  Address post-contingency thermal overloads on the Paris Switch to Monticello Switch 345-kV transmission line in Lamar, Franklin and Titus counties in the North, North Central and East Weather Zones.

## Slide 3: Project Need
ERCOT’s independent review verified reliability planning criteria violations in Lamar, Franklin and Titus counties in the North, North Central and East Weather Zones.
System improvement is needed to meet reliability planning criteria
Contingency Category | Voltage Violations | Thermal Overloads | Unsolved Power Flow
P0: N-0 | None | None | None
P1, P2-1, P7: N-1 | None | None | None
P2, P4, P5 | None | None | None
P3: (G-1+N-1)* | None | 3 | None
P6-2: (X-1+N-1)* | None | 23 | None
Total | None | 26 | None
* See Appendix A for list of G-1 generators and X-1 transformers tested
Notes: *check the # of ctgs

## Slide 4: Project Need (continued)
A minimum deliverability assessment was performed on the base case based on Planning Guide Section 4.1.1.7 and identified additional reliability violations under the minimum deliverability criteria.
System improvement is needed to meet reliability planning criteria
Contingency Category | Voltage Violations | Thermal Overloads | Unsolved Power Flow
P0: N-0 | None | None | None
P1, P2-1, P7: N-1 | None | 2 | None
P2, P4, P5 | None | None | None
P3: (G-1+N-1)* | None | 1 | None
P6-2: (X-1+N-1)* | None | 3 | None
Total | None | 6 | None
* See Appendix A for list of G-1 generators and X-1 transformers tested
Notes: *check the # of ctgs

## Slide 5: Comparison of Project Options
ERCOT analyzed five options and short-listed three options.
Among the three short-listed options, Option 1 addresses all project needs in the study area, meets ERCOT and NERC reliability standards, is the least cost option, and is feasible.
Key Takeaway: Option 1 was selected as the ERCOT preferred option because it addresses all project needs in the study area, meets ERCOT and NERC reliability standards, is the least cost option, and is feasible.
 | Option 1 | Option 2A | Option 3A
Meets ERCOT and NERC Reliability Criteria | Yes | No | Yes
Requires CCN | No | No | No
Cost Estimate* (~$M) | $233.3** | $296.9 | $285.6
Feasible | Yes | Yes | No***
*Cost estimates were provided by Oncor.
** Cost estimate is different from initial project submittal.
*** Infeasible due to expansion restrictions at the existing Paris Switch 345-kV facility.

## Slide 6: Subsynchronous Oscillation (SSO) Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSO screening for Option 1 and found no adverse SSO impacts to the existing and planned generation resources at the time of this study
Key Takeaway: Option 1 did not have an adverse SSO impact at the time of the study.

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations.
  ERCOT concluded that
  Option 1 did not cause any additional congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need
Key Takeaways: Option 1 did not cause any additional congestion in the study area. Potential generation did not impact the preferred option and load scaling did not impact the project need.

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Option 1 to address reliability issues Lamar, Franklin and Titus counties in the North, North Central and East Weather Zones
TSP expect to implement the upgrades May 2027
Estimated Cost: approximately $233.3 million
CCN filling would not be required

## Slide 9: ERCOT Recommendation
Rebuild the existing Paris Switch to Monticello Switch 345-kV transmission line using double-circuit capable structures with one circuit in place with a conductor rated 2,987 MVA or greater, for approximately 49.8 miles; and
Upgrade all terminal and associated equipment to meet or exceed 1,792 MVA.

## Slide 10: Thank you! Questions/Comments?
Gnanaprabhu.Gnanam@ercot.com

## Slide 11: Appendix
Appendix A: G-1 Generators and X-1 Transformers List

## Slide 12: Appendix A: G-1 Generators and X-1 Transformers List
Generator | Transformer
Eiffel Solar | Paris Switch – 345/138-kV
LPCC Unit 1 | Monticello Switch – 345/138-kV
KMCHI Unit 1 | Sulfur Spring Switch – 345/138-kV
Stamped Solar | Valley – 345/138-kV
Samson Solar | 
Rowdy Creek Solar | 
East DC Tie | 
Impact Solar | 
Pineforest Solar |