## Slide 1: Update on the recently published Preliminary Long Term Load Forecast for Years 2026–2032 Nitika Mago Director, Forecasting and Operational Risk Management April 29, 2026 TAC

## Slide 2: Status & Next Steps
ERCOT filed its Preliminary Long-Term Load Forecast (Project No. 58777) using the criteria established in the new Regional Transmission Plan (RTP) Compliance Plan process under 16 Texas Administrative Code (TAC) § 25.370(g).
Transmission Service Providers (TSPs) responses in the recent RFI show continued load growth, driven largely by data centers.
As noted in previous discussions, this Forecast is preliminary and not yet suitable for direct use in studies like the Reliability Assessment, and any other transmission and resource adequacy analysis.
At the Apr 17 Open Meeting, Commissioners agreed that adjustment process under ruler newly enacted 16 TAC § 25.370(e)(2)(B) was appropriate.
Next: Commission Staff, TSPs and ERCOT are coordinating to refine the long-term load forecast for planning use.
Notes: Project No. 58777, Triennial Reliability Assessment for the ERCOT Region under §25.508

## Slide 3: Preliminary Long-Term Load Forecast Peak Demand plus Transmission Service Providers (TSPs) Request for Information (RFI) Submissions
Chart: MW
| 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Forecast | 98087.2959 | 100854.6538 | 102419.7786 | 105382.5226 | 107287.2706 | 108022.9505 | 111317.5323
Forecast + Large Loads + Medium Loads | 112370.9629 | 152881.5018 | 221379.2056 | 278002.5296 | 319649.8186 | 346714.6435 | 367789.8753
Key Takeaway: This forecast should be considered preliminary, and adjustments are expected as the information is further studied, reviewed, and finalized to support its use in planning.
MW= megawatt EV=electric vehicle PV=photovoltaic
The “Forecast” bar represents the core components of the long-term outlook: base economic growth, EV adoption, PV adoption, crypto growth within existing facilities, and known operational Large Load capacity.
The “Forecast + Large Loads + Medium Loads” bar includes the RFI results, which include new Medium (25 MW to 74.9 MW) and Large (75 MW and above) Loads that were reported by TSPs and added to the base forecast.

## Slide 4: TSP Large Load RFI Submissions by Load Type (MW)
Key Takeaway: Data submitted by the Transmission Service Providers (TSPs) in the recent RFIs shows continued growth and interest in Texas and the ERCOT grid, with data centers leading the way.
Load Type | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Cryptocurrency Mining | 2,475 | 3,518 | 5,611 | 7,126 | 7,676 | 8,576 | 9,076
Data Center (non-crypto) | 7,401 | 39,719 | 99,350 | 149,258 | 186,958 | 211,624 | 228,420
Industrial (including Hydrogen/ E-Fuels) | 650 | 1,080 | 1,805 | 2,259 | 2,721 | 2,919 | 2,996
Oil and Gas (Chemical Refining, Production, & Processing) | 917 | 1,214 | 1,650 | 2,017 | 2,187 | 2,347 | 2,507
Total | 11,443 | 45,531 | 108,416 | 160,660 | 199,542 | 225,466 | 242,999
TSP=Transmission Service Provider RFI=Request for Information MW=megawatt