## Slide 1: NOGRR282 and NPRR1308: Frequency and Voltage Ride-Through Requirements for Large Computational Loads Patrick Gravois Principal Operations Engineer TAC Meeting April 29, 2026

## Slide 2: NOGRR282 and NPRR1308 Timeline
ROS vote - April 2 – Passed
Recommend approval of NOGRR282 with ERCOT 3/27/2026 comments revised by ROS
Next Steps
ERCOT seeking vote on NPRR1308 and NOGRR282 at TAC today
ERCOT submitted comments on 4/13/2026
93.1% approval with 8 abstentions; 1 opposing vote (Industrial consumer)
Endorse NPRR1308 as submitted
93.1% approval with 3 abstentions; 1 opposing vote (Industrial consumer)
Changed name from Large Electronic Load (LEL) to Large Computational Load (LCL)
Recommend approval of NPRR1308 with 4/13/2026 ERCOT comments
92.9% approval with 0 abstentions; 1 opposing vote (Industrial consumer)
Target June BOD vote
ERCOT ROS Presentation (technical requirement revisions)
PRS vote - April 15 (NPRR 1308 only) – Passed

## Slide 3: NOGRR282 Comments Received
Comments with Formal ERCOT Response
AEP 12/5/2025 Comments
ERCOT 4/24/2026 Comments
Discussed at DWG
ERCOT responded on 3/11/2026
Tesla 12/18/2025 Comments
ERCOT responded on 1/30/2026
Onward Energy 1/23/2026 Comments
ERCOT responded on 2/16/2026
Data Center Coalition 2/9/2026 Comments
ERCOT responded on 3/11/2026
Data Center Coalition 3/12/2026 Comments
ERCOT responded on 3/27/2026
Comments w/o Formal ERCOT Response
  Texas Blockchain Council 2/18/2026 and 3/18/2026 Comments
    No suggested revisions
    Cannot meet proposed low voltage RT requirements
    Claim RT solutions are neither practical nor economically viable for cryptocurrency Facilities
  Schaper Energy Consultants 3/18/2026 Comments
    Transmission/Market solution requested
    Exemption criteria
    Compliance/Re-Study Risk with PGRR144
  Google 3/31/2026 Comments
    Addressed in ERCOT response to DCC comments
  Address the following comments:
    TIEC 3/25/2026 comments
    Texas Blockchain Council 4/1/2026 comments
    Vistra 4/14/2026 Comments
    Intersect Power 4/1/2026 comments
  Two topics considered in ERCOT comments:
    ERCOT legal authority to adopt grid reliability requirements for Customers
    Exemption criteria of NOGRR282 requirements
NOGRR282 Comment Page

## Slide 4: NOGRR282 Exemption Criteria
LCL Facilities that meet the following criteria are exempt from FRT and VRT requirements in NOGRR282
Operational LCLs and those that have received written approval to energize from ERCOT before November 14, 2025, are exempt
LCLs that meet following criteria are also exempt
LCL has signed interconnection agreement with Transmission Service Provider (TSP), or Generation Resource if co-located, before November 14, 2025
Interconnecting TSP received notice to proceed with construction of required Interconnection Facilities and have received financial security to fund Interconnection Facilities (PG 9.5)
And one of the following were met:
LCL completed and received ERCOT approval for Large Load Interconnection Studies (LLIS) before November 14, 2025
ERCOT received attestation from interconnecting TSP that LLIS were not required, and LCL is expected to energize before 12/31/2026

## Slide 5: Reliability Impact of Changing Exemption Date
At a minimum, 14 GW of LCL Facilities will be exempt
  Includes ~8 GW of LLI LCL projects that were operational or received approval to energize (A2E) before Nov. 14, 2025
  Includes ~6 GW of non-LLI LCL projects that were operational or near operational in Nov. 2025; ERCOT expects this number to increase in 2026
On Nov. 14, 2025, approximately 26 GW of non-operational/ A2E LCL had Steady State and Stability studies approved by ERCOT (met PG 9.4)
  Unknown how much of this 26 GW met PG 9.5 criteria on Nov. 14, 2025
  ERCOT did not track this data before Dec. 15, 2025 (PGRR115 effective date)
  ERCOT reviewing RFIs to determine potential amount of NOGRR282 exempt GW
  Moving exemption date significantly increases percent of this 26 GW to be exempt
Approximately 10 GW have met both PG 9.4 and 9.5 criteria since Nov. 14, 2025
Key Takeaway: Changing the date for exemption criteria to a current or future date greatly increases the amount of LCL Demand that will be exempt from RT requirements, increasing the likelihood, magnitude, and frequency of Load loss events. In addition, increasing the amount of exempted LCLs will increase the need for future curtailment of LCLs during real-time Operations.
Potential Exempt LCL if Exemption Date Moved to Current or Future Date | 
Operational/A2E on 11/14/2025 (LLI projects) | 8 GW
Operational/near Operational on 11/14/2025 (non-LLI projects) | 6 GW
Additional projects with LLIS approved before 11/14/2025 | 26 GW
LLI projects met PG 9.4 and 9.5 after 11/14/2025 to present | 10 GW
Total potential exempt LCLs | 50 GW

## Slide 6: Questions/Comments?

## Slide 7: Appendix: Summary of Changes to Technical Requirements Since March TAC (In Response to DCC Comments)
Increased low frequency threshold from 57.0 Hz to 57.5 Hz
Removed reference to positive sequence voltage in VRT requirements
Increase allowable overcurrent during voltage transient from 125% to 150%
Allowing cooling/mechanical load to trip for V<0.35 pu
Increased low voltage RT threshold from 0.2 pu to 0.35 pu for 0.15 seconds
Allowing load-transfer scheme for multiple fault events with minimum of 6 voltage deviations within 90 seconds
Decrease duration for overvoltage conditions 1.10 < V ≤ 1.20 from 2 seconds to 1 second
Allow LCL to trip for overvoltage condition V>1.08 pu for 5 seconds until 1/1/2028
Allow LCL to reduce consumption to 0 MW with fast recovery of 0.5 seconds or less
Root-Mean-Square Positive Sequence Voltage (p.u. of nominal) | Minimum Ride-Through Time (seconds)
V > 1.20 | May ride-through or trip
1.10 < V ≤ 1.20 | 2.0 1.0
0.90 ≤ V ≤1.10 | continuous
0.80 ≤ V < 0.90 | 2.0
0.50 ≤ V < 0.80 | 0.5
0.20 0.35 ≤ V < 0.50 | 0.25
V < 0.20 0.35 | 0.15