## Slide 1: DWG Report to ROS
Aditi Upadhyay – DWG Chair
May 7th, 2026

## Slide 2: DWG Update
DWG Webex meeting held on 4/16/2026
NOGR282 Updates
"Large Electronic Load" renamed to "Large Computational Load" (LCL) to avoid acronym conflicts and align with NERC terminology. New requirements expected to be enforceable after Board of Directors (BOD) vote in June; exemption date set at November 14, 2025.
In response to DCC and stakeholder feedback, ERCOT increased low-frequency ride-through threshold to 57.5 Hz; Removed positive sequence voltage reference from VRT requirements and raised allowable overcurrent from 125% to 150% for better ride-through
DCC requested exemption for cooling (VFD-driven) loads; ERCOT maintained that all critical cooling must maximize ride-through capability. Exception allowed only for deep voltage sags (<0.35 pu).
Large Load Model Quality Test Updates
The updated load model quality test aims to ensure model accuracy, understanding, and ride-through capability for large electronic (now termed "computational") loads.
The test is aligned with NOGRR 282 requirements, incorporating feedback and recent procedural language updates.
PSCAD model validation required for large computational loads using field measurements; documentation for model version and compiler now recommended
focus remains on aligning with NOGR282 with timing to be finalized expected Q3

## Slide 3: DWG Update, continued
Flat Start Case Build Process Improvements
Proposal to use October cases for dynamic builds to improve data accuracy and reduce mid-cycle rework (with some schedule risk if delayed).
Move to Python-based scripts with variable inputs; encourage annual resubmissions and consolidation of dependent steps to reduce errors
Improve clarity on ERCOT feedback/rejections and introduce structured support (e.g., workshops) for issue resolution
Improve generator spreadsheets (filters, tracking, documentation) and modeling consistency across cases
Next Steps: Stakeholders to provide feedback by April 30 to finalize improvements ahead of next case build cycle
Contingency Modeling and Database Enhancements
Isolate Contingency Proposal: ERCOT seeking feedback on adding node-breaker “isolate” contingencies to SSWG—offers more accurate/simplified modeling for complex systems but depends on high-quality node-breaker data, validation, and tool compatibility; input requested on scope, timeline, and downstream impacts.
Process & Coordination: Cross-group coordination (SSWG,DWG) to ensure changes do not inadvertently affect dynamic studies. Testing and validation across softwares versions (v35/v36) recommended before full roll out.

## Slide 4: DWG Update, continued
2025 Case Quality Metrics- Summary
TRE presented the summary table of case Quality Metrics over multiple years which shows Overall trend improving, but some metrics remain consistently poor (>5% flagged red).
Key challenge: delays from generators in resolving model/data issues. If TSPs struggle to get generator responses, Texas RE can assist
White Paper request: Strong recommendation for NERC to publish a white paper detailing model check parameters and ranges, to aid generators owners in compliance and streamline the model submission/validation process.
MOD-026-2 Standard & Procedure Manual Alignment
MOD-026-2 effective April 1; procedure manual updates ready for approval by year-end to meet the 12-month compliance window.
Ensure DWG and TSP processes align with MOD-026-2, focusing on model verification and validation, especially for inverter-based resources.
Current update focus only on R1 (joint development between TSPs and ERCOT); R2 to R7 are not addressed since they mainly apply to TSP model reviews
Validation criteria for model acceptance/rejection need to be transparent and jointly developed.

## Slide 5: Questions or Feedback?