## Slide 1
Batch Study Details
NPRR1325 (and PGRR145)
May 6, 2026
PRS

## Slide 2: Batch study process for Large Load was introduced to increases outcome certainty and transparency while limiting restudy risk
.
ERCOT action
Non-ERCOT action
Communication point
From the existing single study process…
…to the new batch study process
RPG, QSA
Energization
Batch study: ERCOT compiles applications, studies together as a batch, and allocates load
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
C
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
Single study
Single study (invalidating prior results)
Initial approval
Single study (invalidating prior results)
Initial approval
RPG, QSA
Energization
B
Single study (invalidating prior results)
Single study (invalidating prior results)
Initial approval
Initial approval
Initial approval
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
A
A
A
A
A
C
Frequent restudies required If another project impacts the same transmission zone, all previous studies are invalidated and impacted projects which haven’t yet energized must be restudied
Batching process Every ~6 months, all submitted requests are clustered and studied together; allocated capacity coming out of the study is “reserved” to prevent restudies
B
Restudy loop In the absence of capacity reservation, projects can be repeatedly pulled into restudies as new requests enter the system, delaying approvals and potentially extending timelines by years
Transparent communications Along with the new batch study process, ERCOT is redesigning the study communication process to have clearly defined touchpoints and transparent information handovers

## Slide 3: Batch Zero PGRR145/NPRR1325 timeline and main milestones
Batch Study Kick-Off
PUCT Guidance
Batch Zero filing
PCLR Integration
ERCOT Board Approval
BYOG / WLPUN Integration
Dec 23
ERCOT issues market notice launching Batch Study framework and stakeholder engagement
PUCT guidance to stakeholder-driven process prioritizing durability and market alignment
ERCOT files initial NPRR/ PGRR packages establishing the proposed Batch Zero interconnection framework
ERCOT expands framework to include Provisional Controllable Load Resource (PCLR) construct enabling flexible load participation
ERCOT introduces co-located generation model (WLPUN/BYOG) to enable integrated load and generation interconnection
ERCOT targets Board approval of NPRR145/ PGRR1325 package to finalize Batch Zero framework and implementation
June 1
Feb 6
Mar 4
Apr 17
May 2

## Slide 4: Batch Zero Revision Request Timeline
Forums
ROS (Reliability and Operations Subcommittee)
2026
Q1
Q2
Q3
Feb
Mar
Apr
May
Jun
Jul
Workshop #2 Feb 12
Workshop #4 Mar 10
Workshop #5 Mar 24
Workshop #6 Mar 30
PRS Update 3/11
ROS Vote 5/7
Board Vote 6/1
3/4 ERCOT files Batch Zero Revision Request(s)
7/10 Target effective date of NPRR1325 and PGRR145
Consideration of Batch Zero NPRR 1325 and PGRR 145
LLWG Feb 19
Workshop #3 Feb 26
TAC Vote 5/19-20
6/1 Target Board approval date
Board Meeting 4/20
ROS Update 4/2
Monthly TAC updates
Workshop #7 Apr 9
Special PRS 4/22
Regular TAC 4/29
Special TAC Vote 5/13
PRS Vote 5/6
Monthly LLWG updates
ROS Update (special) 4/14
ROS Update 3/5
ROS Update (special) 4/23
PRS (Protocols Review Subcommittee)
Workshops and working groups
TAC
ERCOT Board
Objective
Align stakeholders on direction/scope following Commission decision
Define the scope, boundaries, and intended role of Batch Zero
File NPRR 1325 for Workshops and PRS review
Endorse NPRR 1325 for advancement to TAC
File PGRR 145 for Workshops and ROS review
Endorse PGRR 145 for advancement to TAC
Review/endorse combined NPRR/PGRR package for Board approval
Close outstanding design and drafting issues, incorporate vetted stakeholder feedback, and finalize Revision Request language for committee approval
Preview structure/governing concepts of Batch Zero PGRR before filing
Note that TAC leadership is involved in considering options to ensure successful review and approval
Source: ERCOT discussions
Regular PRS 4/15
Workshop #8 May 4
4/17 ERCOT files PGRR comments integrating CLR framework
4/30 ERCOT files PGRR comments
5/2 ERCOT files PGRR comments integrating BYOG framework
Workshop #9 TBD

## Slide 5: Reminder of Scope and Priorities
March 4 filings completed for Batch Zero: ERCOT filed the Batch Zero PGRR145 and related NPRR1325 on March 4, initiating the formal governance process and aligning with the May PRS/ROS/TAC sequence and June 1 Board target reflected in the critical path timeline
  March 17 ERCOT comments filed
  April 4 ERCOT comments filed
  April 23 ERCOT comments filed: updated proposal to align with PUCT April 17 Open Meeting guidance
  April 30 ERCOT comments filed: further refined proposal to operationalize framework (standardized financial security methodology, expanded eligibility pathways, enhanced study validation, Year 6/structured study design and allocation mechanics)
ERCOT progressing CLR and BYOG design through parallel comment tracks: Batch Zero comments may include or exclude CLR/BYOG elements, with ERCOT Market Rules managing versioning
  CLR status: April 17 comments filed, formally introducing and detailing PCLR framework (e.g., modular construct, operational treatment, linkage to future market implementation)
  BYOG Status: May 2 comments filed, formally introducing and detailing Withdrawal-Limited PUN (i.e., BYOG) concept
April 29 PUCT Staff comments filed: endorse ERCOT’s April 23 comments; clarify eligibility and study validity, and define financial commitments (non-refundable interconnection costs, tiered refundability for upgrades)

## Slide 6: CLR and BYOG frameworks integrated into Batch Zero filing
PCLR comments
PCLR comments
PCLR comments
BYOG comments
PCLR comments
BYOG comments
March 4: ERCOT files PGRR145 and NPRR1325
Establishes foundational framework for Batch Zero execution and LLI processing
April 17: PCLR introduced as modular enhancement via comments to PGRR145/ NPRR1325
Enables early shaping of controllable load pathway without delaying core filing
May 2: BYOG introduced as modular enhancement via comments to PGRR145 / NPRR1325
Enables integration of generation-backed load pathway without delaying core filing
Path of PGRR145 and NPRR1325 towards governance approval
Key takeaways
Modular approach enables speed without locking design: core framework advanced while PCLR and BYOG are developed in parallel
Convergence toward June Board: PGRR145/NPRR1325, PCLR, and BYOG converge into a complete, minimum viable package for decision-making
Minimum viable, not final design: PCLR and BYOG are introduced as initial concepts, with further refinement expected post June Board
Source: ERCOT discussion
1
2
3
Core Batch Zero framework established
PCLR framework integration
BYOG framework integration
PGRR145
PGRR145
PGRR145
NPRR1325
NPRR1325
NPRR1325

## Slide 7: Scope Mapping to Comments filed by ERCOT
Motion to recommend approval of the RR as amended by the:
Approval options
PGRR145
NPRR 1325
Batch Zero ONLY
(no PCLR, no BYOG)
4/30/26 ERCOT comments w/ desktop edits to remove PCLR
5/1/26 ERCOT comments w/ desktop edits to remove PCLR
1
Batch Zero with PCLR (no BYOG)
4/30/26 ERCOT comments
5/1/26 ERCOT comments
2
Batch Zero with PCLR and BYOG
5/2/26 ERCOT comments
5/2/26 ERCOT comments
3
Link to Workshop #8 from May 4, 2026 with more batch study details

## Slide 8: For ROS- Key updates in both April 30 and May 2 PGRR145 ERCOT comments, including implementation of PUCT guidance (70+ sets of Market Comments filed)
Introduced detailed financial security framework for system upgrades: established a clear methodology for calculating required security (e.g., cost-per-MW from RPG projects or default $50k/MW), including defined acceptable instruments (cash, LOCs, guarantees)
Refined financial responsibility and cost recovery requirements: clarified obligations for direct interconnection costs (CIAC) and system upgrades, with increased flexibility in how costs can be met and inclusion of net metering (PURA 39.169) requirements
Reinstated and clarified site control requirements: explicitly allowed executed purchase and sale agreements (alongside leases/deeds) as valid evidence of site control, clarifying and slightly expanding proof of project readiness
Clarified and expanded eligibility pathways for Batch Zero inclusion: expanded eligibility pathway to include certain loads studied under the interim Large Load interconnection process
Revised Batch Zero Study scope and methodology: refined study scope (full analysis for 2028/2030/2032 and limited for interim years)
Refined minimum load allocation methodology: added 90% minimum for loads under 200 MW
Clarified roles of TSPs and DSPs in interconnection process: added explicit responsibilities across financial security determination, study validation, and data submission to reduce ambiguity in execution
Source: PGRR145 ERCOT Comments, April 30

## Slide 9: For PRS- Scope specifically in NPRR1325 is more limited (1 set of Market Comments filed)
Protocol change Summary:
Batch Zero
  Definitions for Batch Zero, Studies, Interconnecting TSP/DSP
  Batch Zero results submitted for RPG Project Review as single project
PCLR
  Definition of Provisional Controllable Load Resource (PCLR)
  Declaration of Intent to register as PCLR
  SCED modifications for Step 2 with Bid Capping to dispatch PLCR to consume to relieve local congestion
BYOG/WLPUN-
  Defines Withdrawal-Limited Private Use Network (WLPUN)
  Defines Batch Zero allocation and withdrawal limits for WLPUNs
  Creates operating and compliance requirements to ensure WLPUN does not exceed withdrawal limit
  Designation Form for Withdrawal-Limited Private Use Network Designation

## Slide 10: PGRR145 Draft Impact Analysis (NPRR1325 IA points to PGRR145 IA)
Background
ERCOT previously posted an Impact Analysis for PGRR145 on March 4 showing the budget/staffing impacts as TBD
Once PGRR145 language is voted on, ERCOT will file a Revised IA with updated version with approved language
Draft Impacts
  Summary
  PCLR: Project between $300k and $400k
    Estimated project duration: 8 to 12 months
  Batch Zero and WLPUN: Annual Recurring Operations & Maintenance Budget Cost: $3.6M - $4.5M (19.0 Full-Time Employees)
  Ongoing operational impacts to the following departments:
Grid Planning (9.0 FTEs Effort)
• Dynamic Studies (8.9 FTEs Effort)
• Planning Model Administration (1.0 FTE Effort)
ERCOT has assessed its ability to absorb the ongoing efforts of this PGRR with current staff and concluded the need for 18 FTEs

## Slide 11: APPENDIX
PCLR Design Details from prior Workshops
BYOG Design Details from prior Workshops

## Slide 12: Overview of Provisional Controllable Load Resource (PCLR)
  Large Load participates as a Provisional Controllable Load Resource (PCLR), where a portion of load is firm (LPC) and the remaining load is flexible and subject to dispatch
  The PCLR framework enables Load to consume more energy in unconstrained hours of the day ahead of full transmission build-out, with firm MW defined in the Batch Zero study and non-firm MW managed through SCED
Description
Details
  Split between firm and flexible load defined through the Load Commissioning Plan (LCP) (LPC = firm MW; remaining load operates as PCLR)
  PCLR participates as dispatchable demand and must follow SCED basepoints within its operating range
  Full requested load is studied in Batch Zero, with transmission upgrades identified to transition PCLR to firm service over time
Provisional Controllable Load Resource (PCLR)
Point of interconnection
Load
Illustrative scheme

## Slide 13: Provisional CLRs – Definition1
New Resource Type: ‘Provisional CLR’
A Large Load electing to operate as a CLR post-Batch Zero, with LPC defined in study and commitment via Form
What’s different?
PCLR load bids can be ‘capped’ to mitigate transmission constraints identified in SCED
PCLR bids are capped dynamically (“last-in-line/just-in-time”) in each run of SCED to a price that will just allow SCED to resolve a constraint
PCLRs are not eligible to provide Ancillary Services
Submits CLR Energy Bid Curve  bid-to-buy prices between Low Power Consumption (LPC) and Maximum Power Consumption (MPC) – same as any other CLR
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.2.2.1, 9.3.2.1, 9.4.1, 9.5.3, and 9.6.1 (Provisional Controllable Load Resource design, study treatment, and operations)

## Slide 14: Provisional CLRs – Structure of Revision Requests1
Will consist of a comments to existing PGRR145 and companion NPRR1325
Modular structure adds to PGRR145 and NPRR1325
  Example – Section 9.2.2.1, Additional Information Required for Provisional Controllable Load Resources (PCLRs) compliments Section 9.2.2 as written in PGRR145
This structure will allow the PCLR concepts to move forward in parallel with PGRR145 and NPRR1325 if possible, without interfering with the core Batch Zero language
Language related to PCLR approval to energize and PCLR bid capping in SCED is intended to remain grey-boxed until implementation of NPRR1188 and until system changes for the bid capping are in place
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 15: PCLR Language – Foundational Concepts1
Allocation in Batch Zero
Registration Requirements
Ensure Real-Time Dispatch
Load is assessed through the Batch Zero process in the same manner as load requesting firm service for steady state and at full consumption for stability
The level of firm load that can be reliably served becomes the maximum Low Power Consumption (LPC) value for the PCLR in real-time (instead of a hard limit)
The remaining requested load amount is approved contingent on qualification as a PCLR
Intention to register as a PCLR must be declared prior to the start of Batch Zero
Once allocated in Batch Zero, the load must register and qualify as PCLR before it may consume above initial limits
Load must remain registered as a PCLR until an exit date identified in Batch Zero
Obligation to remain a PCLR transfers to subsequent owners of the Large Load
Like traditional CLRs, PCLRs must follow SCED basepoints when consuming energy2
Dynamic bid capping logic is added to ensure the PCLR will be dispatched rather than allowing the constraint to violate
1. Design and NPRR/PGRR language still under internal review and may change prior to filing | 2. On implementation of NPRR1188

## Slide 16: Provisional Controllable Load Resources (PCLRs) in Batch Zero1
ERCOT validates completion of all steps prior to granting Approval to Energize
8
QSE establishes required ICCP telemetry points
7
RE coordinates with ERCOT to establish metering and submit CLR parameters via RIOO
6
ILLE registers with ERCOT as a Resource Entity (RE) and designates a QSE
5
ERCOT studies the full load amount in the Batch Zero Refinement Study
4
ILLE submits updated Declaration to accept allocation amounts2
3
ERCOT studies PCLR in Batch Zero
2
Submission of Declaration and required information to ERCOT
(by July 24)
1
Must be done before non-firm load may energize
May be done in parallel with QSA
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
2. Failure to submit Form W removes project from the refinement story
Detailed next

## Slide 17: Post–Batch Zero, ILLE must elect path via Form W to retain position and proceed
Context
After Batch Zero results, each ILLE receives allocated LPC (firm) and MPC (total) values
To proceed, ILLE must submit Form W Part B election by deadline
Failure to elect leads to project being removed from Refinement study and loses queue position
Description
Option
Accept ERCOT-defined LPC and MPC values without modification
Maintains ability to consume above LPC, subject to PCLR qualification, dispatch, and bid capping
Accept PCLR as is
1
Elect to proceed as PCLR but reduce LPC and/or MPC below awarded levels
Provides flexibility while aligning with project readiness or infrastructure constraints
Accept PCLR with reduced values
2
Withdraw from PCLR and accept LPC values as firm load (with optional reduction), eliminating ability to exceed LPC
Withdraw PCLR, retain firm load
3
Withdraw from process
Decline participation and exit Batch Zero entirely
Project is removed from Refinement Study and must re-enter through a future process
4
Form W Part B election is binding and determines eligibility for Refinement Study and eventual energization. Failure to submit Form W Part B results in removal from Batch Zero

## Slide 18: Provision CLR (PCLR) – Dynamic Bid Capping Process
PUBLIC
1
SCED₋₁ (Previous Run)
After each SCED run, generate a fresh list of transmission constraints whose Shadow Price ≥ 90% of Max Shadow Price:
Constraint₁₂₃
Constraint₂₃₄
Constraint₃₄₅
Constraint₄₅₆
⚡ Shadow price threshold triggered
Match
2
SCEDcurrent (Before Step 2)
Compare the matching list against all active constraints in the current SCED run:
Constraint₂₃₄
Constraint₄₅₆
Constraint₆₇₈
Constraint₇₈₉
✔ 2 constraints match — evaluate PCLRs
Cap
3
SCED Step 2 (Bid Capped)
−0.02
Shift Factor Rule
Only PCLRs with a Shift Factor ≤ −0.02 on a matching constraint are eligible for bid capping
CAP
Bid Cap Applied
The PCLR's Energy Bid Curve is capped at the Adjusted Bid Cap (ABC) value before Step 2 executes
✓
Adjusted Bid Cap Formula:
ABC = Step 1 System Lambda − max ( MaxShadowPrice × ShiftFactor ) − $0.01 / MWh
Only applied where PCLR Shift Factor ≤ −0.02 | Constraint must appear in prior-run trigger list | No standard market mitigation applies to Energy Bid Curves

## Slide 19: A Bring Your Own Generation (BYOG) approach should help stakeholders to solve some of the issues raised with the LLI process
Interconnecting Large Load Entities (ILLEs) can co-develop or contract with co-located generation to:
Secure their own path to energization, independent of grid constraints
Align load ramp with generation availability
Reduce reliance on uncertain transmission upgrades
Intent of BYOG
Potential benefits
  For the ILLEs
  Greater certainty on energization timing and scale
  Ability to bypass grid-driven delays and curtailment risk
  For the generators
  Direct, contracted demand from day one
  Improved bankability vs. merchant exposure
  Clear role in solving interconnection bottlenecks
  For the system
  Accelerates capacity build where it is needed most
  Reduces congestion and transmission pressure
  Improves resource adequacy through demand-linked generation

## Slide 20: A coordinated load–generation study framework is required to enable a viable BYOG construct
Generation Interconnection (Normal GINR process – Planning Guide Section 5)
Large Load Interconnection (PGRR145 process – Planning Guide Section 9)
BYOG agreement
Detailed next
Monitoring and compliance
Establishing metering, telemetry, and real-time compliance mechanisms to ensure the facility continuously operates within its defined limits
Operations
Specifying the facility operating envelope (net import/export limits at POI) and dispatch/curtailment behavior for co-located load, generation, and storage
Study treatment
Defining an integrated study approach where load and generation are modeled as a single facility with consistent assumptions across planning and reliability analyses
Registration
Setting the registration model and load commitment requirements, aligning timing, scale, and obligations across generation and load interconnection processes

## Slide 21: Operational monitoring and control are required to ensure reliable WLPUN integration in Batch Zero
WLPUN
Key operational considerations
~
~
~
Generator
Load
Point of interconnection
ERCOT Grid
1,000MW
~
~
600MW
600MW
Import: max withdrawal limit (Batch study)
Export: available export (SCED dispatch)
Withdrawal limits (net) and stability limits (gross gen / gross load) must be monitored and enforced
Net and gross telemetry available; additional load telemetry can be requested by ERCOT
Additional control room tools and displays required to support real-time operations

## Slide 22: Study treatment should separate generation, load allocation and transmission planning while capturing full facility impact
Generation interconnection study
Studies generation independently under standard GINR assumptions to determine interconnection requirements and export capability
Batch Study
Evaluates load as grid-supplied only (co-located generation not counted) to determine firm load allocation based on system capability
Transmission planning study
Models load and generation together as a single facility to assess full system impact under N-1 (single-contingency) conditions (e.g., generator or transmission outages) and drives upgrades based on worst-case conditions
New discussion topic

## Slide 23: Co-located load and generation are governed by three separate ERCOT evaluation processes
Illustrative scheme
ERCOT lens
Description
Output
Batch Study (Load Interconnection)
Evaluates large load interconnections to determine the maximum import (withdrawal) capability under steady state conditions from the ERCOT grid, independent of on-site generation
Withdrawal limits1 and initial load allocation (subject to stability limits from Gen+Load studies)
Source: ERCOT discussions
1. Import (withdrawal) limit applies to total site demand, including co-located load and any storage charging | 2. Where generation and load share a POI, ERCOT/TSP studies may evaluate both independent and combined configurations; combined cases are particularly relevant for stability and system modeling
Focus
1,000MW
~
~
600MW
600MW
ERCOT Grid
1,000MW
~
~
600MW
600MW
1,000MW
~
~
600MW
600MW
Generation Interconnection
Assesses generation to determine export capability and interconnection requirements; co-located load is included in the study when it materially affects system performance (e.g., stability, voltage, operations)2
Maximum export (injection) limits, stability constraints, and interconnection requirements
ERCOT Grid
ERCOT Grid
1,000MW
~
~
600MW
600MW
Transmission planning
Identifies system constraints and determines network upgrades required to reliably support the combined load and generation under normal planning assumptions (e.g., N-1/G-1)
Required transmission upgrades and validation of SLF-exit (full load) conditions for reliable operation in the long-term (post-BYOG) configuration
ERCOT Grid
Final allowable load is determined by withdrawal limits (Batch Study) and may be further constrained by stability limits (Gen+Load studies) Example: Batch study sets a withdrawal limit of 100 MW. Stability studies identify a maximum stable load of 500 MW. Final allowable load = 500 MW, with up to 100 MW from the grid and the remainder supplied by on-site generation. If no stability constraint is identified, load can reach the full 1,000 MW using on-site generation

## Slide 24: PUN with Self-Limited Withdrawal (BYOG) – Operational Model
Interim operation (pre-transmission): BYOG agreement in place
Post-transmission operation: BYOG agreement exited
ERCOT Grid
1,000MW
~
~
600MW
600MW
New 400 MW transmission line
Export (injection): determined by SCED based on available surplus generation and dispatched at the resource level via COP/telemetry
Import (withdrawal): determined through batch study as a maximum withdrawal from the ERCOT grid, independent of co-located generation; total load cannot exceed identified stability limits
Operations: facility operates as a PUN with self-limited withdrawal
  Load is primarily served by on-site generation and must reduce load to remain within the withdrawal limit if generation is unavailable, within defined operational response times (e.g., cycles to seconds)
  Injection is governed by standard generation interconnection limits and SCED dispatch
SLF agreement dissolved and normal operations
Transmission upgrades: determined through ERCOT transmission planning studies, which evaluate the combined load and generation under standard reliability criteria (e.g., N-1 / G-1) to identify required network upgrades
Import and export: governed by standard interconnection limits and system constraints (no BYOG-specific caps); fully dispatchable through SCED subject to study results
Operations: transitions to standard ERCOT operation
  Generation and load treated as independent resources
  No self-limiting withdrawal requirement
  Full participation in market dispatch and planning
Source: ERCOT discussions
ERCOT Grid
1,000MW
~
~
600MW
600MW
Import: max withdrawal limit (Batch study)
Export: available export (SCED dispatch)

## Slide 25: Sequential BYOG interconnection timeline across Batch, Generation, and Transmission planning processes
Source: ERCOT discussions
Batch Study
Generation study
Transmission Planning
LLIS (meeting Batch Zero eligibility)
Jan 2027
Mar 2027
Developer commitment period (60 days)
BYOG declaration executed to identify load–generation pairing for studies (pre- PG 6.9 milestone of generation)
July 2026
Case building
Batch Study
~
~
Focus on load only
Upgrade identification
Focus on load and gen
Refinement study
Focus on load and gen
Gen FIS studies
Includes load FIS studies as applicable
(includes load for stability/operability assessment)
Focus on gen only
Focus on load and gen
Output: withdrawal limit
Output: stability limit (if any)
Total load allocation = min (Requested Load, Stability Limit – if any)

## Slide 26: ERCOT will need future NPRR on PUN Telemetry and RUC Requirements