## Slide 1
Batch Study Details
PGRR145 and NPRR1325
May 13, 2026
TAC

## Slide 2: Batch study process for Large Load was introduced to increases outcome certainty and transparency while limiting restudy risk
.
ERCOT action
Non-ERCOT action
Communication point
From the existing single study process…
…to the new batch study process
RPG, QSA
Energization
Batch study: ERCOT compiles applications, studies together as a batch, and allocates load
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
C
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
Single study
Single study (invalidating prior results)
Initial approval
Single study (invalidating prior results)
Initial approval
RPG, QSA
Energization
B
Single study (invalidating prior results)
Single study (invalidating prior results)
Initial approval
Initial approval
Initial approval
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
A
A
A
A
A
C
Frequent restudies required If another project impacts the same transmission zone, all previous studies are invalidated and impacted projects which haven’t yet energized must be restudied
Batching process Every ~6 months, all submitted requests are clustered and studied together; allocated capacity coming out of the study is “reserved” to prevent restudies
B
Restudy loop In the absence of capacity reservation, projects can be repeatedly pulled into restudies as new requests enter the system, delaying approvals and potentially extending timelines by years
Transparent communications Along with the new batch study process, ERCOT is redesigning the study communication process to have clearly defined touchpoints and transparent information handovers

## Slide 3: Batch Zero PGRR145/NPRR1325 timeline and main milestones
Batch Study Kick-Off
Dec 23
ERCOT issues market notice launching Batch Study framework and stakeholder engagement
ERCOT Board Approval
ERCOT targets Board approval of NPRR145/ PGRR1325 package to finalize Batch Zero framework and implementation
June 1
PUCT Guidance
PUCT guidance to stakeholder-driven process prioritizing durability and market alignment
Feb 6
Batch Zero filing
ERCOT files initial NPRR/ PGRR packages establishing the proposed Batch Zero interconnection framework
Mar 4
PCLR Integration
ERCOT expands framework to include Provisional Controllable Load Resource (PCLR) construct enabling flexible load participation
Apr 17
BYOG / WLPUN Integration
ERCOT introduces co-located generation model (WLPUN/BYOG) to enable integrated load and generation interconnection
May 2

## Slide 4: Batch Zero Revision Request Timeline
Forums
ROS (Reliability and Operations Subcommittee)
2026
Q1
Q2
Q3
Feb
Mar
Apr
May
Jun
Jul
Workshop #2 Feb 12
Workshop #4 Mar 10
Workshop #5 Mar 24
Workshop #6 Mar 30
PRS Update 3/11
ROS Vote 5/7
Board Vote 6/1
3/4 ERCOT files Batch Zero Revision Request(s)
7/10 Target effective date of NPRR1325 and PGRR145
Consideration of Batch Zero NPRR 1325 and PGRR 145
LLWG Feb 19
Workshop #3 Feb 26
TAC Vote 5/19-20
6/1 Target Board approval date
Board Meeting 4/20
ROS Update 4/2
Monthly TAC updates
Workshop #7 Apr 9
Special PRS 4/22
Regular TAC 4/29
Special TAC Vote 5/13
PRS Vote 5/6
Monthly LLWG updates
ROS Update (special) 4/14
ROS Update 3/5
ROS Update (special) 4/23
PRS (Protocols Review Subcommittee)
Workshops and working groups
TAC
ERCOT Board
Objective
Align stakeholders on direction/scope following Commission decision
Define the scope, boundaries, and intended role of Batch Zero
File NPRR 1325 for Workshops and PRS review
Endorse NPRR 1325 for advancement to TAC
File PGRR 145 for Workshops and ROS review
Endorse PGRR 145 for advancement to TAC
Review/endorse combined NPRR/PGRR package for Board approval
Close outstanding design and drafting issues, incorporate vetted stakeholder feedback, and finalize Revision Request language for committee approval
Preview structure/governing concepts of Batch Zero PGRR before filing
Note that TAC leadership is involved in considering options to ensure successful review and approval
Source: ERCOT discussions
Regular PRS 4/15
Workshop #8 May 4
4/17 ERCOT files PGRR comments integrating CLR framework
4/30 ERCOT files PGRR comments
5/2 ERCOT files PGRR comments integrating BYOG framework
Workshop #9 TBD

## Slide 5: Reminder of Scope and Priorities
March 4 filings completed for Batch Zero: ERCOT filed the Batch Zero PGRR145 and related NPRR1325 on March 4, initiating the formal governance process and aligning with the May PRS/ROS/TAC sequence and June 1 Board target reflected in the critical path timeline
  March 17 ERCOT comments filed
  April 4 ERCOT comments filed
  April 23 ERCOT comments filed: updated proposal to align with PUCT April 17 Open Meeting guidance
  April 30 ERCOT comments filed: further refined proposal to operationalize framework (standardized financial security methodology, expanded eligibility pathways, enhanced study validation, Year 6/structured study design and allocation mechanics)
  May 11 ERCOT comments filed: refined Batch Zero proposal to align with PUCT May 6 guidance and incorporate stakeholder feedback, including updates to eligibility, attestations, prerequisite timing, load classification rules (base vs. studied), financial security, study assumptions/years, and disclosure requirements
ERCOT progressing CLR and BYOG design through parallel comment tracks: Batch Zero comments may include or exclude CLR/BYOG elements, with ERCOT Market Rules managing versioning (Details of CLR/BYOG in Appendix)
  CLR status: April 17 comments filed, formally introducing and detailing PCLR framework (e.g., modular construct, operational treatment, linkage to future market implementation)
  BYOG Status: May 2 comments filed, formally introducing and detailing Withdrawal-Limited PUN (i.e., BYOG) concept
April 29 PUCT Staff comments filed: endorse ERCOT’s April 23 comments; clarify eligibility and study validity, and define financial commitments (non-refundable interconnection costs, tiered refundability for upgrades)
May 6 PUC Staff comments filed: recommended targeted adjustments to Batch Zero eligibility criteria, removing power supply contract requirements and clarifying stage-specific project maturity signals
Main updates

## Slide 6: ERCOT position statements to assist in TAC discussion
ERCOT offers these positions as transparency for TAC discussion:
ERCOT does not support any changes that are in conflict with PUCT 58481 and 59142-related guidance1
  Power/tenant contracts
  Site control
  Financial commitment
  Refundability
ERCOT does not support moving the March 4, 2026 baseload eligibility date any later2
  Allowing in more baseload increases risk of load shed in areas
  Other eligibility paths are defined in PGRR145 to achieve baseload treatment
ERCOT does not support having different eligibility criteria for Large Loads opting for PCLR or BYOG frameworks
Generally speaking, ERCOT does not support further expansion of eligibility
  Numerous proposals to expand eligibility for more recent RPG projects2
1. Aligned with PUCT Guidance from April 17 Open Meeting, PUCT Staff Memo from April 12, and PUCT Staff comments to PGRR145 from April 29 and May 6 | 2. Aligned with PUCT Guidance from April 17 Open Meeting
Source: April17 PUCT Open Meeting, April 12 PUCT Staff Memo, April 29 PUCT Staff Comments to PGRR145, May 6 PUCT Staff filing on PUCT Project No. 59142

## Slide 7: PGRR145 Draft Impact Analysis (NPRR1325 IA points to PGRR145 IA)
Background
ERCOT previously posted an Impact Analysis for PGRR145 on March 4 showing the budget/staffing impacts as TBD
ERCOT has continued refining scope through multiple comment iterations (April–May), including May 11 updates aligned with PUCT guidance
Impact Analysis Summary
  Summary
  PCLR: Project between $300k and $400k
    Estimated project duration: 8 to 12 months
  Batch Zero and WLPUN: Annual Recurring Operations & Maintenance Budget Cost: $3.6M - $4.5M (19.0 Full-Time Employees)
  Ongoing operational impacts to the following departments:
Grid Planning (9.0 FTEs Effort)
• Dynamic Studies (8.0 FTEs Effort)
• Planning Model Administration (1.0 FTE Effort)
ERCOT has assessed its ability to absorb the ongoing efforts of this PGRR with current staff and concluded the need for 18 FTEs

## Slide 8: Key updates from May 6 PUCT Staff filing on Project No. 59142 and May 7 PUCT Open Meeting
On May 6, PUCT Staff published a filing for Project No. 59142 (Review of ERCOT’s Interconnection Processes for Large Loads – Staff Memorandum on Batch Study Process) refining maturity criteria and removing premature requirements
  Removed power supply contracts from “Advancing / Base Load” criteria (too early for most projects)
  Replaced with stage-specific readiness signals, including:
    Advancing (Base Load): tenant contract (demand signal)
    Developing (Base Load): contracts with general contractor and substation contractor and evidence of zoning approval
On May 7 PUCT Open Meeting:
  ERCOT presented progress since the last Open Meeting, highlighting key design choices (bookend vs. rollover study approaches) and outlining remaining stakeholder feedback and open questions (e.g., treatment of RPG projects and entry criteria)
  Commissioners asked questions on the trade-offs between bookend vs. rollover approach, but emphasized that the ultimate choice should be guided by stakeholder preference
  PUCT Staff clarified that changes to the maturity criteria were driven by stakeholder feedback, specifically removing the power contract requirement and replacing it with more achievable indicators
Source: April 7 PUCT Open Meeting, May 6 PUCT Staff filing on PUCT Project No. 59142

## Slide 9: Key updates in May 11 PGRR145 ERCOT comments, including implementation of PUCT guidance
Updated eligibility framework to align with PUCT May 7 guidance: revised Section 9.2.1.1 criteria and gating requirements to better reflect Commission direction and ensure only viable projects qualify for Batch Zero
Clarified attestation requirements and consequences: defined required attestations (site control, contracts, equipment orders, etc.) and removal from Batch Zero for false or deficient attestations
Refined base load vs. studied load treatment: clarified modeling assumptions and enabled certain base load (with valid studies and phased ramp) to be reflected as studied load in earlier years
Clarified study validity criteria: further defined what constitutes a “complete and valid” study and limited reliance on RPG-only studies going forward
Clarified financial security application: maintained standardized methodology ($/MW) and added process for loads failing base load criteria to transition to studied load with security
Added participation guardrails: required single classification (standalone, PCLR, or WLPUN) and clarified that PCLR/WLPUN treatment applies only to studied load
Refined study scope, assumptions, and timing: clarified study years (2028, 2030, 2032), modeling inputs, and additional study conditions
Expanded disclosure and readiness requirements: clarified Texas-only duplicate request disclosure, commissioning plan alignment, and project maturity expectations
90+ set of market comments received
Source: PGRR145 ERCOT Comments, May 11

## Slide 10: Key stakeholder feedback not adopted and ERCOT rationale
Source: PGRR145 ERCOT Comments, May 11
Rejected inclusion of post–Dec 15, 2025 RPG-based loads as “studied load”: RPG submissions after implementation of the new process do not qualify as valid interconnection studies and should not be used for Batch Zero eligibility
Did not allow unreviewed TSP studies to qualify for inclusion: studies must be approved/ endorsed by ERCOT or accepted by RPG, not simply performed by a TSP, since RPG studies assess transmission need
Rejected proposals to prioritize RPG-based loads over LLIS-based loads: maintained ERCOT approval and study completion as the objective, uniform criterion for study validity rather than giving preference to specific study pathways
Did not expand Batch Zero to include additional ~40 GW of RPG-associated load: risk of exceeding reasonable study bounds, with total modeled load already exceeding ~180 GW vs. ~111 GW baseline forecast
Rejected allowing ineligible loads to enter as studied load via PCLR/WLPUN election: this would effectively open Batch Zero to 400+ GW of requests, significantly increasing study complexity and jeopardizing timelines
Did not rely on PCLR/WLPUN designation as a screening mechanism: flexible load treatment does not substitute for prior study validation or system impact analysis
Declined to revise Planning Guide language for TPIT data concerns: committed to an ad hoc TPIT update with TSPs to incorporate latest transmission information without formal rule changes

## Slide 11: APPENDIX
PCLR Design Details from prior Workshops
BYOG Design Details from prior Workshops
Details on non-linearity of studying 2032

## Slide 12: Overview of Provisional Controllable Load Resource (PCLR)
  Large Load participates as a Provisional Controllable Load Resource (PCLR), where a portion of load is firm (LPC) and the remaining load is flexible and subject to dispatch
  The PCLR framework enables Load to consume more energy in unconstrained hours of the day ahead of full transmission build-out, with firm MW defined in the Batch Zero study and non-firm MW managed through SCED
Description
Details
  Split between firm and flexible load defined through the Load Commissioning Plan (LCP) (LPC = firm MW; remaining load operates as PCLR)
  PCLR participates as dispatchable demand and must follow SCED basepoints within its operating range
  Full requested load is studied in Batch Zero, with transmission upgrades identified to transition PCLR to firm service over time
Provisional Controllable Load Resource (PCLR)
Point of interconnection
Load
Illustrative scheme

## Slide 13: Provisional CLRs – Definition1
New Resource Type: ‘Provisional CLR’
A Large Load electing to operate as a CLR post-Batch Zero, with LPC defined in study and commitment via Form
What’s different?
PCLR load bids can be ‘capped’ to mitigate transmission constraints identified in SCED
PCLR bids are capped dynamically (“last-in-line/just-in-time”) in each run of SCED to a price that will just allow SCED to resolve a constraint
PCLRs are not eligible to provide Ancillary Services
Submits CLR Energy Bid Curve  bid-to-buy prices between Low Power Consumption (LPC) and Maximum Power Consumption (MPC) – same as any other CLR
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.2.2.1, 9.3.2.1, 9.4.1, 9.5.3, and 9.6.1 (Provisional Controllable Load Resource design, study treatment, and operations)

## Slide 14: Provisional CLRs – Structure of Revision Requests1
Will consist of a comments to existing PGRR145 and companion NPRR1325
Modular structure adds to PGRR145 and NPRR1325
  Example – Section 9.2.2.1, Additional Information Required for Provisional Controllable Load Resources (PCLRs) compliments Section 9.2.2 as written in PGRR145
This structure will allow the PCLR concepts to move forward in parallel with PGRR145 and NPRR1325 if possible, without interfering with the core Batch Zero language
Language related to PCLR approval to energize and PCLR bid capping in SCED is intended to remain grey-boxed until implementation of NPRR1188 and until system changes for the bid capping are in place
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 15: PCLR Language – Foundational Concepts1
Allocation in Batch Zero
Registration Requirements
Ensure Real-Time Dispatch
Load is assessed through the Batch Zero process in the same manner as load requesting firm service for steady state and at full consumption for stability
The level of firm load that can be reliably served becomes the maximum Low Power Consumption (LPC) value for the PCLR in real-time (instead of a hard limit)
The remaining requested load amount is approved contingent on qualification as a PCLR
Intention to register as a PCLR must be declared prior to the start of Batch Zero
Once allocated in Batch Zero, the load must register and qualify as PCLR before it may consume above initial limits
Load must remain registered as a PCLR until an exit date identified in Batch Zero
Obligation to remain a PCLR transfers to subsequent owners of the Large Load
Like traditional CLRs, PCLRs must follow SCED basepoints when consuming energy2
Dynamic bid capping logic is added to ensure the PCLR will be dispatched rather than allowing the constraint to violate
1. Design and NPRR/PGRR language still under internal review and may change prior to filing | 2. On implementation of NPRR1188

## Slide 16: Provisional Controllable Load Resources (PCLRs) in Batch Zero1
ERCOT validates completion of all steps prior to granting Approval to Energize
8
QSE establishes required ICCP telemetry points
7
RE coordinates with ERCOT to establish metering and submit CLR parameters via RIOO
6
ILLE registers with ERCOT as a Resource Entity (RE) and designates a QSE
5
ERCOT studies the full load amount in the Batch Zero Refinement Study
4
ILLE submits updated Declaration to accept allocation amounts2
3
ERCOT studies PCLR in Batch Zero
2
Submission of Declaration and required information to ERCOT
(by July 24)
1
Must be done before non-firm load may energize
May be done in parallel with QSA
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
2. Failure to submit Form W removes project from the refinement story
Detailed next

## Slide 17: Post–Batch Zero, ILLE must elect path via Form W to retain position and proceed
Context
After Batch Zero results, each ILLE receives allocated LPC (firm) and MPC (total) values
To proceed, ILLE must submit Form W Part B election by deadline
Failure to elect leads to project being removed from Refinement study and loses queue position
Description
Option
Accept ERCOT-defined LPC and MPC values without modification
Maintains ability to consume above LPC, subject to PCLR qualification, dispatch, and bid capping
Accept PCLR as is
1
Elect to proceed as PCLR but reduce LPC and/or MPC below awarded levels
Provides flexibility while aligning with project readiness or infrastructure constraints
Accept PCLR with reduced values
2
Withdraw from PCLR and accept LPC values as firm load (with optional reduction), eliminating ability to exceed LPC
Withdraw PCLR, retain firm load
3
Withdraw from process
Decline participation and exit Batch Zero entirely
Project is removed from Refinement Study and must re-enter through a future process
4
Form W Part B election is binding and determines eligibility for Refinement Study and eventual energization. Failure to submit Form W Part B results in removal from Batch Zero

## Slide 18: Provision CLR (PCLR) – Dynamic Bid Capping Process
PUBLIC
1
SCED₋₁ (Previous Run)
After each SCED run, generate a fresh list of transmission constraints whose Shadow Price ≥ 90% of Max Shadow Price:
Constraint₁₂₃
Constraint₂₃₄
Constraint₃₄₅
Constraint₄₅₆
⚡ Shadow price threshold triggered
Match
2
SCEDcurrent (Before Step 2)
Compare the matching list against all active constraints in the current SCED run:
Constraint₂₃₄
Constraint₄₅₆
Constraint₆₇₈
Constraint₇₈₉
✔ 2 constraints match — evaluate PCLRs
Cap
3
SCED Step 2 (Bid Capped)
−0.02
Shift Factor Rule
Only PCLRs with a Shift Factor ≤ −0.02 on a matching constraint are eligible for bid capping
CAP
Bid Cap Applied
The PCLR's Energy Bid Curve is capped at the Adjusted Bid Cap (ABC) value before Step 2 executes
✓
Adjusted Bid Cap Formula:
ABC = Step 1 System Lambda − max ( MaxShadowPrice × ShiftFactor ) − $0.01 / MWh
Only applied where PCLR Shift Factor ≤ −0.02 | Constraint must appear in prior-run trigger list | No standard market mitigation applies to Energy Bid Curves

## Slide 19: A Bring Your Own Generation (BYOG) approach should help stakeholders to solve some of the issues raised with the LLI process
Interconnecting Large Load Entities (ILLEs) can co-develop or contract with co-located generation to:
Secure their own path to energization, independent of grid constraints
Align load ramp with generation availability
Reduce reliance on uncertain transmission upgrades
Intent of BYOG
Potential benefits
  For the ILLEs
  Greater certainty on energization timing and scale
  Ability to bypass grid-driven delays and curtailment risk
  For the generators
  Direct, contracted demand from day one
  Improved bankability vs. merchant exposure
  Clear role in solving interconnection bottlenecks
  For the system
  Accelerates capacity build where it is needed most
  Reduces congestion and transmission pressure
  Improves resource adequacy through demand-linked generation

## Slide 20: A coordinated load–generation study framework is required to enable a viable BYOG construct
Generation Interconnection (Normal GINR process – Planning Guide Section 5)
Large Load Interconnection (PGRR145 process – Planning Guide Section 9)
BYOG agreement
Detailed next
Monitoring and compliance
Establishing metering, telemetry, and real-time compliance mechanisms to ensure the facility continuously operates within its defined limits
Operations
Specifying the facility operating envelope (net import/export limits at POI) and dispatch/curtailment behavior for co-located load, generation, and storage
Study treatment
Defining an integrated study approach where load and generation are modeled as a single facility with consistent assumptions across planning and reliability analyses
Registration
Setting the registration model and load commitment requirements, aligning timing, scale, and obligations across generation and load interconnection processes

## Slide 21: Operational monitoring and control are required to ensure reliable WLPUN integration in Batch Zero
WLPUN
Key operational considerations
~
~
~
Generator
Load
Point of interconnection
ERCOT Grid
1,000MW
~
~
600MW
600MW
Import: max withdrawal limit (Batch study)
Export: available export (SCED dispatch)
Withdrawal limits (net) and stability limits (gross gen / gross load) must be monitored and enforced
Net and gross telemetry available; additional load telemetry can be requested by ERCOT
Additional control room tools and displays required to support real-time operations

## Slide 22: Study treatment should separate generation, load allocation and transmission planning while capturing full facility impact
Generation interconnection study
Studies generation independently under standard GINR assumptions to determine interconnection requirements and export capability
Batch Study
Evaluates load as grid-supplied only (co-located generation not counted) to determine firm load allocation based on system capability
Transmission planning study
Models load and generation together as a single facility to assess full system impact under N-1 (single-contingency) conditions (e.g., generator or transmission outages) and drives upgrades based on worst-case conditions
New discussion topic

## Slide 23: Co-located load and generation are governed by three separate ERCOT evaluation processes
Illustrative scheme
ERCOT lens
Description
Output
Batch Study (Load Interconnection)
Evaluates large load interconnections to determine the maximum import (withdrawal) capability under steady state conditions from the ERCOT grid, independent of on-site generation
Withdrawal limits1 and initial load allocation (subject to stability limits from Gen+Load studies)
Source: ERCOT discussions
1. Import (withdrawal) limit applies to total site demand, including co-located load and any storage charging | 2. Where generation and load share a POI, ERCOT/TSP studies may evaluate both independent and combined configurations; combined cases are particularly relevant for stability and system modeling
Focus
1,000MW
~
~
600MW
600MW
ERCOT Grid
1,000MW
~
~
600MW
600MW
1,000MW
~
~
600MW
600MW
Generation Interconnection
Assesses generation to determine export capability and interconnection requirements; co-located load is included in the study when it materially affects system performance (e.g., stability, voltage, operations)2
Maximum export (injection) limits, stability constraints, and interconnection requirements
ERCOT Grid
ERCOT Grid
1,000MW
~
~
600MW
600MW
Transmission planning
Identifies system constraints and determines network upgrades required to reliably support the combined load and generation under normal planning assumptions (e.g., N-1/G-1)
Required transmission upgrades and validation of SLF-exit (full load) conditions for reliable operation in the long-term (post-BYOG) configuration
ERCOT Grid
Final allowable load is determined by withdrawal limits (Batch Study) and may be further constrained by stability limits (Gen+Load studies) Example: Batch study sets a withdrawal limit of 100 MW. Stability studies identify a maximum stable load of 500 MW. Final allowable load = 500 MW, with up to 100 MW from the grid and the remainder supplied by on-site generation. If no stability constraint is identified, load can reach the full 1,000 MW using on-site generation

## Slide 24: PUN with Self-Limited Withdrawal (BYOG) – Operational Model
Interim operation (pre-transmission): BYOG agreement in place
Post-transmission operation: BYOG agreement exited
ERCOT Grid
1,000MW
~
~
600MW
600MW
New 400 MW transmission line
Export (injection): determined by SCED based on available surplus generation and dispatched at the resource level via COP/telemetry
Import (withdrawal): determined through batch study as a maximum withdrawal from the ERCOT grid, independent of co-located generation; total load cannot exceed identified stability limits
Operations: facility operates as a PUN with self-limited withdrawal
  Load is primarily served by on-site generation and must reduce load to remain within the withdrawal limit if generation is unavailable, within defined operational response times (e.g., cycles to seconds)
  Injection is governed by standard generation interconnection limits and SCED dispatch
SLF agreement dissolved and normal operations
Transmission upgrades: determined through ERCOT transmission planning studies, which evaluate the combined load and generation under standard reliability criteria (e.g., N-1 / G-1) to identify required network upgrades
Import and export: governed by standard interconnection limits and system constraints (no BYOG-specific caps); fully dispatchable through SCED subject to study results
Operations: transitions to standard ERCOT operation
  Generation and load treated as independent resources
  No self-limiting withdrawal requirement
  Full participation in market dispatch and planning
Source: ERCOT discussions
ERCOT Grid
1,000MW
~
~
600MW
600MW
Import: max withdrawal limit (Batch study)
Export: available export (SCED dispatch)

## Slide 25: Sequential BYOG interconnection timeline across Batch, Generation, and Transmission planning processes
Source: ERCOT discussions
Batch Study
Generation study
Transmission Planning
LLIS (meeting Batch Zero eligibility)
Jan 2027
Mar 2027
Developer commitment period (60 days)
BYOG declaration executed to identify load–generation pairing for studies (pre- PG 6.9 milestone of generation)
July 2026
Case building
Batch Study
~
~
Focus on load only
Upgrade identification
Focus on load and gen
Refinement study
Focus on load and gen
Gen FIS studies
Includes load FIS studies as applicable
(includes load for stability/operability assessment)
Focus on gen only
Focus on load and gen
Output: withdrawal limit
Output: stability limit (if any)
Total load allocation = min (Requested Load, Stability Limit – if any)

## Slide 26: ERCOT will need future NPRR on PUN Telemetry and RUC Requirements

## Slide 27: April 30th comments/approach: proposed “bookend” allocation Approach addresses developer ‘gap year’ concerns at the cost of extending the Batch Zero timeline
Example: 1,000 MW data center requiring full capacity by 2032
Chart: 
 | 300 | 300 | 500 | 500 | 1000
 | 100 | 200
2027
2028
2029
2030
2031
2032
400
700
Illustrative ramp schedule and allocation methodology by year, MW
Key highlights
Not studied: based on existing system capacity (no upgrades)
Fully studied (all cases)
Allocated with incremental transmission
Fully studied (all cases)
Allocated with incremental transmission
Fully studied (all cases)
Studied
Allocated
Adjusted “bookend” study approach: fully study 2028, 2030, and 2032, while allocating 2029 and 2031 using anchored transmission plans
Mitigates key developer concerns on “gap years” by avoiding zero-allocation outcomes:
  Improves project economics and bankability by providing interim MW visibility, reducing delayed revenues/underutilization
  Anchors allocation on years with major planned transmission additions (e.g., backbone upgrades)
Trade-off: additional 10 weeks of steady-state analysis, delaying Batch Zero results publication and potentially pushing the start of Batch 1
Enablers
Early TSP involvement at study kickoff, with a shared 2032 system case
Parallel development of transmission solutions and cost estimates
Centralized ERCOT coordination, consolidating TSP inputs into a single plan
Advantages
Delivers an actionable 2032 transmission plan within Batch Zero timeline, with full TSPs engagement and avoiding reliance on future cycles
Provides full 2027-2032 visibility for customer decisions
Reduces complexity and rework

## Slide 28: Batch Zero Adjusted Timelines Comparison
Activity
RPG Comment period and Board approval
Developer Commitment Deadline
Steady State Analysis (15 weeks)
Case Build (13 weeks)
Stability Screening Study + Final Report (16 weeks)
FAC-002 Stability + Batch Refinement Study ((14 weeks)
Aug
Sep
Oct
Nov
Jul
Dec
Feb
Mar
Apr
May
Jun
Aug
Oct
Jan
Dec
Nov
Sep
Jul
2026
2027
Old Batch Zero Timeline
Scenario
Potential Batch 1 start date (case building)
Activity getting extended
Batch Zero report published
RPG Comment period and Board approval
Developer Commitment Deadline
Steady State Analysis (15 weeks)
Case Build (13 weeks)
Stability Screening Study + Final Report (16 weeks)
FAC-002 Stability + Batch Refinement Study ((14 weeks)
“Rollover” Batch Zero Timeline – if needed
Extra 30 days for developer commitment
RPG Comment period and Board approval
Developer Commitment Deadline
Steady State Analysis (25 weeks)
Case Build (13 weeks)
Stability Screening Study + Final Report (16 weeks)
FAC-002 Stability + Batch Refinement Study ((14 weeks)
April 30th comments Batch Zero Timeline
Extra 30 days for developer commitment
Extra 10 weeks for steady state analysis

## Slide 29: Alternative option: "Rollover" approach
Old PGRR145 Approach
“Rollover” approach to subsequent batch
Example: 1,000 MW data center requiring full capacity by Year 6
Years 1-5
Request studied in Batch Zero: initial MWs allocated based on system capability; transmission constraints and required upgrades identified
Request studied in Batch Zero: initial MWs allocated based on system capability; transmission constraints and required upgrades identified
Considerations
Provides certainty by guaranteeing full MWs by Year 6
Creates a potential step-change in MWs between Years 5 and 6, with limited time to develop required transmission
Full MW allocation is aligned with identified transmission upgrades
Requires financial commitment for partial MWs without clear visibility on timing or certainty of full MW delivery
Year 6
Full MW automatically allocated based on Batch Zero results; transmission solutions further defined in the 2027 RTP
Full MW not committed in Batch Zero; additional MWs studied and allocated through a subsequent Batch 1 process
Chart: 
 | 0 | 100 | 450 | 600 | 600 | 1000
2027
2028
2029
2030
2031
2032
0
Illustrative ramp schedule, MW
Chart: 
 | 0 | 100 | 450 | 600 | 600 | 600
 | 400
2027
2028
2029
2030
2031
TBD
2032
0
Automatically set at requested peak Demand
TBD: additional MWs studied in next batch and allocated based on available capacity
Preferred alternative option

## Slide 30: Study effort scales non-linearly: later years require disproportionate effort
12 months (+24 weeks)
Timeline
6 months
8.5 months (+10 weeks)
Source: ERCOT discussions
Year
Key takeaways
Study effort is heavily back-loaded: final year (2032) requires disproportionately more effort than earlier years across all approaches
The “rollover” approach focuses on studying 2028–2031 within ~6 months, deliberately leaving 2032 to Batch 1 to avoid including the most effort-intensive year within the baseline timeline
The “bookend” approach includes 2032 within a limited ~10-week extension by assessing 2032 requirements early and identifying transmission elements that can be accelerated to support earlier years (e.g., 2029–2031), while trading depth in intermediate years (2029, 2031)
The “study all” approach maintains full depth across all years but requires a material timeline extension (~12 months total), reflecting the non-linear increase in effort
Total effort, % of “Rollover” approach
Year treatment
Effort, %
“Rollover” approach
1
100%
Year treatment
Effort, %
“Bookend” approach
2
140%
Fully studied
Fully studied
Fully studied
2028
10%
10%
10%
2030
Fully studied
20%
Fully studied
20%
Fully studied
20%
2032
Not studied (left to Batch 1)
-
Fully studied
100%
Fully studied
100%
Year treatment
Effort, %
“Study all” approach
2029
Fully studied
15%
Load allocation only studied
5%
15%
Fully studied
Fully studied
Load allocation only studied
2031
55%
5%
55%
Fully studied
3
200%
1
2
3
ILLUSTRATIVE
Detailed next

## Slide 31: 2032 is the primary driver of non-linear effort across scenarios
Source: ERCOT Board Meeting supporting materials, Feb 9-10; 9.1 System Planning and Weatherization Update
Key takeaways
Historical RTP data shows non-linear (exponential-like) scaling, with projects per GW almost doubling in recent years (from ~0.6 in 2016-22 to ~1.2 in 2023-25)
Complexity is driven not only by load, but also by system interactions:
  Location of generation and load (distance, congestion, zonal interactions)
  Need to model generation resources beyond ERCOT’s existing queue
Unlike RTP, studies cannot rely on placeholders or partial analysis and require fully resolved system configurations across all years
Study effort is constrained by limited parallelization, creating a plateau even with additional resources or tools (not expected to be in place for Batch Zero)
Fully studying 2032 requires significant coordination with TSPs to determine full load to be served, validate transmission feasibility and upgrades and identify opportunities to accelerate solutions into earlier years (e.g., 2030–2031)
Chart: 
| 89 | 89 | 85 | 89 | 93 | 92 | 94 | 111 | 152 | 159
 | 40 | 60 | 38 | 56 | 50 | 67 | 89 | 173 | 145 | 192
80
85
90
95
100
105
110
115
120
125
130
135
140
145
150
155
160
75
0
50
100
150
200
Total RTP Reliability Projects Proposed
2016
2017
2018
2019
2020
2021
2022
2023
2024
2025
Peak Load Level Studied in RTP
2016-2025 RTP summary by year, # of projects (Y-axis), GW (X-axis)
~0.6
~1.2
Average # of projects per GW
xx