## Slide 1: Oncor Electric Delivery Company LLC (Oncor) and LCRA Transmission Services Corporation (LCRA TSC) – Muscovy and Voss Lake 345/138-kV Project (25RPG009) Prabhu Gnanam Director, Grid Planning Technical Advisory Committee Meeting May 19, 2026

## Slide 2: Overview
Oncor Electric Delivery Company LLC (Oncor) and LCRA Transmission Services Corporation (LCRA TSC) submitted the Muscovy and Voss Lake 345/138-kV Project (25RPG009) for Reginal Planning Group (RPG) review in April 2025.
  The Tier 1 Oncor and LCRA TSC proposed project submission was estimated to cost $381.83 million and will require a Convenience and Necessity (CCN).
  Addresses post-contingency and thermal overloads and voltage violations in the Williamson and Milam counties.

## Slide 3: Project Need
ERCOT’s independent review verified reliability planning criteria violations in Bell, Milam, Williamson, Bastrop, Travis, Hays, Caldwell and Robertson counties in the North Central, South Central and East Weather Zones.
ERCOT Independent Review (EIR) was separated into two Phases
  Phase 1 of the EIR addresses the violations identified in Study Area 1 – North of Hutto
  Phase 2 of the EIR addresses the violations identified in Study Area 2 – South of Hutto
    The evaluation of Phase 2 will be conducted after the completion of Phase 1
System improvement is needed to meet reliability planning criteria in Study area 1 – North of Hutto.
* See Appendix A for the list of G-1 generators and X-1 transformers being tested
Contingency Category | Thermal Overloads | Voltage Violations | Unsolved Power Flow
P0: N-0 | 2 | 7 | None
P1, P2-1, P7: N-1 | 10 | 97 | 2
P2-2, P2-3, P4, P5 | 3 | None | 3
P3: (G-1+N-1)* | 7 | 6 | 1
P6-2: (X-1+N-1)* | 6 | 13 | None

## Slide 4: Project Evolution
Oncor and LCRA TSC submitted the Muscovy and Voss Lake 345/138-kV Project to address post-contingency and thermal overloads and voltage violations in Williamson and Milam counties due to significant and rapid load growth. (Approximately $388.94 million)
ERCOT’s review of the study area identified reliability issues not addressed by the initial RPG submission. ERCOT’s 2024 and 2025 Regional Transmission Plans (RTP) identified upgrades to address most of the additional reliability issues in Study Area 1 – North of Hutto. These upgrades were included as part of the Oncor Set 1 North Central and South Central Texas Reliability Project (25RPG041) and were included in the option development for the phase 1 EIR. (Approximately $603.33 million)
Due to the increase of Large Loads modeled in the study case, additional upgrades were identified to resolve the remaining reliability issues identified in Study Area 1 – North of Hutto. (Approximately $465.20 million)

## Slide 5: Comparison of Project Options
ERCOT analyzed ten options and short-listed four options.
Among the four short-listed options, Option 7A addresses all project needs, meets ERCOT and NERC reliability criteria, improves long-term load-serving capability, supports future load growth in the area and is feasible for construction.
Key Takeaway: Option 7A was selected as the ERCOT preferred option because it addresses all project needs in the study area, meets ERCOT and NERC reliability standards, improves long-term load-serving capability, and facilitates future loads.
Contingency Category | Option 3 | Option 4A | Option 5 | Option 7A
Met ERCOT and NERC Reliability Criteria | Yes | Yes | Yes | Yes
Improves Long-Term Load-Serving Capability (~MW) | 350 | 550 | 450 | 1000
Supports additional new contracted Loads | No | Yes | No | Yes
CCN Required (~miles) | Yes (56.2) | Yes (105.4) | Yes (95.7) | Yes (97.3)
Construction Feasibility (Based on TSP assessment) | Yes | Yes | Yes | Yes
Capital Cost Estimates (~$B) | 1.272 | 1.549 | 1.336 | 1.457
Estimated ISD (Year) | LCRA TSC: August 2031 Oncor: May 2031 | LCRA TSC: August 2031 Oncor: December 2032 | LCRA TSC: August 2031 Oncor: December 2032 | LCRA TSC: December 2031 Oncor: December 2031

## Slide 6: Subsynchronous Oscillation (SSO) Assessment
SSO Assessment Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSO screening for Option 7A and found no adverse SSO impacts to the existing and planned generation resources at the time of this study
Key Takeaway: Option 7A did not have an adverse SSO impact at the time of the study.

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations.
  ERCOT concluded that:
  Option 7A did not cause any additional congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need
Key Takeaways: Option 7A did not cause any additional congestion in the study area. Potential generation did not impact the preferred option and load scaling did not impact the project need.

## Slide 8: Overall Project Summary
  Approximately 159 circuit-miles of new 345-kV transmission lines;
  Approximately 100.8 circuit-miles of rebuilt 345-kV transmission lines;
  Approximately 45.4 circuit-miles of rebuilt 138-kV transmission lines;
  Construct three (3) new 345/138-kV Stations;
  Construct one (1) new 345-kV Station;
  Install five (5) new 345/138-kV auto transformers; and
  Install sized capacitors totaling 110.4 MVAr
Detailed list of upgrades are in Appendix B

## Slide 9: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Option 7A to address reliability issues in Bell, Milam, Williamson and Robertson counties in the North Central, South Central and East Weather Zones.
TSPs expect to implement the upgrades by December 2031
Estimated Cost: approximately $1.457 billion
  Updated CPS’s initial cost estimate (approximately $388.94 million);
  A subset of upgrades identified in Oncor Set 1 North Central and South Central Texas Reliability Project (25RPG041) were included as part of this project (approximately $603.33 million); and
  Approximately $465.20 million in upgrades to address additional reliability violations under peak load conditions.
  CCN filling would be required for:
  Construct a new 345-kV double-circuit transmission line from Limmer Substation (LCRA TSC) to Muscovy Switch with a normal and emergency ratings of at least 2,987 MVA or greater, for approximately 4 miles;
  Construct a new 345-kV transmission line from Voss Lake Switch to Walleye Creek Switch with a normal and emergency ratings of at least 2,987 MVA or greater on double-circuit structures with one circuit installed initially, for approximately 2 miles;

## Slide 10: ERCOT Recommendation (cont.)
  Construct a new 345-kV double-circuit transmission line from Muscovy Switch to Voss Lake Switch with a normal and emergency ratings of at least 2,987 MVA or greater, for approximately 25 miles;
  Construct two new 345-kV single-circuit transmission lines from Tower Switch to Knob Creek Switch on independent, single-circuit structures with a normal and emergency rating 2,987 MVA, for approximately 1.2 miles;
  Rebuild the Salado Switch to Tower Switch 345-kV transmission line using double-circuit capable structures with two circuits installed with normal and emergency rating 2,987 MVA, for approximately 12.4 miles;
  Rebuild the Tower Switch to Temple Switch 345-kV transmission line using double-circuit capable structures with two circuits installed with normal and emergency rating 2,987 MVA, for approximately 2.9 miles;
  Rebuild Hutto to Limmer 345-kV double-circuit transmission line on separate structures, for approximately 3 miles;
  Construct a new 345-kV double-circuit transmission line from Salado to Gabriel Substation with normal and emergency rating 2,987 MVA, for approximately 28.5 miles; and
  Construct a new 345-kV double-circuit transmission line from Gabriel Substation to Hutto Switch with normal and emergency rating 2,987 MVA, for approximately 12.6 miles.

## Slide 11: ERCOT Recommendation

## Slide 12: Thank you! Questions/Comments?
Gnanaprabhu.Gnanam@ercot.com

## Slide 13: Appendix
Appendix A: G-1 Generators and X-1 Transformers List
Appendix B: ERCOT Recommendation

## Slide 14: Appendix A: G-1 Generators and X-1 Transformers List
Generator | Transformer
Bastrop Energy Center | Sandow – Ckt 1 345/138-kV
Giga Energy Storage | Hutto – Ckt 1 345/138-kV
East Backland Solar | Teal – Ckt 1 345/138-kV
Garfield Generator | Austrop –Ckt 1 345/138-kV
LostPines Generator | Dunlap –Ckt 1 345/138-kV
 | Gilleland Creek –Ckt 1 345/138-kV
 | Muscovy–Ckt 1 345/138-kV
 | Lytton–Ckt 1 345/138-kV
 | Salado–Ckt 1 345/138-kV
 | Temple–Ckt 1 345/138-kV
 | Temple Pecan–Ckt 1 345/138-kV
 | Voss Lake–Ckt 1 345/138-kV

## Slide 15: Appendix B: ERCOT Recommendation
  Establish the new Muscovy 345/138-kV Switch by installing ten 345-kV, 5000 A and twelve 138-kV, 3200 A breakers in a breaker-and-a-half bus arrangement, for approximately 3.3 miles east of the 345-kV Limmer Substation (LCRA TSC) and 138-kV Teal Switch (Oncor);
  Install two 345/138-kV autotransformers with normal rating of 700 MVA and emergency rating of 750 MVA;
  Install three 36.8 MVAr capacitor banks;
  Ensure all line terminal and associated equipment elements are rated to meet or exceed 5000 A for 345-kV and 3200 A for 138-kV;
  Construct a new 345-kV double-circuit transmission line which will require a CCN from Limmer Substation (LCRA TSC) to Muscovy Switch with a normal and emergency ratings of at least 2,987 MVA or greater, for approximately 4 miles;
  Construct a loop of the existing Teal Switch to Pintail Switch 138-kV double-circuit transmission line with a normal and emergency ratings of at least 614 MVA into the new Muscovy 138-kV Switch, for approximately 0.1 miles;

## Slide 16: Appendix B: ERCOT Recommendation (cont.)
  Establish the new Voss Lake 345/138-kV Switch by installing ten 345-kV, 5000 A and nine 138-kV, 3200 A breakers in a breaker-and-a-half bus arrangement, for approximately 1.9 miles north of Sandow 345/138-kV Switch;
  Install one 345/138-kV autotransformer with normal ratings of at least 700 MVA and emergency ratings of at least 750 MVA;
  Ensure all line terminal and associated equipment elements are rated to meet or exceed 5000 A for 345-kV and 3200 A for 138-kV;
  Construct a loop of the existing Sandow Switch to Bell County East Switch 345-kV double-circuit transmission line into the Voss Lake 345- kV Switch with a normal and emergency ratings of at least 2,987 MVA or greater, for approximately 0.1 miles;
  Construct a loop of the existing Sandow Switch to Temple Switch 138-kV transmission line into the Voss Lake 138-kV Switch with a normal and emergency ratings of at least 614 MVA or greater, for approximately 0.1 miles;
  Construct a loop of the existing Sandow Switch to Minerva Switch 138-kV transmission line into the Voss Lake 138-kV Switch with a normal and emergency ratings of at least 614 MVA or greater, for approximately 0.1 miles;

## Slide 17: Appendix B: ERCOT Recommendation (cont.)
  Construct a new 345-kV transmission line which will require a CCN from Voss Lake Switch to Walleye Creek Switch with a normal and emergency ratings of at least 2,987 MVA or greater on double-circuit structures with one circuit installed initially, for approximately 2 miles;
  Construct a new 345-kV double-circuit transmission line which will require a CCN from Muscovy Switch to Voss Lake Switch with a normal and emergency ratings of at least 2,987 MVA or greater, for approximately 25 miles;
  Install terminal equipment in existing bays at Limmer Substation to connect both circuits of the new 345-kV double-circuit transmission line to Muscovy Switch, including two 345-kV, 5000 A circuit breakers and associated equipment. All associated terminal equipment will have a minimum rating of 5000 A;

## Slide 18: Appendix B: ERCOT Recommendation (cont.)
  Establish the Tower 345-kV Switch by installing ten 345-kV, 5000 A circuit breakers in a breaker-and-a-half bus arrangement;
  Loop the existing Salado Switch to Knob Creek Switch 345-kV transmission line into Tower 345-kV Switch to create the new Salado Switch to Tower Switch 345-kV transmission line, for approximately 12.4 miles and Tower Switch to Temple Switch 345-kV transmission line, for approximately 2.9 miles;
  Construct two new 345-kV single-circuit transmission lines from Tower Switch to Knob Creek Switch on independent, single-circuit structures with a normal and emergency rating 2,987 MVA, for approximately 1.2 miles, this upgrade will require a CCN;
  Rebuild the Salado Switch to Tower Switch 345-kV transmission line using double-circuit capable structures with two circuits installed with normal and emergency rating 2,987 MVA, for approximately 12.4 miles, this upgrade will require a CCN;
  Rebuild the Tower Switch to Temple Switch 345-kV transmission line using double-circuit capable structures with two circuits installed with normal and emergency rating 2,987 MVA, for approximately 2.9 miles, this upgrade will require a CCN;
  Ensure all associated terminal equipment to meet or exceed 5000 A (2,987 MVA);

## Slide 19: Appendix B: ERCOT Recommendation (cont.)
  Rebuild the Bell County East Switch to Voss Lake Switch 345-kV double-circuit transmission line with a normal and emergency rating of 1,912 MVA, for approximately 29.6 miles (due to the existing 3200 A terminal equipment, this transmission line will be operated at a normal and emergency rating 1,912 MVA), and ensure all associated terminal equipment to meet or exceed 3200 A (1,912 MVA);
  Rebuild the Minerva Switch to Robertson 138-kV transmission line using double-circuit capable structures with one circuit installed with a normal and emergency rating of 614 MVA, for approximately 29.1 miles, and ensure all associated terminal equipment to meet or exceed 3200 A (764 MVA);
  Rebuild the Temple Switch to Tinroof 138-kV transmission line using double-circuit capable structures with one circuit installed with a normal and emergency rating of 614 MVA, for approximately 1.85 miles, and ensure all associated terminal equipment to meet or exceed 3200 A (764 MVA);

## Slide 20: Appendix B: ERCOT Recommendation (cont.)
  Rebuild the Bell County East Switch to Little Pond 345-kV transmission line with a normal and emergency rating of 1,912 MVA, for approximately 17.75 miles (due to the existing 3200 A terminal equipment, this transmission line will be operated at a normal and emergency rating 1,912 MVA), and ensure all associated terminal equipment to meet or exceed 3200 A (1,912 MVA);
  Rebuild the Bell County East Switch to Brangus 345-kV transmission line with a normal and emergency rating of 1,912 MVA, for approximately 8.8 miles (due to the existing 3200 A terminal equipment, this transmission line will be operated at a normal and emergency rating 1,912 MVA), and ensure all associated terminal equipment to meet or exceed 3200 A (1,912 MVA);
  Rebuild the Temple Switch to Temple Pecan Creek Switch 345-kV double-circuit transmission line with a normal and emergency rating 2,987 MVA, on separate structures, for approximately 4.5 miles, and ensure all associated terminal equipment to meet or exceed 5000 A (2,987 MVA);

## Slide 21: Appendix B: ERCOT Recommendation (cont.)
  Rebuild the Hutto to Round Rock Northeast 138-kV transmission line using double-circuit capable structures with normal and emergency rating of 614 MVA, for approximately 5.3 miles, and ensure all associated terminal equipment to meet or exceed 3200 A (764 MVA);
  Rebuild Hutto to Limmer 345-kV double-circuit transmission line on separate structures, for approximately 3 miles, this upgrade will require a CCN;
  Establish a new 345-kV yard at Gabriel Substation by installing ten 345-kV, 5000 A circuit breakers in a breaker-and-a-half bus arrangement;
  Install two 345/138-kV autotransformers with normal rating of 672 MVA and emergency rating of 739 MVA;
  Construct a new 345-kV double-circuit transmission line from Salado to Gabriel Substation with normal and emergency rating 2,987 MVA, for approximately 28.5 miles, this upgrade will require a CCN;
  Construct a new 345-kV double-circuit transmission line from Gabriel Substation to Hutto Switch with normal and emergency rating 2,987 MVA, for approximately 12.6 miles, this upgrade will require a CCN;
  Rebuild the Gabriel to Rivery 138-kV transmission line using double-circuit capable structures with one circuit installed with normal and emergency rating 614 MVA, for approximately 2.5 miles, and ensure all associated terminal equipment to meet or exceed 3000 A (717 MVA); and

## Slide 22: Appendix B: ERCOT Recommendation (cont.)
  Rebuild the Gabriel to Glasscock 138-kV transmission line using double-circuit capable structures with one circuit installed with normal and emergency rating 614 MVA, for approximately 6.6 miles, and ensure all associated terminal equipment to meet or exceed 3000 A (717 MVA).