## Slide 1: CPS Energy (CPS) – Combined Reactive Power Planning Project & Helotes 345/138-kV Switching Station and Autotransformer Addition at Eastside Switching Station Project (25RPG013 & 25RPG017) Prabhu Gnanam Director, Grid Planning Technical Advisory Committee Meeting May 19, 2026

## Slide 2: Overview
CPS Energy (CPS) submitted the Reactive Power Planning Project (25RPG013) for Electric Reliability Council of Texas’ (ERCOT) Regional Planning Group (RPG) review in May 2025.
CPS submitted the Helotes 345/138-kV Switching Station and Autotransformer Addition at Eastside Switching Station Project (25RPG017) for ERCOT RPG review in June 2025.
  The Tier 1 CPS proposed project submission 25RPG013 was estimated to cost $116.5 million and will not require a Convenience and Necessity (CCN).
  The Tier 1 CPS proposed project submission 25RPG017 was estimated to cost $110.0 million and will not require a Convenience and Necessity (CCN).
  Address reliability issues in Bexar County in the South Central Weather Zone.
  ERCOT conducted a single ERCOT Independent Review (EIR) for these two projects.

## Slide 3: Project Need
ERCOT’s independent review verified reliability planning criteria violations in Bexar County in the South Central Weather Zone.
System improvement is needed to meet reliability planning criteria
Contingency Category | Voltage Violations | Thermal Overloads | Unsolved Power Flow
P0: N-0 | None | None | None
P1, P2-1, P7: N-1 | 14* | 144* | 2*
P2, P4, P5 | None | None | None
P3: (G-1+N-1)** | 12* | 144* | 37*
P6-2: (X-1+N-1)** | 17* | 145* | 11*
* Violations seen in the basecase under P1 and P7 events were also seen under G-1+N-1 and/or X-1+N-1 events
** See Appendix A for the list of G-1 generators and X-1 transformers being tested

## Slide 4: Comparison of Project Options
ERCOT analyzed four options.
Among the four options, Option 3A addresses all project needs, meets ERCOT and NERC reliability criteria, improves long-term load-serving capability, and is feasible for construction.
Key Takeaway: Option 3A was selected as the ERCOT preferred option because it addresses all project needs in the study area, meets ERCOT and NERC reliability standards, improves long-term load-serving capability, and is feasible for construction.
 | Option 1 | Option 2 | Option 3 | Option 3A
Meets ERCOT and NERC Reliability Criteria | No | No | No | Yes
Improves Long-Term Load-Serving Capability (~MW) | 37.7 | 8.7 | 136.4 | 178.3
Requires CCN (~miles) | No | Yes (62.5) | Yes (14.3) | Yes (14.3)
Cost Estimate* (~$M) | 235.0 | N/A | N/A | 477.7
Construction Feasibility | No | No | No | Yes
Expected ISD | December 2029 | N/A | N/A | May 2031
*Cost estimates were provided by the TSP(s)

## Slide 5: Subsynchronous Oscillation (SSO) Assessment
SSO Assessment Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSO screening for Option 3A and found no adverse SSO impacts to the existing and planned generation resources at the time of this study
Key Takeaway: Option 3A did not have an adverse SSO impact at the time of the study.

## Slide 6: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations.
  ERCOT concluded that:
  Option 3A did not cause any additional congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need
Key Takeaways: Option 3A did not cause any additional congestion in the study area. Potential generation did not impact the preferred option and load scaling did not impact the project need.

## Slide 7: Dynamic Stability Analysis
ERCOT conducted a dynamic stability analysis for the ERCOT-preferred Option 3A. ERCOT updated the DWG 2031 Summer Peak case by incorporating the following key elements for evaluation:
  Additional PG6.9 generation in the study area
  Dynamic load models provided by CPS
  Option 3A upgrades, including STATCOM dynamic data provided by CPS
  Critical contingencies in the study area: P1, P2, P4, P5, P7, and ERCOT2
  No adverse dynamic stability impacts were observed from the implementation of Option 3A (ERCOT-preferred option).
Key Takeaway: No adverse dynamic stability impacts were observed from the implementation of Option 3A (ERCOT-preferred option).

## Slide 8: Overall Project Summary
Convert the existing Helotes 138-kV substation into a new 345-kV switching substation looping into the adjacent 345-kV transmission lines;
Three (3) new 345/138-kV autotransformers;
Install sized capacitors totaling 270 MVAr;
Two (2) new STATCOMs totaling 600 MVAr;
Approximately 14.3 circuit-miles of new 345-kV transmission line; and
Approximately 43.1 circuit-miles of rebuilt 138-kV transmission lines
Detailed list of upgrades are in Appendix B

## Slide 9: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Option 3A to address reliability issues Bexar County in the South Central Weather Zone.
TSPs expect to implement the upgrades by October 2031
Estimated Cost: approximately $477.7 million
  Updated CPS’s initial combined cost estimate ($235.0 million);
  Approximately $242.7 million in upgrades to address additional reliability violations under peak and maintenance conditions
CCN filling would be required to construct a new Hill Country to Bergheim 345-kV transmission line on double-circuit capable structures with one circuit on place, approximately 14.3 miles of new ROW.

## Slide 10: ERCOT Recommendation

## Slide 11: Thank you! Questions/Comments?
Gnanaprabhu.Gnanam@ercot.com

## Slide 12: Appendix
Appendix A: G-1 Generators and X-1 Transformers List
Appendix B: ERCOT Recommendation

## Slide 13: Appendix A: G-1 Generators and X-1 Transformers List
Generator | Transformer
Leon Creek U1 | Cagnon X1 345/138-kV
Guadalupe Energy Center CTG 1 | Howard Road X1 345/138-kV
 | Hill Country X1 345/138-kV
 | Martinez X1 345/138-kV

## Slide 14: Appendix B: ERCOT Recommendation
  Convert the existing Helotes 138-kV substation to a new 345/138-kV switching substation;
  Construct a new 345-kV Helotes switching yard using a breaker-and-a-half configuration utilizing seven circuit breakers;
  Install two new 345/138-kV autotransformers at the new Helotes 345/138-kV switching substation, with normal and emergency ratings of at least 600 MVA;
  Loop into the existing Hill Country to Cagnon 345-kV transmission line into the new Helotes 345-kV substation;
  Install a new 345/138-kV autotransformer at the existing Eastside 345/138-kV substation, with normal and emergency ratings of at least 600 MVA;
  Construct a new Hill Country to Bergheim 345-kV transmission line on double-circuit structures with one circuit in place, with normal and emergency ratings of at least 1,980 MVA, which will require a new ROW, approximately 14.28 miles;
  Rebuild the existing Castle to Dresden 138-kV transmission line on single-circuit structures where not sharing a common tower, with normal and emergency ratings of at least 478 MVA, approximately 3.79 miles;
  The existing infrastructure is approximately 55 years old with a current normal and emergency ratings of 206 MVA;

## Slide 15: Appendix B: ERCOT Recommendation (cont.)
  Rebuild the existing Cagnon to Potranco 138-kV transmission line on single-circuit structures where not sharing a common tower, with normal and emergency ratings of at least 478 MVA, approximately 5.87 miles;
  The existing infrastructure is approximately 54 years old with a current normal and emergency ratings of 314 MVA;
  Rebuild the existing Leon Creek to Palo Alto 138-kV transmission line on single-circuit structures where not sharing a common tower, with normal and emergency ratings of at least 478 MVA, approximately 3.64 miles;
  The existing infrastructure is approximately 30 years old with a current normal and emergency ratings of 314 MVA;
  Rebuild the existing Medinabs to 36th Street 138-kV transmission line on single-circuit structures where not sharing a common tower, with normal and emergency ratings of at least 478 MVA, approximately 8.57 miles;
  The existing infrastructure is approximately 52 years old with a current normal and emergency ratings of 213 MVA;

## Slide 16: Appendix B: ERCOT Recommendation (cont.)
  Rebuild the existing Cagnon to VLSI 138-kV transmission line on single-circuit structures where not sharing a common tower, with normal and emergency ratings of at least 478 MVA, approximately 8.74 miles;
  The existing infrastructure is approximately 58 years old with a current normal and emergency ratings of 314 MVA;
  Rebuild the existing Five_pts to Wstside 138-kV transmission line on single-circuit structures where not sharing a common tower, with normal and emergency ratings of at least 478 MVA, approximately 3.78 miles;
  The existing infrastructure is approximately 9 years old with a current normal and emergency ratings of 287 MVA;
  Rebuild the existing Grissom to VLSI 138-kV transmission line on single-circuit structures where not sharing a common tower, with normal and emergency ratings of at least 478 MVA, approximately 3.03 miles;
  The existing infrastructure is approximately 42 years old with a current normal and emergency ratings of 293 MVA;

## Slide 17: Appendix B: ERCOT Recommendation (cont.)
  Rebuild the existing Anderson to Helotes 138-kV transmission line on single-circuit structures where not sharing a common tower, with normal and emergency ratings of at least 600 MVA, approximately 5.67 miles;
  The existing infrastructure is approximately 58 years old with a current normal and emergency ratings of 478 MVA;
  Install a 50 MVAr sized capacitor at the existing Helotes 138-kV substation;
  Install a 50 MVAr sized capacitor at the existing Howard 138-kV substation;
  Install a 35 MVAr sized capacitor at the existing Ingram Road 138-kV substation;
  Install a 25 MVAr sized capacitor at the existing Legend Falls 138-kV substation;
  Install a 50 MVAr sized capacitor at the existing Panther Springs 138-kV substation;
  Install a 25 MVAr sized capacitor at the existing Tally_Rd 138-kV substation;
  Install a 35 MVAr sized capacitor at the existing Tezel Road 138-kV substation;
  Install a 300 MVAr STATCOM at the existing Grissom 138-kV substation; and
  Install a 300 MVAr STATCOM at the existing Martinez 138-kV substation.