## Slide 1: Oncor Electric Delivery Company LLC (Oncor) – Combined Oncor Set 1 North and Central Texas Reliability Project & Oncor Set 2 North and Central Texas Reliability Project (25RPG040 & 25RPG042) Prabhu Gnanam Director, Grid Planning Technical Advisory Committee Meeting May 19, 2026

## Slide 2: Overview
Oncor Electric Delivery Company LLC (Oncor) submitted the Set 1 North and Central Texas Reliability Project (25RPG040) for Electric Reliability Council of Texas’ (ERCOT) Reginal Planning Group (RPG) review in November 2025.
Oncor submitted the Set 2 North and Central Texas Reliability Project (25RPG042) for ERCOT’s RPG review in November 2025.
.
  The Tier 1 Oncor proposed project submission 25RPG040 was estimated to cost $1.798 billion and will require a Convenience and Necessity (CCN).
  The Tier 1 Oncor proposed project submission 25RPG042 was estimated to cost $1.330 billion and will require a Convenience and Necessity (CCN).
  Address reliability issues in the North, North Central, and East Weather Zones.
  ERCOT conducted a single ERCOT Independent Review (EIR) for these two projects.

## Slide 3: Project Need
Key Takeaway: In addition to the proposed Set 1 and Set 2 projects, substantial amounts of new transmission upgrades would also be needed to serve these additional projected loads which is beyond the study scope of this EIR.
Set 1 North and Central Texas Reliability Project was identified and included in the both 2024 and 2025 Regional Transmission Plan (RTP)
Set 2 North and Central Texas Reliability Project was identified and included in the 2024 RTP and subset of this project was identified and included in the 2025 RTP
With the current method of including full Officer Letter Loads in the EIR review, the study area will have over 16 GW of large loads than the 2025 RTP load level (over 13 GW than the 2024 RTP load level)
Weather Zone | EIR Study Load Level (~MW) | 2025 RTP 2031 Load (~MW) | 2024 RTP 2030 Load (~MW)
East | 3,599 | 3,269 | 3,756
North | 12,889* | 12,526 | 8,103
North Central | 55,410 | 39,606 | 46,424
Total | 71,898 | 55,401 | 58,283
* This load does not include the Panhandle area full Officer Letter Load

## Slide 4: Study Evaluation
Group 1
  Upgrades evaluated and endorsed in the EIR for the Oncor Southern DFW Load Interconnection and General Grid Strengthening Project (25RPG004), and these upgrades were not evaluated as part of this EIR evaluation. Upgrades are listed in Appendix A1.
Group 2
  ERCOT proposed to confirm and approve the remaining transmission upgrades proposed in the Oncor Set 1 and Set 2 North and Central Texas Reliability Projects based on the reliability need identified in the 2024 and 2025 RTP evaluations to expedite the RPG review process except for the one which Transmission Service Providers (TSPs) (Brazos and TNMP) commented on for alternative. Upgrades are listed in Appendix A2.
Group 3
  ERCOT conducted an independent review for the upgrade that Braz Brazos and TNMP commented on for alternative. Upgrade is listed in Appendix A3.

## Slide 5: Group 2 Upgrades: Subsynchronous Oscillation (SSO) Assessment
SSO Assessment Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSO screening for Group 2 and found no adverse SSO impacts to the existing and planned generation resources at the time of this study
Key Takeaway: Group 2 upgrades did not have an adverse SSO impact at the time of the study.

## Slide 6: Group 2 Upgrades: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations.
  ERCOT concluded that:
  Group 2 upgrades did not cause any additional congestion within the study area
  No potential future generation studied impacts the Group 2 upgrades
  The load scaling did not have a material impact on the project need
Key Takeaways: Group 2 upgrades did not cause any additional congestion in the study area. Potential generation did not impact the preferred option and load scaling did not impact the project need.

## Slide 7: Comparison of Group 3 Project Options
ERCOT analyzed two options.
Among the two options for Group 3, Option 1 addresses all project needs, meets ERCOT and NERC reliability criteria, is the least cost option, improves long-term load-serving capability, and does not require a CCN.
Key Takeaway: Option 1 was selected as the ERCOT preferred option for Group 3 because it addresses all project needs in the study area, meets ERCOT and NERC reliability standards, is the least cost option, improves long-term load-serving capability, and does not require a CCN.
 | Option 1 | Option 2
Meets ERCOT and NERC Reliability Criteria | Yes | Yes
Improves Long-Term Load-Serving Capability (~MW) | 721 | 344
Requires CCN (~miles) | No | Yes (18.4)
Cost Estimate* (~$Million) | 56.4 | 80.8
Construction Feasibility | Yes | Yes
Expected ISD | May 2030 | November 2030
* Cost Estimate provided by the TSPs

## Slide 8: Group 3 Option 1: Subsynchronous Oscillation (SSO) Assessment
SSO Assessment Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSO screening for Group 3 Option 1 and found no adverse SSO impacts to the existing and planned generation resources at the time of this study
Key Takeaway: Group 3 Option 1 did not have an adverse SSO impact at the time of the study.

## Slide 9: Group 3 Option 1: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations.
  ERCOT concluded that:
  Group 3 Option 1 did not cause any additional congestion within the study area
  No potential future generation studied impacts the Group 3 Option 1
  The load scaling did not have a material impact on the project need
Key Takeaways: Group 3 Option 1 did not cause any additional congestion in the study area. Potential generation did not impact the preferred option and load scaling did not impact the project need.

## Slide 10: Overall Project Summary for Group 2 and 3 Upgrades
  Construct one (1) new substation and three (3) transformers;
  One (1) new 345-kV substation;
  Three (3) new 345/138-kV transformers;
  Rebuild five (5) existing substations and one transformer;
  Two (2) 345-kV substations and one (1) 345/138-kV transformer;
  Three (3) 138-kV substations;
  Construct five (5) new 345-kV and 138-kV transmission lines;
  Two (2) new 345-kV double-circuit transmission lines, approximately 115.5 miles;
  Three (3) new 138-kV single-circuit transmission lines, approximately 32.9 miles;
  Upgrade existing 345-kV and 138-kV transmission lines;
  Approximately 288.8 circuit miles of existing 345-kV transmission lines; and
  Approximately 233.4 circuit miles of existing 138-kV transmission lines.
  Detailed components list in Appendix B

## Slide 11: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Group 2 and Group 3 upgrades to address reliability issues in the North, North Central, and East Weather Zones.
TSPs expect to implement the upgrades phases between 2028 to 2034
Estimated Cost: approximately $2.363 billion
  Group 2 cost estimate, approximately $2.307 billion
  Group 3 cost estimate, approximately $56.4 million
CCN fillings would be required for the new Lavon Switch to Allen Switch 138-kV single-circuit transmission line, DeSoto Switch to Loop Nine Switch 138-kV single-circuit transmission line, Greene Switch to Wilmer Switch 345-kV double-circuit transmission line, and Jewett Switch to Greene Switch 345-kV double-circuit transmission line, total approximately 131.0 miles of new right of way (ROW).

## Slide 12: ERCOT Recommendation

## Slide 13: Thank you! Questions/Comments?
Gnanaprabhu.Gnanam@ercot.com

## Slide 14: Appendix
Appendix A1: Group 1 Upgrades
Appendix A2: Group 2 Upgrades
Appendix A3: Group 3 Upgrade
Appendix B: ERCOT Recommendation

## Slide 15: Appendix A1: Group 1 Upgrades
Oncor Project Description | RTP Project Number | Counties
Rebuild the Tri Corner 345-kV Switch; Rebuild the Watermill Switch to Tri Corner Switch 345-kV double-circuit line between structure 102/3 and Tri Corner Switch, ~ 8.4 miles; and Rebuild the Trinidad Switch to Tri Corner 345-kV double-circuit line, ~ 40.40 miles | 2024-NC11 | Dallas, Henderson, and Kaufman
Rebuild the Saltillo Switch to Farmersville Switch 345-kV line, ~ 59.9 miles | 2024-NC31 | Collin, Fannin, Grayson, Hunt and Lamar
Rebuild the DeSoto 345/138 kV Switch | 2024-NC80 | Dallas

## Slide 16: Appendix A2: Group 2 Upgrades
Oncor Project Description | RTP Project Number | Counties
Rebuild the Venus Switch to Old Country Switch 345-kV double-circuit line, ~ 15.9 miles; and Rebuild the Notus Switch to Old Country Switch 345-kV double-circuit Line. ~ 14.8 miles | 2024-NC56 and 2024-NC42 | Ellis and Navarro
Rebuild the Hagansport (fka Monticello Tap) Switch to Sulphur Springs East Tap 138-kV line, ~ 20.6 miles | 2024-E8 | Franklin and Hopkins
Reconductor the Monticello Switch to Cash Switch 345-kV line, ~ 62.3 miles | 2024-E9 | Collin, Hopkins, Hunt and Franklin
Rebuild the Valley Switch to Progress Park Switch 138-kV line, 15.6 miles | 2024-N07 | Grayson
Rebuild the Cleburne 138-kV Switch; Rebuild the Cleburne Switch to Venus 138-kV line, ~ 19.5 miles; and Rebuild the Red Hill Switch to Rio Vista Tap 138-kV line, ~ 6.6 miles | 2024-NC04 | Johnson, Ellis and Hill
Rebuild the Commerce Switch to Crossroads Switch 138-kV line, ~ 22.1 miles | 2024-NC36 | Hunt and Delta
Rebuild the Valley Switch to Valley South Switch 345-kV line, ~ 0.9 miles; Rebuild the Valley 345-kV Switch; Rebuild the Anna 345-kV Switch; Rebuild the Anna Switch to Valley Switch 345-kV line, ~ 26.6 miles; and Reconductor the Paris Switch to Valley South Switch 345-kV line, ~ 46.3 miles | 2024-NC31 | Collin, Fannin, Grayson, Hunt and Lamar
Establish a new Lavon 345-kV Switch; Terminate the Allen Switch to Royse Switch/Stouts Creek Switch 345-kV double-circuit line into Lavon 345-kV Switch; Install one 600 MVA (nameplate) 345/138-kV autotransformer at Lavon Switch; and Construct a new Lavon Switch to Allen Switch 138-kV line, ~ 12.7 miles | 2024-NC59 | Collin
Rebuild the Batchler Road Switch to Stainback Switch 345-kV double-circuit line, ~ 3.2 miles | 2024-NC68 | Dallas and Ellis

## Slide 17: Appendix A2: Group 2 Upgrades (cont.)
Oncor Project Description | RTP Project Number | Counties
Add one new 345/138-kV autotransformer at DeSoto; and New DeSoto to Loop Nine 138-kV line, ~ 3.82 miles | 2024-NC80 | Dallas
Rebuild the south circuit of Loop Nine – Watermill 345 kV double-circuit line, ~ 4.0 miles | 2024-NC16 | Dallas
Rebuild the Kaufman Northwest – Seven Point 138-kV line, ~ 20.8 miles | 2024-NC53 | Henderson and Kaufman
New Greene to Wilmer 345-kV double-circuit line, ~ 3.0 miles | 2024-NC86 | Dallas
New Jewett to Greene 345-kV double-circuit line, ~ 112.5 miles | 2024-NC63 | Dallas, Ellis, Freestone, Leon and Navarro
Upgrade the Benbrook 345/138-kV Autotransformer #1 | 2024-NC79 | Tarrant
Add a second 345/138-kV autotransformer at Gunter; and Add two 37.5 MVAr reactors | 2024-NC76 | Collin
Rebuild Argyle 138-kV Switch; Rebuild the Argyle to Highlands (TNMP) 138-kV line, ~ 7.5 miles; Rebuild the Argyle to Corinth 138-kV line, ~ 2.9 miles; and Rebuild the Argyle to Krum 138-kV line, ~ 8.54 miles | 2024-NC72 and 2024-NC40 | Denton
Rebuild the Rivercrest to Hawk Hollow 138-kV line, ~ 25.5 miles; and Rebuild the Hagansport (fka Monticello tap) to Rivercrest 138-kV line, ~ 9.5 miles | 2024-N14 | Lamar and Red River
Rebuild the Paris to Valley 138-kV line, ~ 46.1 miles; and Rebuild the Paris to Commerce 138-kV line, ~ 14.0 miles | 2024-N16 | Delta, Fannin, Hunt and Lamar
Reconductor the Allen to Stouts Creek 345-kV line, ~ 80.9 miles | 2024-NC29 | Collin, Hopkins, Hunt

## Slide 18: Appendix A3: Group 3 Upgrade
Oncor Project Description | RTP Project Number | Counties
Install a second circuit by rebuilding the existing Gunter Switch to Collin Switch 138-kV line to create the Gunter Switch to Collin 138-kV double-circuit line, ~ 16.4 miles | 2024-NC76 | Collin and Grayson

## Slide 19: Appendix B: ERCOT Recommendation
  Rebuild the existing Venus Switch to Old Country Switch 345-kV double-circuit transmission line, on double-circuit-capable structures with both circuits in place, using a conductor rated at 5000 A or greater; increase the existing normal and emergency ratings of 1072 MVA to at least 1912 MVA (due to the limit of existing 3200 A terminal equipment), for approximately 15.9 miles/circuit
  The existing infrastructure is from 1970s
  Rebuild the existing Notus Switch to Old Country Switch 345-kV double-circuit transmission line, on double-circuit-capable structures with both circuits in place, using a conductor rated at 5000 A or greater; increase the existing normal and emergency ratings of 1072 MVA to at least 2987 MVA, for approximately 14.8 miles/circuit
  The existing infrastructure is from 1970s
  Rebuild the existing Hagansport (fka Monticello Tap) Switch to Sulphur Springs East Tap 138- kV transmission line section, on double-circuit-capable structures with one circuit in place, using a conductor rated at 2569 A or greater; increase the existing normal and emergency ratings of 186 MVA to at least 614 MVA, for approximately 20.6 miles
  The existing infrastructure is from 1950s
  Reconductor the existing Monticello Switch to Cash Switch 345-kV transmission line (which is part of an existing 345 kV double-circuit transmission line) using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 1072 MVA to at least 1912 MVA, for approximately 62.3 miles
  The existing infrastructure is from 1960s
  Rebuild the existing Valley Switch to Progress Park Switch 138-kV transmission line, on double-circuit-capable structures with one circuit in place, using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 326 MVA to at least 764 MVA, for approximately 15.6 miles
  The existing infrastructure is from 1960s

## Slide 20: Appendix B: ERCOT Recommendation (cont.)
  Rebuild the existing Cleburne 138-kV Switch by installing six 138-kV, 3200 A circuit breakers in a breaker-and-a-half bus arrangement
  Rebuild the existing Cleburne Switch to Venus 138-kV transmission line section, on double-circuit-capable structures with one circuit in place, using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 214 MVA to at least 764 MVA, for approximately 19.5 miles
  The existing infrastructure is from 1980s
  Rebuild the existing Red Hill Switch to Rio Vista Tap 138-kV transmission line section, on double-circuit-capable structures with one circuit in place, using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 186 MVA to at least 764 MVA, for approximately 6.6 miles
  The existing infrastructure is from 1950s
  Rebuild the existing Commerce Switch to Crossroads Switch 138-kV transmission line (which is part of an existing 138 kV double-circuit transmission line) using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 250 MVA to at least 764 MVA, for approximately 22.1 miles
  The existing infrastructure is from 2000s
  Rebuild the existing Valley Switch to Valley South Switch 345-kV transmission line, on double-circuit-capable structures with one circuit in place, using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 1631 MVA to at least 2987 MVA, for approximately 0.9 miles
  The existing infrastructure is from 2000s
  Rebuild the existing Valley 345-kV Switch by installing eight 345-kV, 5000 A circuit breakers in a breaker-and-a-half bus arrangement

## Slide 21: Appendix B: ERCOT Recommendation (cont.)
  Rebuild the existing Anna 345-kV Switch by installing twelve 345-kV, 5000 A circuit breakers in a breaker-and-a-half bus arrangement
  Rebuild the existing Anna Switch to Valley Switch 345-kV transmission line section, on double-circuit-capable structures with one circuit in place, using a conductor rated at 5000 A or greater; increase the existing normal and emergency ratings of 1912 MVA to at least 2987 MVA, for approximately 26.6 miles/circuit
  The existing infrastructure is from 1960s
  Reconductor the existing Paris Switch to Valley South Switch 345-kV transmission line (which is part of an existing 345 kV double-circuit transmission line) using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 1072 MVA to at least 1912 MVA, for approximately 46.3 miles
  The existing infrastructure is from 2000s
  Establish a new Lavon 345-kV Switch by installing six 345-kV, 5000 A circuit breakers in a breaker-and-a-half bus arrangement and adding two 138-kV, 3200 A circuit breakers
  Terminate the existing Allen Switch to Royse Switch/Stouts Creek Switch 345-kV double-circuit transmission line into Lavon 345-kV Switch, which creates the new Allen Switch to Lavon Switch 345-kV double-circuit transmission line for approximately 11.9 miles/circuit (the north circuit will have normal and emergency ratings of 1072 MVA, the south circuit will have normal and emergency ratings of 1631 MVA) and the new Lavon Switch to Royse Switch/Stouts Creek Switch 345-kV double-circuit transmission line (the Lavon to Stouts Creek Switch circuit will have normal and emergency ratings of 1072 MVA for approximately 69 miles, the Lavon to Royse circuit will have normal and emergency ratings of 1631 MVA for approximately 10.9 miles);
  Install one new 345/138-kV autotransformer with normal and emergency ratings of at least 700 MVA and 750 MVA, respectively
  Construct a new Lavon Switch to Allen Switch 138-kV transmission line, on double-circuit-capable structures with one circuit in place, using a conductor rated at 3200 A or greater with normal and emergency ratings of at least 764 MVA, which will require a new ROW, for approximately 12.7 miles

## Slide 22: Appendix B: ERCOT Recommendation (cont.)
  Rebuild the existing Batchler Road Switch to Stainback Switch 345-kV double-circuit transmission line, on double-circuit-capable structures with both circuits in place, using a conductor rated at 5000 A or greater; increase the existing normal and emergency ratings of 1631 MVA to at least 2987 MVA, for approximately 3.2 miles/circuit
  The existing infrastructure is from 1980s
  Install one new 345/138-kV autotransformer at the existing DeSoto Switch with normal and emergency ratings of at least 700 MVA and 750 MVA, respectively
  Construct a new DeSoto Switch to Loop Nine Switch 138-kV transmission line, on double-circuit-capable structures with one circuit in place, using a conductor rated at 3200 A or greater with normal and emergency ratings of at least 764 MVA, which will require a new ROW, for approximately 3.82 miles
  Rebuild the existing south circuit of Loop Nine Switch to Watermill Switch 345-kV double-circuit transmission line using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 1072 MVA to at least 1912 MVA, for approximately 4.0 miles
  The existing infrastructure is from 1960s
  Rebuild the existing Kaufman Northwest Switch to Seven Point 138-kV transmission line section, on double-circuit-capable structures with one circuit in place, using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 250 MVA to at least 764 MVA, for approximately 20.8 miles
  The existing infrastructure is from 1980s
  Construct a new Greene Switch to Wilmer Switch 345-kV double-circuit transmission line, on double-circuit-capable structures with both circuits in place, using a conductor rated at 5000 A or greater with normal and emergency ratings of at least 2987 MVA, which will require a new ROW, for approximately 3.0 miles/circuit

## Slide 23: Appendix B: ERCOT Recommendation (cont.)
  Construct a new Jewett Switch to Greene Switch 345-kV double-circuit transmission line, on double-circuit-capable structures with both circuits in place, using a conductor rated at 5000 A or greater with normal and emergency ratings of at least 1912 MVA, which will require a new ROW, for approximately 112.5 miles/circuit
  Upgrade the existing Benbrook 345/138-kV autotransformer #1; increase the existing normal and emergency ratings of 552 MVA and 625 MVA, respectively to at least 700 MVA and 750 MVA, respectively
  Install a second 345/138-kV autotransformer at Gunter Switch with normal and emergency ratings of at least 700 MVA and 750 MVA, respectively, and install two 37.5 MVAr reactors on the tertiary winding of the autotransformer
  Rebuild the existing Argyle 138-kV Switch by installing six 138-kV, 3200 A circuit breakers in a breaker-and-a-half bus arrangement
  Rebuild the existing Argyle Switch to Highlands 138-kV transmission line, on double-circuit-capable structures with one circuit in place, using a conductor rated at 2569 A or greater; increase the existing normal and emergency ratings of 214 MVA to at least 614 MVA, for approximately 7.5 miles
  The existing infrastructure is from 1960s
  Rebuild the existing Argyle Switch to Corinth 138-kV transmission line section, on double-circuit-capable structures with one circuit in place, using a conductor rated at 2569 A or greater; increase the existing normal and emergency ratings of 314 MVA to at least 614 MVA, for approximately 2.9 miles
  The existing infrastructure is from 1950s

## Slide 24: Appendix B: ERCOT Recommendation (cont.)
  Rebuild the existing Argyle Switch to Krum Tap Switch 138-kV transmission line, on double-circuit-capable structures with one circuit in place, using a conductor rated at 2569 A or greater; increase the existing normal and emergency ratings of 210 MVA to at least 614 MVA, for approximately 8.54 miles
  The existing infrastructure is from 1960s
  Rebuild the existing Rivercrest 138-kV Switch
  Rebuild the existing Rivercrest Switch to Hawk Hollow Switch 138-kV transmission line, on double-circuit-capable structures with one circuit in place, using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 186 MVA to at least 764 MVA, for approximately 25.5 miles
  The existing infrastructure is from 1950s
  Rebuild the existing Hagansport (fka Monticello tap) Switch to Rivercrest Switch 138-kV transmission line, on double-circuit-capable structures with one circuit in place, using a conductor rated at 2569 A or greater; increase the existing normal and emergency ratings of 186 MVA to at least 614 MVA, for approximately 9.5 miles
  The existing infrastructure is from 1950s
  Rebuild the existing Paris Switch to Valley Switch 138-kV transmission line, on double-circuit-capable structures with one circuit in place, using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 214 MVA to at least 764 MVA, for approximately 46.1 miles
  The existing infrastructure is from 2000s

## Slide 25: Appendix B: ERCOT Recommendation (cont.)
  Rebuild the existing Paris Switch to Commerce 138-kV transmission line section (which is part of an existing 138-kV double-circuit transmission line) using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 250 MVA to at least 764 MVA, for approximately 14.0 miles
  The existing infrastructure is from 2000s
  Reconductor the existing Allen Switch to Stouts Creek Switch 345-kV transmission line (which is part of an existing 345-kV double-circuit transmission line) using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 1072 MVA to at least 1912 MVA, for approximately 80.9 miles
  The existing infrastructure is from 1960s
  Install a second circuit by rebuilding the existing Gunter Switch to Collin Switch 138-kV transmission line to create the Gunter Switch to Collin Switch 138-kV double-circuit transmission line, on double-circuit-capable structures with both circuits in place, using a conductor rated at 3200 A or greater; increase the existing normal and emergency ratings of 495 MVA to at least 765 MVA for approximately 16.4 miles/circuit
  The existing infrastructure is from 2010s