## Slide 1: Oncor Electric Delivery Company LLC (Oncor) – Combined Oncor Set 1 North Central & South Central Texas Reliability Project & Oncor Set 2 North Central & South Central Texas Reliability Project (25RPG041 & 25RPG043) Prabhu Gnanam Director, Grid Planning Technical Advisory Committee Meeting May 19, 2026

## Slide 2: Overview
Oncor Electric Delivery Company LLC (Oncor) submitted the Set 1 North Central and South Central Texas Reliability Project (25RPG041) for Electric Reliability Council of Texas’ (ERCOT) Reginal Planning Group (RPG) review in November 2025.
Oncor submitted the Set 2 North Central and South Central Texas Reliability Project (25RPG043) for ERCOT’s RPG review in November 2025.
  The Tier 1 Oncor proposed project submission 25RPG041 was estimated to cost $943.92 million and will require a Convenience and Necessity (CCN).
  The Tier 1 Oncor proposed project submission 25RPG043 was estimated to cost $440.79 million and will require a Convenience and Necessity (CCN).
  Address reliability issues in the North Central, South Central, and East Weather Zones.
  ERCOT conducted a single ERCOT Independent Review (EIR) for these two projects.

## Slide 3: Project Need
Key Takeaway: In addition to the proposed Set 1 and Set 2 projects, additional new transmission upgrades would also be needed to serve these additional loads which is beyond the study scope of this EIR.
Set 1 North Central and South Central Texas Reliability Project was identified and included in the both 2024 and 2025 Regional Transmission Plan (RTP)
Set 2 North Central and South Central Texas Reliability Project was identified and included in the 2024 RTP and subset of this project was identified and included in the 2025 RTP
With the current method of including full Officer Letter Loads in the EIR review, the study area will have over 19 GW of large loads than the 2025 RTP load level (over 18 GW than the 2024 RTP load level)
Weather Zone | EIR Study Load Level (~MW) | 2025 RTP 2031 Load (~MW) | 2024 RTP 2030 Load (~MW)
East | 3,599 | 3,269 | 3,756
North Central | 55,410 | 39,606 | 46,424
South Central | 30,872 | 27,969 | 21,181
Total | 89,880 | 70,844 | 71,361

## Slide 4: Study Evaluation
Group 1
  ERCOT has evaluated and included the overlapping upgrades (highlighted on slide 5) as part of the ongoing EIR for the Oncor and LCRA TSC Muscovy and Voss Lake 345/138-kV Project (25RPG009), and these upgrades will not be evaluated as part of this EIR evaluation. Upgrades are listed in Appendix A1.
Group 2
  ERCOT conducted an expedited review of the remaining transmission upgrades proposed in the Oncor Set 1 and Set 2 North Central and South Central Texas Reliability Projects based on the reliability need identified in the 2024 and 2025 RTP evaluations, except for the upgrades which Transmission Service Providers (TSPs) commented for alternative. Upgrades are listed in Appendix A2.
Group 3
  ERCOT is conducting an independent review for the upgrades that TSPs commented for alternative. Upgrades are listed in Appendix A3. The EIR review for these upgrades is expected to be completed in Q3 2026.

## Slide 5: Group 2 Upgrades: Subsynchronous Oscillation (SSO) Assessment
SSO Assessment Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSO screening for Group 2 and found no adverse SSO impacts to the existing and planned generation resources at the time of this study
Key Takeaway: Group 2 upgrades did not have an adverse SSO impact at the time of the study.

## Slide 6: Group 2 Upgrades: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations.
  ERCOT concluded that:
  Group 2 upgrades did not cause any additional congestion within the study area
  No potential future generation studied impacts the Group 2 upgrades
  The load scaling did not have a material impact on the project need
Key Takeaways: Group 2 upgrades did not cause any additional congestion in the study area. Potential generation did not impact the preferred option and load scaling did not impact the project need.

## Slide 7: Overall Project Summary for Group 2 Upgrades
  Construct approximately 13.8 miles of new 345-kV double-circuit transmission lines, which will require new right of way (ROW);
  Rebuild approximately 67.0 miles of existing 138-kV single-circuit transmission lines;
  Rebuild two (2) existing 345/138-kV substations; and
  Upgrade one (1) existing 345/138-kV autotransformer.
  Detailed components list in Appendix B

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Group 2 upgrades to address reliability issues in the North Central, South Central, and East Weather Zones.
TSPs expect to implement the upgrades phases between 2028 to 2034
Estimated Cost: approximately $381.09 million
CCN filling would be required for the new Elkton Switch to Shamburger Switch 345-kV double-circuit transmission line for approximately 13.8 miles of new ROW.

## Slide 9: ERCOT Recommendation

## Slide 10: Thank you! Questions/Comments?
Gnanaprabhu.Gnanam@ercot.com

## Slide 11: Appendix
Appendix A1: Group 1 Upgrades
Appendix A2: Group 2 Upgrades
Appendix A3: Group 3 Upgrades
Appendix B: ERCOT Recommendation

## Slide 12: Appendix A1: Group 1 Upgrades
Oncor Project Description | RTP Project Number | Counties
Construct a new Tower 345-kV Switch (SW); Terminate the existing Salado SW to Knob Creek SW 345-kV Line into the new Tower 345-kV SW; Construct a new Tower SW to Knob Creek 345-kV Line on separate structures, ~1.2-mile Rebuild the Salado SW to Tower SW 345-kV Line, ~12.4-mile; | 2024-NC12 | Bell
Rebuild the existing Temple SW to Temple Pecan Creek SW 345-kV Double-Circuit Line, ~4.5-mile; | 2024-NC32 | Bell
Rebuild the existing Bell County East SW to Gibson SW 345-kV Double-Circuit Line, ~23.4-mile; | 2024-NC60 and 2024-NC91 | Bell and Milam
Rebuild the existing Bell County East SW to Voss Lake SW 345-kV Double-Circuit Line, ~29.6-mile; Rebuild the existing Minerva SW to Cannon 138-kV Line, ~9.9-mile; | 2024-SC28 | Bell and Milam

## Slide 13: Appendix A2: Group 2 Upgrades
Oncor Project Description | RTP Project Number | Counties
Rebuild the existing Revolution SW to Hubbard 138-kV Line, ~27.3-mile; Rebuild the Ash Creek Switch to Hubbard 138-kV Line, ~5.1-mile; Rebuild the Hillsboro Switch to Ash Creek Switch 138-kV Line, ~19.30-mile; | 2024-NC27 and 2024-NC04 | Hill and Navarro
Rebuild the existing Mankin SW to Seven Points 138-kV Line, ~11.2-mile; | 2024-NC44 | Henderson
Rebuild the existing Trinidad SW to Mankin SW 138-kV Line, ~4.1-mile; | 2024-NC34 | Henderson
Rebuild the existing Elkton 345/138-kV Switch; Install one new 345/138-kV autotransformer at Elkton Switch; Construct a new Elkton Switch to Shamburger Switch 345-kV Double-Circuit Line, ~13.8-mile; Rebuild the existing Shamburger 345/138 kV Switch; and Install one new 345/138-kV autotransformer at Shamburger | 2024-E2 | Smith

## Slide 14: Appendix A3: Group 2 Upgrades
Oncor Project Description | RTP Project Number | Counties
Rebuild the existing Temple Pecan Creek SW to Bellfalls/STR26/4C 345-kV Double-Circuit Line, ~2.6-mile; Rebuild the existing Possum Trot SW to Bellfalls/STR26/4C 345-kV Double-Circuit Line, ~26.1-mile; Rebuild the Tradinghouse Switch to Four Brothers Switch 345-kV Line, ~20.6-mile; Rebuild the Tiger Creek Switch to Sam Switch (Lone Star) 345-kV Line, ~21.2-mile; and Rebuild the Possum Trot Switch to Lake Hall Switch to Tradinghouse Switch 345-kV Double-Circuit Line, ~9.6-mile | 2024-NC32 | Bell, Falls, Hill, and McLennan
Rebuild the existing Sam SW to Four Brothers SW 345-kV Line, ~2.3-mile; | 2024-NC69 | Hill, and McLennan
Rebuild the existing Possum Trot SW to St John SW to Bale SW to Stranger SW 345-kV Line, ~18.4-mile; | 2024-NC23 | McLennan, Falls, and Limestone

## Slide 15: Appendix B: ERCOT Recommendation
  Rebuild the existing Revolution Switch to Haney to Hubbard Switch 138-kV single-circuit transmission lines, using double-circuit capable structures with only one circuit installed, using a conductor rated 2,569 A or greater; increase the existing normal and emergency ratings of 84 MVA to at least 614 MVA; and ensure all associated terminal equipment are rated meet or exceed 3,200 A (764 MVA), for approximately 27.3 miles
  The existing infrastructure is from the 1960s
  Rebuild the existing Hillsboro Switch to Ash Creek Switch 138-kV single-circuit transmission lines, using double-circuit capable structures with only one circuit installed using a conductor rated 2,569 A or greater; increase the existing normal and emergency ratings of 124 MVA to at least 614 MVA; and ensure all associated terminal equipment are rated meet or exceed 3,000A (717 MVA), for approximately 19.3 miles
  The existing infrastructure is from the 1940s
  Rebuild the existing Ash Creek Switch to Hubbard Switch 138-kV single-circuit transmission lines, using double-circuit capable structures with only one circuit installed using a conductor rated 2,569 A or greater; increase the existing normal and emergency ratings of 124 MVA to at least 614 MVA; and ensure all associated terminal equipment meet or exceed 3,200A (764 MVA), for approximately 5.1 miles
  The existing infrastructure is from the 1940s
  Rebuild the existing Mankin Switch to Seven Points 138-kV single-circuit transmission lines, using double-circuit capable structures with only one circuit installed, using a conductor rated 3,200 A or greater; increase the existing normal and emergency ratings of 250 MVA to at least 764 MVA; and ensure all associated terminal equipment are rated meet or exceed 3,200A (764 MVA), for approximately 11.2 miles
  The existing infrastructure is from the 1980s

## Slide 16: Appendix B: ERCOT Recommendation (cont.)
  Rebuild the existing Trinidad Switch to Mankin Switch 138-kV single-circuit transmission lines, using double-circuit capable structures with only one circuit installed, using a conductor rated 3,200 A or greater; increase the existing with normal and emergency ratings of 250 MVA to at least 764 MVA; and ensure all associated terminal equipment are rated to meet or exceed 3,200A (764 MVA), for approximately 4.1 miles
  The existing infrastructure is from the 1920s
  Rebuild the existing Elkton 345/138-kV Switch at a nearby location
  The existing substation was put into service in the 1940s and has property constraints for expansion
  Install eight (8) 345-kV 5,000 A circuit breakers in a breaker-and-a-half arrangement and install twelve (12) 138-kV 3,200 A circuit breakers in a breaker-and-a-half arrangement
  Upgrade the existing 345/138-kV autotransformer with normal and emergency ratings of 468 MVA and 528 MVA, respectively, with a new 600 MVA (nameplate) 345/138-kV autotransformer with normal and emergency ratings of 700 MVA and 750 MVA, respectively
  Ensure all line terminal and associated equipment are rated to meet or exceed 5,000 A (2,987 MVA) for 345-kV and 3,200 A (764 MVA) for 138-kV
  Rebuild the existing Shamberger 345/138-kV Switch at a nearby location
  The existing substation was put into service in the 1970s and has property constraints for expansion
  Install five (5) 345-kV 5,000 A circuit breakers in a breaker-and-a-half arrangement and install seven (7) 138-kV 3,200 A circuit breakers in a breaker-and-a-half arrangement
  Relocated the existing 345/138-kV autotransformer with normal and emergency ratings of 687 MVA and 750 MVA, respectively, to the new location of the Shamburger 345/138-kV Switch
  Ensure all line terminal and associated equipment are rated to meet or exceed 5,000 A (2,987 MVA) for 345-kV and 3,200 A (764 MVA) for 138-kV

## Slide 17: Appendix B: ERCOT Recommendation (cont.)
  Construct a new Elkton Switch to Shamburger Switch 345-kV double-circuit transmission line, using double-circuit capable structures on a new ROW, using a conductor rated 5,000 A or greater, with normal and emergency ratings of at least 2,987 MVA, for approximately 13.8 miles per circuits
  Install four (4) 345-kV 5,000 A circuit breakers at Elkton 345-kV Switch
  Install four (4) 345-kV 5,000 A circuit breakers at the Shamberger 345-kV Switch
  Ensure all associated terminal equipment are rated to meet or exceed 5,000 A (2,987 MVA)