## Slide 1: LCRA Transmission Services Corporation (LCRA TSC) and CenterPoint Energy Houston Electric, LLC (CEHE) Euclid 765-kV Substation and Transmission Line Addition Project (26RPG001) Prabhu Gnanam Director, Grid Planning Technical Advisory Committee Meeting May 19, 2026

## Slide 2: Overview
LCRA Transmission Services Corporation (LCRA TSC) and CenterPoint Energy Houston Electric, LLC (CEHE) submitted the Euclid 765-kV Substation and Transmission Line Addition Project for Regional Planning Group (RPG) review in January 2026.
  This Tier 1 LCRA TSC and CEHE proposed project submission was estimated to cost $1.831 billion and will require a Convenience and Necessity (CCN).
  This project was identified and included in 2025 Regional Transmission Plan (RTP) to address the reliability need and a growing import need in Central Texas.

## Slide 3: Project Need
The 2025 RTP developed the Euclid 765-kV Substation and Transmission Line Addition Project to address the 2030 base case reliability needs.
The expansion of the existing 345-kV Euclid station in Central Texas to include 765-kV helps support bus voltages and provides a new source into the Central Texas area.
Adding the Euclid 765-kV Substation and Transmission Line Addition Project in Central Texas brings additional transfer capacity needed for the Central Texas area.
With the current method of including full Officer Letter Loads in the EIR review, the study area will have over 19 GW of large loads than the 2025 RTP load.
Key Takeaway: In addition to the proposed project, additional new transmission upgrades would also be needed to serve these additional loads which is beyond the study scope of this EIR.
Weather Zone | EIR Study Load Level (~MW) | 2025 RTP 2031 Load (~MW) | 2024 RTP 2030 Load (~MW)
East | 3,599 | 3,269 | 3,756
North Central | 55,410 | 39,606 | 46,424
South Central | 30,872 | 27,969 | 21,181
Total | 89,880 | 70,844 | 71,361

## Slide 4: Comparison of Project Options
ERCOT performed a comprehensive evaluation for determining the Euclid 765-kV Substation and Transmission Line Addition Project to satisfy the need in the 2025 RTP evaluation.
ERCOT conducted extensive analysis of the Euclid 765-kV Substation and Transmission Line Addition Project and obtained substantial review and input from Transmission and Distribution Service Providers (TDSPs) and other stakeholders in the ERCOT region through the RPG meetings. As a culmination of these efforts, ERCOT has proposed the Euclid 765-kV Substation and Transmission Line Addition Project during 2025 RTP study.
Key Takeaway: Euclid 765-kV Substation and Transmission Line Addition Project was identified in the 2025 RTP evaluation.

## Slide 5: Subsynchronous Oscillation (SSO) Assessment and Dynamic Stability Analysis
SSO Assessment Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSO screening for the Euclid 765-kV Substation and Transmission Line Addition Project and found no adverse SSO impacts to the existing and planned generation resources at the time of this study
  Dynamic Stability Analysis
  The results of the analysis indicate that the addition of the recommended Euclid – Hillje area 765-kV and 345-kV upgrades does not impact the West Texas Export stability limit of 16.2 GW identified under the approved full 765-kV STEP.
Key Takeaway: Euclid 765-kV Substation and Transmission Line Addition Project did not have an adverse SSO or West Texas Export stability limit impact at the time of the study.

## Slide 6: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations.
  ERCOT concluded that:
  Euclid 765-kV Substation and Transmission Line Addition Project 1 did cause an additional congestion within the study area. The new congestion will be evaluated in forthcoming studies. A decreased in the total system wide congestion was observed in the study.
  No potential future generation studied impacts the Euclid 765-kV Substation and Transmission Line Addition Project.
  Starting 2024, ERCOT RTP adopted a new methodology of having one summer peak case for each study year with non-coincident peaks for each of the Weather Zones, which eliminates the load scaling impact.
Key Takeaways: Euclid 765-kV Substation and Transmission Line Addition Project did not cause any additional congestion in the study area. Potential generation did not impact the preferred option and load scaling did not impact the project need.

## Slide 7: Overall Project Summary
Approximately 131.4 miles of new 765-kV single-circuit transmission line;
One (1) new 765-kV Substation;
Two (2) new 765/345-kV transformers;
765-kV Switch Shunt Reactors;
Upgrade existing 345-kV circuit breakers to 80 kA interrupting capability; and
Two (2) new, approximately 2.0 miles, 345-kV transmission lines.

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Euclid 765-kV Substation and Transmission Line Addition Project as identified in the 2025 RTP to address a growing import need in Central Texas.
TSP expect to implement the upgrades by June 30, 2031
Estimated Cost: approximately $1.831 billion
CCN filling would be required to construct a new Euclid to Hillje 765-kV single-circuit transmission line, with normal and emergency ratings of at least 7,602 MVA, which will require a new right of way (ROW), approximately 131.4 miles.

## Slide 9: ERCOT Recommendation (cont.)
Construct a new Euclid 765-kV Substation
  Install adjacent to existing Euclid 345-kV Station expanding Euclid Station
  Install two (2) new 765/345-kV transformers rated to at least 2,403 MVA Normal and 2,772 MVA Emergency;
  Connect Euclid 765-kV as cut-in to planned Bell County East to Howard Road 765-kV transmission line; and
  Install 765-kV Switch Shunt Reactors sufficient to ensure voltage remains within acceptable operating limits.
At Planned Hillje 765/345-kV Substation
  Install or modify existing Switch Shunt Reactors sufficient to ensure voltage remains within acceptable operating limits; and
  Upgrade existing 345-kV circuit breakers to 80 kA interrupting capability.

## Slide 10: ERCOT Recommendation (cont.)
Construct a new Euclid to Hillje 765-kV single-circuit transmission line, with normal and emergency ratings of at least 7,602 MVA, which will require a new ROW, approximately 131.4 miles
  LCRA TSC to construct approximately 65.7 miles segment from Euclid to point-of-interconnection with CEHE; and
  CEHE to construct approximately 65.7 miles segment from Hillje to point-of-interconnection with LCRA TSC.
At Existing Euclid 345-kV Substation
  Connect Euclid 345-kV as Cut-in to the existing John Dumas to Hornsby 345-kV transmission line;
  Construct two (2) new Euclid to Misty 345-kV transmission lines rated to at least 2,988 MVA on separate structures, which will require a new ROW, approximately 2.0 miles;
  All equipment will be rated at 2,988 MVA (5000 Amps); and
  Install new 345-kV circuit breakers with 80 kA interrupting capability.
At Existing Misty 345-kV Substation
  All equipment will be rated at 2,988 MVA (5000 Amps); and
  Install new 345-kV circuit breakers with 80 kA interrupting capability.

## Slide 11: ERCOT Recommendation

## Slide 12: Thank you! Questions/Comments?
Gnanaprabhu.Gnanam@ercot.com