## Slide 1
Batch Study Details
PGRR145 and NPRR1325
May 19-20, 2026
TAC

## Slide 2: Batch Zero Revision Request Timeline
Forums
ROS (Reliability and Operations Subcommittee)
2026
Q1
Q2
Q3
Feb
Mar
Apr
May
Jun
Jul
Workshop #2 Feb 12
Workshop #4 Mar 10
Workshop #5 Mar 24
Workshop #6 Mar 30
PRS Update 3/11
ROS Vote 5/7
Board Vote 6/1
3/4 ERCOT files Batch Zero Revision Request(s)
7/10 Target effective date of NPRR1325 and PGRR145
Consideration of Batch Zero NPRR 1325 and PGRR 145
LLWG Feb 19
Workshop #3 Feb 26
TAC Vote 5/19-20
6/1 Target Board approval date
Board Meeting 4/20
ROS Update 4/2
Monthly TAC updates
Workshop #7 Apr 9
Special PRS 4/22
Regular TAC 4/29
Special TAC Vote 5/13
PRS Vote 5/6
Monthly LLWG updates
ROS Update (special) 4/14
ROS Update 3/5
ROS Update (special) 4/23
PRS (Protocols Review Subcommittee)
Workshops and working groups
TAC
ERCOT Board
Objective
Align stakeholders on direction/scope following Commission decision
Define the scope, boundaries, and intended role of Batch Zero
File NPRR 1325 for Workshops and PRS review
Endorse NPRR 1325 for advancement to TAC
File PGRR 145 for Workshops and ROS review
Endorse PGRR 145 for advancement to TAC
Review/endorse combined NPRR/PGRR package for Board approval
Close outstanding design and drafting issues, incorporate vetted stakeholder feedback, and finalize Revision Request language for committee approval
Preview structure/governing concepts of Batch Zero PGRR before filing
Note that TAC leadership is involved in considering options to ensure successful review and approval
Source: ERCOT discussions
Regular PRS 4/15
Workshop #8 May 4
4/17 ERCOT files PGRR comments integrating CLR framework
4/30 ERCOT files PGRR comments
5/2 ERCOT files PGRR comments integrating BYOG framework

## Slide 3: PGRR145 Update
May 15- ERCOT filed comments providing further clarifications (and will provide walk through)
May 18- ERCOT updated the Impact Analysis to clarify ongoing Batch Study activities after Batch Zero:
May 19- ERCOT filed comments with clarifications (and will provide walk through)
Generally speaking, there were no major changes incorporated by ERCOT in either set of comments

## Slide 4: Batch Zero is already stretched: further expansion risks non-actionable study outcomes
Chart: 
 | 113.2 | 97.2968
 | 13.6 | 42.0073
 | 79.3 | 30.2239
 | 12.5 | 7.8827
 | 38.2 | 11.7267
 | 34.5 | 21.8786
 | 95.3145
 | 2.546
~35
~38
~13
~79
~14
~113
Load requests1
~3
~95
~22
~12
~8
~30
~42
~97
Available generation2
~291
~309
Source: ERCOT April GIS Report, PGRR145 ERCOT Comments, May 15, ERCOT analysis
2032 estimate of load vs. available generation by PG 6.9 category, GW
Key considerations
Current Batch Zero scope is already aggressive at ~220 GW of potential modeled 2032 load (including ~113 GW of base forecast), significantly increasing study complexity and uncertainty
Further expansion would push modeled load well beyond reasonable study bounds, increasing risk of unreliable or non-actionable study outcomes
Serving this load already requires reliance on later-stage generation (PG 6.9(5)(c)(iii) and beyond), reflecting projects without full interconnection or operational certainty
Additional load would require assuming capacity from inactive or highly uncertain resources (e.g., 6.9(5)(d)), increasing risk that modeled generation is not deliverable
1. 2032 load estimate reflects a preliminary non-LL forecast and includes assumptions for EV, rooftop PV, medium TSP loads, and crypto loads. Large-load values are derived from the LLIS PUC report, supplemental TSP inputs, and ERCOT analysis and are shown by category. Some overlap may remain between certain large-load categories, particularly early-stage LLIS and RPG/PBRP-related loads | 2. Generation estimate reflects expected available capacity by resource type during the summer peak hour. Values represent expected available generation, not installed nameplate capacity | 3. RPG Large Load and Permian Basin Plan Load may have overlap with Batch Zero – Base and Studied Loads
6.9(5)(c)(ii) - “Planned” status, started FIS - completed steady state studies
6.9(1)
6.9(5)(a) - “Planned” status, signed SGIA
6.9(5)(b) - “Planned” status, completed FIS
6.9(5)(c)(i) - “Planned” status, started FIS – completed steady state and stability studies
Operational
6.9(5)(c)(iii) - “Planned” status, started FIS
6.9(5)(d) - “Inactive” status with completed FIS stability study
Base Forecast
Medium TSP Loads
Batch Zero – Base and Studied Load (Eligible based on validated study as of 5/12/26)
Permian Basin Plan Load3
RPG Large Load3
AEP Comments Load
HIGHLY PRELIMINARY

## Slide 5: Background on study validity check
Prior to the implementation of PGRR115 on December 15, 2025:
  Large Loads included in an RPG transmission project review could use those studies as their interconnection study for purposes of ERCOT’s FAC-002 compliance if their in-service date was more than 2 years in the future
  Large Loads were required to follow the Large Load Interconnection Study (LLIS) process if their in-service date was less than 2 years in the future and could optionally follow it if greater than 2 years
RPG Projects submitted before April 1, 2026 used the Protocol defined substantiated load process. Each TSP would notify ERCOT via the RPG comment process of load that should be added and why
ERCOT must ensure that Large Loads categorized as base load in Batch Zero have valid studies demonstrating that the subject load and all other base loads can be reliably served
If two or more Large Loads are not included in each other’s interconnection studies, ERCOT needs a way to rank the priority of those studies for purposes of Batch Zero
ERCOT’s proposal in PGRR145 is to use study completion date for that ranking, regardless of whether the study was completed through the RPG process or LLIS
Based on this ranking, ERCOT will do a study validity check to ensure reliability
  Loads that fail the validity check will be included in Batch Zero as studied load

## Slide 6: Change in eligibility for RPG loads will impact completed and in-progress reviews of study validity
Key takeaways
Current reviews are ongoing
Change will require new checks
Changing the date of automatically valid studies for Large Loads in RPG studies will impact study validity for many LLIS loads
In order to maintain a reliability-based approach for Batch Zero, ERCOT must reassess existing LLIS studies to ensure the load can still be reliably served in the context of the automatically valid RPG studies.
The impact is that many LLIS loads, including those considered to have valid studies under the current draft language, would need to be reassessed and potentially restudied after the endorsement or approval of RPG projects.
LLIS – Load 1 (Jan 20, 2026)
✔
RPG A – Loads 1&2 (Feb 9, 2026)
LLIS – Load 2 (Feb 26, 2026)
LLIS – Load 3 (March 2, 2026)
RPG B – Load 1, 2, 3 (April 20, 2026)
LLIS – Load 11 (April 27, 2026)
RPG C – Load 1 (April 20, 2026)
LLIS – Load 12 (May 3, 2026)
…
LLIS – Load 4 (March 6, 2026)
LLIS – Load 5 (March 14, 2026)
LLIS – Load 6 (March 23, 2026)
LLIS – Load 7 (March 23, 2026)
LLIS – Load 8 (April 7, 2026)
LLIS – Load 9 (April 15, 2026)
LLIS – Load 10 (April 17, 2026)
✔
✔
✔
✔
✔
↻
✔
↻
↻
↻
?
?
?
?
Automatically Valid
Restudies in progress
or completed
Initial validity check in progress
LLIS – Load 1 (Jan 20, 2026)
LLIS – Load 2 (Feb 26, 2026)
LLIS – Load 3 (March 2, 2026)
RPG B – Load 1, 2, 3 (April 20, 2026)
LLIS – Load 11 (April 27, 2026)
RPG C – Load 1 (April 20, 2026)
LLIS – Load 12 (May 3, 2026)
LLIS – Load 4 (March 6, 2026)
LLIS – Load 5 (March 14, 2026)
LLIS – Load 6 (March 23, 2026)
LLIS – Load 7 (March 23, 2026)
LLIS – Load 8 (April 7, 2026)
LLIS – Load 9 (April 15, 2026)
LLIS – Load 10 (April 17, 2026)
…
RPG A – Loads 1&2 (Feb 9, 2026)
✔
✔
✔
Automatically Valid
?
?
?
?
?
?
?
?
?
?
?
?
New validity checks needed and restudies may be required
Status of Studies
Studies are automatically valid
Studies are provisionally valid after check
Restudy in progress after failed validity check
Validity check in progress
✔
✔
↻
?

## Slide 7: TAC consideration and the June Board meeting
In the event stakeholders want to file comments for the ERCOT Board meeting:
  ERCOT posts Board materials one week prior to the meeting; and comments received after that date may still be posted but may not be available in time for Board consideration.
  To allow time for formal posting and review, comments should be submitted as soon as possible.
If a stakeholder wants to present comments at the Board they will need to email and coordinate through ERCOT’s General Counsel, Chad.Seely@ercot.com.

## Slide 8: APPENDIX
PCLR Design Details from prior Workshops
BYOG Design Details from prior Workshops
Details on non-linearity of studying 2032

## Slide 9: Overview of Provisional Controllable Load Resource (PCLR)
  Large Load participates as a Provisional Controllable Load Resource (PCLR), where a portion of load is firm (LPC) and the remaining load is flexible and subject to dispatch
  The PCLR framework enables Load to consume more energy in unconstrained hours of the day ahead of full transmission build-out, with firm MW defined in the Batch Zero study and non-firm MW managed through SCED
Description
Details
  Split between firm and flexible load defined through the Load Commissioning Plan (LCP) (LPC = firm MW; remaining load operates as PCLR)
  PCLR participates as dispatchable demand and must follow SCED basepoints within its operating range
  Full requested load is studied in Batch Zero, with transmission upgrades identified to transition PCLR to firm service over time
Provisional Controllable Load Resource (PCLR)
Point of interconnection
Load
Illustrative scheme

## Slide 10: Provisional CLRs – Definition1
New Resource Type: ‘Provisional CLR’
A Large Load electing to operate as a CLR post-Batch Zero, with LPC defined in study and commitment via Form
What’s different?
PCLR load bids can be ‘capped’ to mitigate transmission constraints identified in SCED
PCLR bids are capped dynamically (“last-in-line/just-in-time”) in each run of SCED to a price that will just allow SCED to resolve a constraint
PCLRs are not eligible to provide Ancillary Services
Submits CLR Energy Bid Curve  bid-to-buy prices between Low Power Consumption (LPC) and Maximum Power Consumption (MPC) – same as any other CLR
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
Reference: Batch Zero PGRR145 (April 23, 2026), Sections 9.2.2.1, 9.3.2.1, 9.4.1, 9.5.3, and 9.6.1 (Provisional Controllable Load Resource design, study treatment, and operations)

## Slide 11: Provisional CLRs – Structure of Revision Requests1
Will consist of a comments to existing PGRR145 and companion NPRR1325
Modular structure adds to PGRR145 and NPRR1325
  Example – Section 9.2.2.1, Additional Information Required for Provisional Controllable Load Resources (PCLRs) compliments Section 9.2.2 as written in PGRR145
This structure will allow the PCLR concepts to move forward in parallel with PGRR145 and NPRR1325 if possible, without interfering with the core Batch Zero language
Language related to PCLR approval to energize and PCLR bid capping in SCED is intended to remain grey-boxed until implementation of NPRR1188 and until system changes for the bid capping are in place
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 12: PCLR Language – Foundational Concepts1
Allocation in Batch Zero
Registration Requirements
Ensure Real-Time Dispatch
Load is assessed through the Batch Zero process in the same manner as load requesting firm service for steady state and at full consumption for stability
The level of firm load that can be reliably served becomes the maximum Low Power Consumption (LPC) value for the PCLR in real-time (instead of a hard limit)
The remaining requested load amount is approved contingent on qualification as a PCLR
Intention to register as a PCLR must be declared prior to the start of Batch Zero
Once allocated in Batch Zero, the load must register and qualify as PCLR before it may consume above initial limits
Load must remain registered as a PCLR until an exit date identified in Batch Zero
Obligation to remain a PCLR transfers to subsequent owners of the Large Load
Like traditional CLRs, PCLRs must follow SCED basepoints when consuming energy2
Dynamic bid capping logic is added to ensure the PCLR will be dispatched rather than allowing the constraint to violate
1. Design and NPRR/PGRR language still under internal review and may change prior to filing | 2. On implementation of NPRR1188

## Slide 13: Provisional Controllable Load Resources (PCLRs) in Batch Zero1
ERCOT validates completion of all steps prior to granting Approval to Energize
8
QSE establishes required ICCP telemetry points
7
RE coordinates with ERCOT to establish metering and submit CLR parameters via RIOO
6
ILLE registers with ERCOT as a Resource Entity (RE) and designates a QSE
5
ERCOT studies the full load amount in the Batch Zero Refinement Study
4
ILLE submits updated Declaration to accept allocation amounts2
3
ERCOT studies PCLR in Batch Zero
2
Submission of Declaration and required information to ERCOT
(by July 24)
1
Must be done before non-firm load may energize
May be done in parallel with QSA
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
2. Failure to submit Form W removes project from the refinement story
Detailed next

## Slide 14: Post–Batch Zero, ILLE must elect path via Form W to retain position and proceed
Context
After Batch Zero results, each ILLE receives allocated LPC (firm) and MPC (total) values
To proceed, ILLE must submit Form W Part B election by deadline
Failure to elect leads to project being removed from Refinement study and loses queue position
Description
Option
Accept ERCOT-defined LPC and MPC values without modification
Maintains ability to consume above LPC, subject to PCLR qualification, dispatch, and bid capping
Accept PCLR as is
1
Elect to proceed as PCLR but reduce LPC and/or MPC below awarded levels
Provides flexibility while aligning with project readiness or infrastructure constraints
Accept PCLR with reduced values
2
Withdraw from PCLR and accept LPC values as firm load (with optional reduction), eliminating ability to exceed LPC
Withdraw PCLR, retain firm load
3
Withdraw from process
Decline participation and exit Batch Zero entirely
Project is removed from Refinement Study and must re-enter through a future process
4
Form W Part B election is binding and determines eligibility for Refinement Study and eventual energization. Failure to submit Form W Part B results in removal from Batch Zero

## Slide 15: Provision CLR (PCLR) – Dynamic Bid Capping Process
PUBLIC
1
SCED₋₁ (Previous Run)
After each SCED run, generate a fresh list of transmission constraints whose Shadow Price ≥ 90% of Max Shadow Price:
Constraint₁₂₃
Constraint₂₃₄
Constraint₃₄₅
Constraint₄₅₆
⚡ Shadow price threshold triggered
Match
2
SCEDcurrent (Before Step 2)
Compare the matching list against all active constraints in the current SCED run:
Constraint₂₃₄
Constraint₄₅₆
Constraint₆₇₈
Constraint₇₈₉
✔ 2 constraints match — evaluate PCLRs
Cap
3
SCED Step 2 (Bid Capped)
−0.02
Shift Factor Rule
Only PCLRs with a Shift Factor ≤ −0.02 on a matching constraint are eligible for bid capping
CAP
Bid Cap Applied
The PCLR's Energy Bid Curve is capped at the Adjusted Bid Cap (ABC) value before Step 2 executes
✓
Adjusted Bid Cap Formula:
ABC = Step 1 System Lambda − max ( MaxShadowPrice × ShiftFactor ) − $0.01 / MWh
Only applied where PCLR Shift Factor ≤ −0.02 | Constraint must appear in prior-run trigger list | No standard market mitigation applies to Energy Bid Curves

## Slide 16: A Bring Your Own Generation (BYOG) approach should help stakeholders to solve some of the issues raised with the LLI process
Interconnecting Large Load Entities (ILLEs) can co-develop or contract with co-located generation to:
Secure their own path to energization, independent of grid constraints
Align load ramp with generation availability
Reduce reliance on uncertain transmission upgrades
Intent of BYOG
Potential benefits
  For the ILLEs
  Greater certainty on energization timing and scale
  Ability to bypass grid-driven delays and curtailment risk
  For the generators
  Direct, contracted demand from day one
  Improved bankability vs. merchant exposure
  Clear role in solving interconnection bottlenecks
  For the system
  Accelerates capacity build where it is needed most
  Reduces congestion and transmission pressure
  Improves resource adequacy through demand-linked generation

## Slide 17: A coordinated load–generation study framework is required to enable a viable BYOG construct
Generation Interconnection (Normal GINR process – Planning Guide Section 5)
Large Load Interconnection (PGRR145 process – Planning Guide Section 9)
BYOG agreement
Detailed next
Monitoring and compliance
Establishing metering, telemetry, and real-time compliance mechanisms to ensure the facility continuously operates within its defined limits
Operations
Specifying the facility operating envelope (net import/export limits at POI) and dispatch/curtailment behavior for co-located load, generation, and storage
Study treatment
Defining an integrated study approach where load and generation are modeled as a single facility with consistent assumptions across planning and reliability analyses
Registration
Setting the registration model and load commitment requirements, aligning timing, scale, and obligations across generation and load interconnection processes

## Slide 18: Operational monitoring and control are required to ensure reliable WLPUN integration in Batch Zero
WLPUN
Key operational considerations
~
~
~
Generator
Load
Point of interconnection
ERCOT Grid
1,000MW
~
~
600MW
600MW
Import: max withdrawal limit (Batch study)
Export: available export (SCED dispatch)
Withdrawal limits (net) and stability limits (gross gen / gross load) must be monitored and enforced
Net and gross telemetry available; additional load telemetry can be requested by ERCOT
Additional control room tools and displays required to support real-time operations

## Slide 19: Study treatment should separate generation, load allocation and transmission planning while capturing full facility impact
Generation interconnection study
Studies generation independently under standard GINR assumptions to determine interconnection requirements and export capability
Batch Study
Evaluates load as grid-supplied only (co-located generation not counted) to determine firm load allocation based on system capability
Transmission planning study
Models load and generation together as a single facility to assess full system impact under N-1 (single-contingency) conditions (e.g., generator or transmission outages) and drives upgrades based on worst-case conditions
New discussion topic

## Slide 20: Co-located load and generation are governed by three separate ERCOT evaluation processes
Illustrative scheme
ERCOT lens
Description
Output
Batch Study (Load Interconnection)
Evaluates large load interconnections to determine the maximum import (withdrawal) capability under steady state conditions from the ERCOT grid, independent of on-site generation
Withdrawal limits1 and initial load allocation (subject to stability limits from Gen+Load studies)
Source: ERCOT discussions
1. Import (withdrawal) limit applies to total site demand, including co-located load and any storage charging | 2. Where generation and load share a POI, ERCOT/TSP studies may evaluate both independent and combined configurations; combined cases are particularly relevant for stability and system modeling
Focus
1,000MW
~
~
600MW
600MW
ERCOT Grid
1,000MW
~
~
600MW
600MW
1,000MW
~
~
600MW
600MW
Generation Interconnection
Assesses generation to determine export capability and interconnection requirements; co-located load is included in the study when it materially affects system performance (e.g., stability, voltage, operations)2
Maximum export (injection) limits, stability constraints, and interconnection requirements
ERCOT Grid
ERCOT Grid
1,000MW
~
~
600MW
600MW
Transmission planning
Identifies system constraints and determines network upgrades required to reliably support the combined load and generation under normal planning assumptions (e.g., N-1/G-1)
Required transmission upgrades and validation of SLF-exit (full load) conditions for reliable operation in the long-term (post-BYOG) configuration
ERCOT Grid
Final allowable load is determined by withdrawal limits (Batch Study) and may be further constrained by stability limits (Gen+Load studies) Example: Batch study sets a withdrawal limit of 100 MW. Stability studies identify a maximum stable load of 500 MW. Final allowable load = 500 MW, with up to 100 MW from the grid and the remainder supplied by on-site generation. If no stability constraint is identified, load can reach the full 1,000 MW using on-site generation

## Slide 21: PUN with Self-Limited Withdrawal (BYOG) – Operational Model
Interim operation (pre-transmission): BYOG agreement in place
Post-transmission operation: BYOG agreement exited
ERCOT Grid
1,000MW
~
~
600MW
600MW
New 400 MW transmission line
Export (injection): determined by SCED based on available surplus generation and dispatched at the resource level via COP/telemetry
Import (withdrawal): determined through batch study as a maximum withdrawal from the ERCOT grid, independent of co-located generation; total load cannot exceed identified stability limits
Operations: facility operates as a PUN with self-limited withdrawal
  Load is primarily served by on-site generation and must reduce load to remain within the withdrawal limit if generation is unavailable, within defined operational response times (e.g., cycles to seconds)
  Injection is governed by standard generation interconnection limits and SCED dispatch
SLF agreement dissolved and normal operations
Transmission upgrades: determined through ERCOT transmission planning studies, which evaluate the combined load and generation under standard reliability criteria (e.g., N-1 / G-1) to identify required network upgrades
Import and export: governed by standard interconnection limits and system constraints (no BYOG-specific caps); fully dispatchable through SCED subject to study results
Operations: transitions to standard ERCOT operation
  Generation and load treated as independent resources
  No self-limiting withdrawal requirement
  Full participation in market dispatch and planning
Source: ERCOT discussions
ERCOT Grid
1,000MW
~
~
600MW
600MW
Import: max withdrawal limit (Batch study)
Export: available export (SCED dispatch)

## Slide 22: Sequential BYOG interconnection timeline across Batch, Generation, and Transmission planning processes
Source: ERCOT discussions
Batch Study
Generation study
Transmission Planning
LLIS (meeting Batch Zero eligibility)
Jan 2027
Mar 2027
Developer commitment period (60 days)
BYOG declaration executed to identify load–generation pairing for studies (pre- PG 6.9 milestone of generation)
July 2026
Case building
Batch Study
~
~
Focus on load only
Upgrade identification
Focus on load and gen
Refinement study
Focus on load and gen
Gen FIS studies
Includes load FIS studies as applicable
(includes load for stability/operability assessment)
Focus on gen only
Focus on load and gen
Output: withdrawal limit
Output: stability limit (if any)
Total load allocation = min (Requested Load, Stability Limit – if any)

## Slide 23: ERCOT will need future NPRR on PUN Telemetry and RUC Requirements

## Slide 24: April 30th comments/approach: proposed “bookend” allocation Approach addresses developer ‘gap year’ concerns at the cost of extending the Batch Zero timeline
Example: 1,000 MW data center requiring full capacity by 2032
Chart: 
 | 300 | 300 | 500 | 500 | 1000
 | 100 | 200
2027
2028
2029
2030
2031
2032
400
700
Illustrative ramp schedule and allocation methodology by year, MW
Key highlights
Not studied: based on existing system capacity (no upgrades)
Fully studied (all cases)
Allocated with incremental transmission
Fully studied (all cases)
Allocated with incremental transmission
Fully studied (all cases)
Studied
Allocated
Adjusted “bookend” study approach: fully study 2028, 2030, and 2032, while allocating 2029 and 2031 using anchored transmission plans
Mitigates key developer concerns on “gap years” by avoiding zero-allocation outcomes:
  Improves project economics and bankability by providing interim MW visibility, reducing delayed revenues/underutilization
  Anchors allocation on years with major planned transmission additions (e.g., backbone upgrades)
Trade-off: additional 10 weeks of steady-state analysis, delaying Batch Zero results publication and potentially pushing the start of Batch 1
Enablers
Early TSP involvement at study kickoff, with a shared 2032 system case
Parallel development of transmission solutions and cost estimates
Centralized ERCOT coordination, consolidating TSP inputs into a single plan
Advantages
Delivers an actionable 2032 transmission plan within Batch Zero timeline, with full TSPs engagement and avoiding reliance on future cycles
Provides full 2027-2032 visibility for customer decisions
Reduces complexity and rework

## Slide 25: Batch Zero Adjusted Timelines Comparison
Activity
RPG Comment period and Board approval
Developer Commitment Deadline
Steady State Analysis (15 weeks)
Case Build (13 weeks)
Stability Screening Study + Final Report (16 weeks)
FAC-002 Stability + Batch Refinement Study ((14 weeks)
Aug
Sep
Oct
Nov
Jul
Dec
Feb
Mar
Apr
May
Jun
Aug
Oct
Jan
Dec
Nov
Sep
Jul
2026
2027
Old Batch Zero Timeline
Scenario
Potential Batch 1 start date (case building)
Activity getting extended
Batch Zero report published
RPG Comment period and Board approval
Developer Commitment Deadline
Steady State Analysis (15 weeks)
Case Build (13 weeks)
Stability Screening Study + Final Report (16 weeks)
FAC-002 Stability + Batch Refinement Study ((14 weeks)
“Rollover” Batch Zero Timeline – if needed
Extra 30 days for developer commitment
RPG Comment period and Board approval
Developer Commitment Deadline
Steady State Analysis (25 weeks)
Case Build (13 weeks)
Stability Screening Study + Final Report (16 weeks)
FAC-002 Stability + Batch Refinement Study ((14 weeks)
April 30th comments Batch Zero Timeline
Extra 30 days for developer commitment
Extra 10 weeks for steady state analysis

## Slide 26: Alternative option: "Rollover" approach
Old PGRR145 Approach
“Rollover” approach to subsequent batch
Example: 1,000 MW data center requiring full capacity by Year 6
Years 1-5
Request studied in Batch Zero: initial MWs allocated based on system capability; transmission constraints and required upgrades identified
Request studied in Batch Zero: initial MWs allocated based on system capability; transmission constraints and required upgrades identified
Considerations
Provides certainty by guaranteeing full MWs by Year 6
Creates a potential step-change in MWs between Years 5 and 6, with limited time to develop required transmission
Full MW allocation is aligned with identified transmission upgrades
Requires financial commitment for partial MWs without clear visibility on timing or certainty of full MW delivery
Year 6
Full MW automatically allocated based on Batch Zero results; transmission solutions further defined in the 2027 RTP
Full MW not committed in Batch Zero; additional MWs studied and allocated through a subsequent Batch 1 process
Chart: 
 | 0 | 100 | 450 | 600 | 600 | 1000
2027
2028
2029
2030
2031
2032
0
Illustrative ramp schedule, MW
Chart: 
 | 0 | 100 | 450 | 600 | 600 | 600
 | 400
2027
2028
2029
2030
2031
TBD
2032
0
Automatically set at requested peak Demand
TBD: additional MWs studied in next batch and allocated based on available capacity
Preferred alternative option

## Slide 27: Study effort scales non-linearly: later years require disproportionate effort
12 months (+24 weeks)
Timeline
6 months
8.5 months (+10 weeks)
Source: ERCOT discussions
Year
Key takeaways
Study effort is heavily back-loaded: final year (2032) requires disproportionately more effort than earlier years across all approaches
The “rollover” approach focuses on studying 2028–2031 within ~6 months, deliberately leaving 2032 to Batch 1 to avoid including the most effort-intensive year within the baseline timeline
The “bookend” approach includes 2032 within a limited ~10-week extension by assessing 2032 requirements early and identifying transmission elements that can be accelerated to support earlier years (e.g., 2029–2031), while trading depth in intermediate years (2029, 2031)
The “study all” approach maintains full depth across all years but requires a material timeline extension (~12 months total), reflecting the non-linear increase in effort
Total effort, % of “Rollover” approach
Year treatment
Effort, %
“Rollover” approach
1
100%
Year treatment
Effort, %
“Bookend” approach
2
140%
Fully studied
Fully studied
Fully studied
2028
10%
10%
10%
2030
Fully studied
20%
Fully studied
20%
Fully studied
20%
2032
Not studied (left to Batch 1)
-
Fully studied
100%
Fully studied
100%
Year treatment
Effort, %
“Study all” approach
2029
Fully studied
15%
Load allocation only studied
5%
15%
Fully studied
Fully studied
Load allocation only studied
2031
55%
5%
55%
Fully studied
3
200%
1
2
3
ILLUSTRATIVE
Detailed next

## Slide 28: 2032 is the primary driver of non-linear effort across scenarios
Source: ERCOT Board Meeting supporting materials, Feb 9-10; 9.1 System Planning and Weatherization Update
Key takeaways
Historical RTP data shows non-linear (exponential-like) scaling, with projects per GW almost doubling in recent years (from ~0.6 in 2016-22 to ~1.2 in 2023-25)
Complexity is driven not only by load, but also by system interactions:
  Location of generation and load (distance, congestion, zonal interactions)
  Need to model generation resources beyond ERCOT’s existing queue
Unlike RTP, studies cannot rely on placeholders or partial analysis and require fully resolved system configurations across all years
Study effort is constrained by limited parallelization, creating a plateau even with additional resources or tools (not expected to be in place for Batch Zero)
Fully studying 2032 requires significant coordination with TSPs to determine full load to be served, validate transmission feasibility and upgrades and identify opportunities to accelerate solutions into earlier years (e.g., 2030–2031)
Chart: 
| 89 | 89 | 85 | 89 | 93 | 92 | 94 | 111 | 152 | 159
 | 40 | 60 | 38 | 56 | 50 | 67 | 89 | 173 | 145 | 192
80
85
90
95
100
105
110
115
120
125
130
135
140
145
150
155
160
75
0
50
100
150
200
Total RTP Reliability Projects Proposed
2016
2017
2018
2019
2020
2021
2022
2023
2024
2025
Peak Load Level Studied in RTP
2016-2025 RTP summary by year, # of projects (Y-axis), GW (X-axis)
~0.6
~1.2
Average # of projects per GW
xx