April 2026 ERCOT Monthly Operations Report

Reliability and Operations Subcommittee Meeting

June 4, 2026

Table of Contents

1.	Report Highlights	2

2.	Frequency Control	3

2.1.	Frequency Events	3

2.2.	Automatic/Manual Load Resource Deployments	4

3.	Reliability Unit Commitment	5

4.	IRR, Wind, and Solar Generation as a Percent of Load	6

5.	Largest Net-Load Ramps	8

6.	Congestion Analysis	9

6.1.	Notable Constraints	9

6.2.	Generic Transmission Constraint Congestion	22

6.3.	Manual Overrides	22

6.4.	Congestion Costs for Calendar Year 2026	23

7.	System Events	24

7.1.	ERCOT Peak Load	24

7.2.	Load Shed Events	24

7.3.	Stability Events	25

7.4.	Notable PMU Events	25

7.5.	DC Tie Curtailment	25

7.6.	TRE/DOE Reportable Events	25

7.7.	New/Updated Constraint Management Plans	25

7.8.	New/Modified/Removed RAS	25

7.9.	New Procedures/Forms/Operating Bulletins	25

8.	Emergency Conditions	25

8.1.	OCNs	25

8.2.	Advisories	26

8.3.	Watches	26

8.4.	Emergency Notices	26

9.	Application Performance	26

9.1.	TSAT/VSAT Performance Issues	26

9.2.	Communication Issues	26

9.3.	Market System Issues	26

10.	Model Updates	26

Appendix A: Real-Time Constraints	29

# Report Highlights

The unofficial ERCOT peak load for April 2026 was 74,603 MW and occurred on 04/27/2026 during hour ending 17:00, this is 8,986 MW higher than the April 2025 demand of 65,617 MW on 04/14/2025 during hour ending 18:00.

On 15-minute settlement interval basis, maximum demand of 74,922 MW occurred on 4/27/2026 during interval ending 17:00 and minimum demand of 39,565 MW occurred on 4/20/2026 during interval ending 03:45.

There were 2 frequency events.

There were no events which required automatic/manual deployment of Load Resources that were controlled by an Under-Frequency Relays.

There was 1 Advisory due to the Space Weather Prediction Center issuing a GMD Warning of K-7.

There was 1 Advisory due to ERCOT’s Transient Security Assessment Tool being unavailable.

There was 1 Watch due to transmission watch for the Del Rio area due to planned and forced outages in the area.

There were 16 RUC commitments.

A Wind Penetration Record of 69.15% was set on 4/10/2022 at 01:43.

The following GTCs saw congestion in April:

| GTC | Days Congestion |
| --- | --- |
| Nelson Sharpe - Rio Hondo | 26 |
| North Edinburg - Lobo | 21 |
| Wharton | 20 |
| South Texas Export Pawnee - Spruce | 18 |
| East Texas | 17 |
| Panhandle | 16 |
| South Texas Export Pawnee - Tango | 16 |
| West Texas | 15 |
| North - Houston | 15 |
| South Texas Import Katoen - Lonhill | 9 |
| Kinney | 7 |
| Valley Export | 5 |
| McCamey | 5 |
| Zapata Starr | 4 |
| Uvalde | 1 |
| South - Far West | 1 |
| South Texas Import Pawnee - Spruce | 1 |

# Frequency Control

## Frequency Events

The ERCOT Interconnection experienced 2 frequency events.

A summary of the frequency events is provided below. The reported frequency events meet one of the following criteria: Delta Frequency is 60 mHz or greater; the MW loss is 350 MW or greater; resource trip event triggered ECRS deployment. Frequency events that have been identified as Frequency Measurable Events (FME) for purposes of BAL-001-TRE-2 analysis are highlighted in blue. When analyzing frequency events, ERCOT evaluates PMU data according to industry standards. Events with an oscillating frequency of less than 1 Hz are inter-area, while higher frequencies indicate local events. Industry standards specify that damping ratio for inter-area oscillations should be 3.0% or greater. For the frequency event listed below, the ERCOT system met these standards and transitioned well after the disturbance. In the case of negative delta frequency, the MW Loss column could refer to load loss.

| Date and Time | Delta Frequency | Max/Min Frequency | Duration of Event | PMU Data |  | MW Loss | Load | IRR | Inertia |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | (Hz) | (Hz) |  | Oscillation Mode (Hz) | Damping Ratio |  | (MW) | % | (MW-s) |
| 4/19/2026 2:13:25 | 0.053 | 59.962 | 00:02:00 | 0.6 | 13% | 543 | 41,195 | 34% | 187,358 |
| 4/28/2026 15:57:20 | 0.055 | 59.947 | 00:05:06 | 0.71 | 10% | 882 | 71,628 | 52% | 263,787 |

(Note: All data on this graph encompasses frequency event analysis based on BAL-001-TRE-2.)

## Automatic/Manual Load Resource Deployments

| Resource Location | # of Resources | Operating Day | Total # of Hours Committed | Total MWhs | Reason for Commitment | MWs of ECRS Deployed | MWs of RRS Deployed |
| --- | --- | --- | --- | --- | --- | --- | --- |

There were no events which required automatic/manual deployment of Load Resources that were controlled by an Under-Frequency Relays.

# Reliability Unit Commitment

ERCOT reports on Reliability Unit Commitments (RUC) monthly. Commitments are reported grouped by operating day and weather zone. The total number of hours committed is the sum of the hours for all the units in the specified region. Additional information on RUC commitments can be found on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

There were 16 RUC commitments.

| Resource Location | # of Resources | Operating Day | Total # of Hours Committed | Total MWhs | Reason for Commitment |
| --- | --- | --- | --- | --- | --- |
| NORTH_CENTRAL | 1 | April 1, 2026 | 8 | 456.0 | MKRWDHM5 |
| NORTH_CENTRAL | 2 | April 9, 2026 | 8 | 3,308.0 | MRAMBN25 |
| COAST, NORTH_CENTRAL, SOUTHERN | 3 | April 10, 2026 | 12 | 3,245.0 | MHCKRA25, SPAWSAN5 |
| NORTH_CENTRAL, SOUTHERN | 3 | April 15, 2026 | 13 | 5,263.0 | Capacity, Min Run Time |
| SOUTHERN | 1 | April 16, 2026 | 3 | 1,917.0 | Min Run Time |
| COAST, NORTH_CENTRAL | 2 | April 21, 2026 | 7 | 2,499.0 | Capacity, MRGRMGS5 |
| EAST, NORTH_CENTRAL | 4 | April 27, 2026 | 11 | 1,290.0 | DCDHTVW5, DNORSD85 |

# IRR, Wind, and Solar Generation as a Percent of Load

The graph below shows the maximum, minimum and average aggregate solar, wind and IRR output as a percentage of total ERCOT load when evaluated as 10-minute averaged intervals, over the past 13 months. Current wind and solar generation and penetration records are listed in the footnote below. Maximum IRR penetration for April 2026 was 80.27% on 4/19/2026 interval ending 11:20 and minimum IRR penetration for April 2026 was 8.26% on 4/24/2026 interval ending 20:10.

During the hour of peak load for the month, hourly integrated wind generation was 11,243 MW and solar generation was 22,054 MW. The graph below shows the wind and solar penetration percentage during the hour of the peak load in the last 13 months.

Lastly, the graph below shows the minimum wind, solar, and IRR output during the peak load hour as a percentage of the daily peak load for every day in the month.

# Largest Net-Load Ramps

The net-load ramp is defined as the change in net-load (load minus wind and PVGR generation) during the defined time horizon. Such a variation in net-load needs to be accommodated in grid operations to ensure that the reliability of the grid is satisfactorily maintained. The largest net-load ramps over 5-minute, 10-minute, 15-minute, 30-minute, and 60-minute intervals in April 2026 were 1,898 MW, 3,516 MW, 4,975 MW, 9,509 MW, and 18,089 MW respectively. A comparison with historical values is provided in the table below.

| Month and Year | 5 min | 10 min | 15 min | 30 min | 60 min |
| --- | --- | --- | --- | --- | --- |
| April 2015 | 835 MW | 1,482 MW | 1,985 MW | 3,216 MW | 5,330 MW |
| April 2016 | 1,183 MW | 1,666 MW | 2,394 MW | 3,804 MW | 5,101 MW |
| April 2017 | 914 MW | 1,492 MW | 2,315 MW | 3,779 MW | 6,385 MW |
| April 2018 | 947 MW | 1,366 MW | 1,710 MW | 3,303 MW | 5,030 MW |
| April 2019 | 1,147 MW | 1,778 MW | 1,866 MW | 2,866 MW | 4,856 MW |
| April 2020 | 1,189 MW | 1,655 MW | 1,578 MW | 2,773 MW | 4,948 MW |
| April 2021 | 1,414 MW | 1,664 MW | 1,967 MW | 2,874 MW | 4,860 MW |
| April 2022 | 1,218 MW | 1,594 MW | 2,179 MW | 4,191 MW | 7,851 MW |
| April 2023 | 1,282 MW | 2,452 MW | 3,583 MW | 6,640 MW | 12,352 MW |
| April 2024 | 1,418 MW | 2,720 MW | 3,640 MW | 6,769 MW | 12,282 MW |
| April 2025 | 1,744 MW | 3,396 MW | 4,768 MW | 9,032 MW | 16,541 MW |
| April 2026 | 1,898 MW | 3,516 MW | 4,975 MW | 9,509 MW | 18,089 MW |
|  | 4/6/2026 | 4/6/2026 | 4/6/2026 | 4/6/2026 | 4/6/2026 |
|  | (IE 18:23) | (IE 18:27) | (IE 18:32) | (IE 18:47) | (IE 19:17) |
| All Months in 2015-2026 | 2,276 MW | 3,516 MW | 5,018 MW | 9,696 MW | 18,089 MW |
|  | 2/6/2025 | 4/6/2026 | 2/24/2025 | 2/24/2025 | 4/6/2026 |
|  | (IE 6:05) | (IE 18:27) | (IE 17:39) | (IE 17:51) | (IE 19:17) |

# Congestion Analysis

## Notable Constraints

Nodal protocol section 3.20 specifies that ERCOT shall identify transmission constraints that are binding in Real-Time three or more Operating Days within a calendar month. As part of this process, ERCOT reports congestion that meets this criterion to ROS. In addition, ERCOT also highlights notable constraints that have an estimated congestion rent exceeding $1,000,000 for a calendar month. These constraints are detailed in the table below, including approved transmission upgrades from TPIT that may provide some congestion relief based on ERCOT’s engineering judgement. Rows highlighted in blue indicate the congestion was affected by one or more outages. For a list of all constraints activated in SCED, please see Appendix A at the end of this report.

| Contingency Name | Overloaded Element | Contingency Name | Overloaded Element | # of Days Constraint Binding | Congestion Rent | Transmission Project |
| --- | --- | --- | --- | --- | --- | --- |
| MHCKRA25 | HCKSW_MR2L | MANUAL HCKSW-RAMSW 345 kV_2 | Hicks Switch 138kV | 6 | $51,703,803.38 |  |  |
| BASE CASE | EASTEX | Basecase | EASTEX GTC | 16 | $21,112,784.36 |  |  |
| MSSNDBG5 | 421__A | MANUAL SINGLE SANDOW SWITCH to BADGER SWITCH 345 | Sandow Switch - Bell County East Switch 345kV | 20 | $15,349,924.53 |  |  |
| MRGRMGS5 | 6945__A | MAN_SGL_RGRSW-MGSES_345KV | Morgan Creek Ses - Cattleman Switch 345kV | 15 | $12,978,231.83 | West Texas 345-kV Infrastructure Rebuild Project (23RPG034) |  |
| BASE CASE | WESTEX | Basecase | WESTEX GTC | 11 | $12,320,073.49 | Permian Basin Reliability Plan (765-kV import paths) (The PUCT approved, helps improve, but not fully exit, the GTC yet.) |  |
| DTVWJON5 | 6033__A | TVWSW TO CPSES 345 AND CPSES TO JONSW 345 DBLCKT | Comanche Peak Ses - Mitchell Bend Switch 345kV | 2 | $10,001,621.45 |  |  |
| DSALKLN5 | 630__B | SALSW TO KLNSW 345 DBLCKT | Harker Heights South - Killeen Switch 138kV | 12 | $9,068,277.83 | ONCOR_SE_87699_Belton - Killeen 138 kV_Line (MOD 87699, 24RPG001) |  |
| DNORSD85 | 3610__G | NORSW TO CDHSW 345 AND NORSW TO MCSES 138 DBLCKT | Parkdale Switch - Pleasant Grove Tap 1 138kV | 4 | $8,737,525.67 |  |  |
| XVE2N58 | 945__B | VENUS SWITCH TRX VENSW_3_3 345/138 | Glen Heights - Sterrett 138kV | 5 | $8,541,207.93 |  |  |
| DBAKCED5 | 6965__A | BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Longshore Switch - Prairieland Switch 345kV | 18 | $8,030,254.37 | Oncor_FW_81268_Longshore – Consavvy 345 kV Double-Circuit Line Rebuild (MOD 81268, 23RPG034) |  |
| DCDHTVW5 | 3180__A | TVWSW TO CDHSW 345 AND CDHSW TO VENSW 345 DBLCKT | Fish Creek Switch - Cedar Hill Switch 138kV | 9 | $7,486,029.07 |  |  |
| DSALHUT5 | 421__A | SALSW - HUTTO 345KV | Sandow Switch - Bell County East Switch 345kV | 11 | $6,667,985.21 |  |  |
| MKRWDHM5 | EXCSW_MR1L | MANUAL KRWSW TO WDENT 345&KRWSW TO DHMSW 345 DBLCKT | Exchange Switch 138kV | 3 | $6,405,641.20 | Oncor_MW_RoanokeAreaProjects (MOD 70900, 21RPG003) |  |
| SMDOOAS5 | BG_GT_37_A | MEADOW to OASIS LIN A | Blodgett - Garrott 138kV | 8 | $5,961,167.68 |  |  |
| SLHLLCS5 | 1025__B | LAKE CREEK SES to LAKE CREEK SES LIN _A | Mclane Switch - Frow Sub 138kV | 13 | $5,594,647.63 |  |  |
| BASE CASE | NE_LOB | Basecase | NE_LOB GTC | 17 | $5,551,700.88 | San Antonio South Reliability I Project (22RPG048) LRGV Transmission Improvement Project (21RPG017) San Antonio South Reliability II Project (23RPG032) |  |
| SBWDDBM5 | LPLMK_LPLNE_1 | BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1 | Mackenzie Substation - Northeast Substation 115kV | 12 | $5,416,509.37 |  |  |
| DFOAVLO5 | NLARSW_PILONC1_1 | FOWLERTON to LOBO & AVANZADA | North Laredo Switch - Piloncillo 138kV | 21 | $5,352,944.64 |  |  |
| SPAWSAN5 | MAGRUD_VICTOR2_1 | SAN MIGUEL 345_138 KV SWITCHYARDS to PAWNEE SWITCHING STATION LIN 1 | Magruder - Victoria 138kV | 6 | $5,125,480.37 |  |  |
| DTRCFOR5 | 3610__G | TRCNR-SGVSW345kV&TRCNR-FORSW345KV_DBLCKT | Parkdale Switch - Pleasant Grove Tap 1 138kV | 2 | $5,056,539.35 |  |  |
| DMTSCOS5 | 6437__F | DMTSW TO SCOSW 345 DBLCKT | Knapp - Scurry Chevron 138kV | 20 | $4,716,212.27 | Oncor_FW_102849_Union 138 kV Switch (MOD 102849) |  |
| MLWSWDE5 | 587__A | MANUAL RNKSW TO WDENT 345&KRWSW TO DHMSW 345 DBLCKT | Argyle - Highlands Tnp 138kV | 7 | $4,666,502.84 |  |  |
| DCHBJO25 | CBY_AT3H | TWR (345) CHB-JOR97 & CBY-JOR99 | Cedar Bayou Plant 345kV | 11 | $4,478,283.68 | CNP_28TPIT99274_Cedar_Bayou_RPG_Substation_Upgrades (MOD 99274, 25RPG014) |  |
| SCRDJON5 | HOOD_DECRDVA_1 | CONCORD to CONCORD LIN G1 | Hood - Decordova Dam 138kV | 2 | $4,192,911.84 | ERCOT_25INR0231_APHL_ESS_Simple (MOD 86339) |  |
| DVENFTS5 | 505__B | VENSW-FTSSW & VENSW-SAMSW 345 DBLCKT | Tradinghouse Ses - Four Brothers Switch 345kV | 12 | $3,722,494.74 |  |  |
| BASE CASE | NELRIO | Basecase | NELRIO GTC | 24 | $3,494,947.23 | The Lower Rio Grande Valley (LRGV) System Enhancement Project (21RPG017) |  |
| BASE CASE | E_PASP | Basecase | E_PASP GTC | 12 | $3,265,574.25 | San Antonio South Reliability I Project, 22RPG048 LRGV Transmission Improvement Project (21RPG017) San Antonio South Reliability II Project (23RPG032) |  |
| MRNKDHM5 | 587__A | MANUAL RNKSW TO DHMSW 345&KRWSW TO DHMSW 345 DBLCKT | Argyle - Highlands Tnp 138kV | 7 | $3,140,430.72 |  |  |
| MBIKBHC8 | DT_PK_91_A | MANUAL TWR (138) BI-KB37 & GT-HOC90 | Downtown - Polk 138kV | 1 | $3,100,201.01 |  |  |
| DCHBJO25 | CBY_AT1H | TWR (345) CHB-JOR97 & CBY-JOR99 | Cedar Bayou Plant 345kV | 6 | $3,030,305.00 |  |  |
| MHARNED5 | BURNS_HEIDLBRG_1 | Manual dbl ckt for NEDIN-BONILLA 345kV & RIOH-PRIM138kV | Burns Sub - Heidelburg Sub 138kV | 16 | $2,932,814.93 | STEC_71926_Burns_Heidelberg_Upgrade (MOD 71926) |  |
| MPRLCO25 | 6960__A | MAN_SGL_PRLSW-CONSW_345KV_2 | Consavvy Switch - Prairieland Switch 345kV | 14 | $2,859,092.30 |  |  |
| SFMRRYS5 | 400__A | Farmersville Switch to Farmersville Switch LIN _A | Royse Switch - Farmersville Switch 345kV | 3 | $2,524,297.18 | ONCOR_MNE_99066_Royse Switch – Farmersville Switch 345 kV Double-Circuit Line (MOD 99066, 25RPG004) |  |
| SLHLTHS5 | 1025__B | LAKE HALL SWITCH to LAKE HALL SWITCH LIN _A | Mclane Switch - Frow Sub 138kV | 10 | $2,502,946.41 |  |  |
| DBUCRGP5 | 505__B | MANUAL DOUBLE RGPSW - KLNSW 345 KV & BUCSW - KLNSW 345 KV | Tradinghouse Ses - Four Brothers Switch 345kV | 8 | $2,464,448.36 |  |  |
| DRNS_TB5 | THWZEN71_A | Rns-Rtw & Sng-Tb 345kV | Th Wharton - Zenith 345kV | 8 | $2,303,774.23 |  |  |
| DTCRTHS5 | 35065__A | THSES TO FBRSW & TCRSW 345 DBLCKT | Fort Smith Switch - Files Valley Switch 345kV | 7 | $2,040,949.84 |  |  |
| SPAWSAN5 | COLETO_VICTOR2_1 | SAN MIGUEL 345_138 KV SWITCHYARDS to PAWNEE SWITCHING STATION LIN 1 | Coleto Creek - Victoria 138kV | 12 | $1,611,079.75 |  |  |
| DELMTEX5 | BLESSING_1382 | Elmcreek-STP 345kV | Blessing 345kV | 3 | $1,606,720.41 |  |  |
| DNORSD85 | 3150__A | NORSW TO CDHSW 345 AND NORSW TO MCSES 138 DBLCKT | Cedar Crest Switch - Oak Cliff South 138kV | 2 | $1,584,365.35 |  |  |
| BASE CASE | HHGTOM_1 | Basecase | Omega - Horse Hollow Generation Tie 345kV | 8 | $1,495,362.17 |  |  |
| DWAP_OB5 | MDOPHR99_A | TWR (345) OB-WAP98 & OB-WAP99 | Meadow - Ph Robinson 345kV | 8 | $1,451,079.42 | CNP_28TPIT103344_PH_Robinson_to_WA_Parish_Hardening (MOD 103344 Phase 103435, 25RPG028) |  |
| BASE CASE | WHARTN | Basecase | WHARTN GTC | 17 | $1,447,390.91 |  |  |
| SMDOOAS5 | GN_PZ_08_A | MEADOW to OASIS LIN A | Grant - Plaza 138kV | 4 | $1,352,422.04 |  |  |
| MCONPRL5 | 6470__E | MAN_DBL_PRLSW-CONSW_345KV | Polecat Creek Switch - Forsan Tap 138kV | 6 | $1,268,067.05 | ONCOR_FW_98953_McDonaldRoad_PolecatCreek_138kV (MOD 98953, 25RPG035) |  |
| DBAKCED5 | LAKENA_SAMATH1_1 | BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Lake Nasworthy - San Angelo Mathis Field 69kV | 8 | $1,218,141.77 |  |  |
| BASE CASE | PNHNDL | Basecase | PNHNDL GTC | 13 | $1,139,752.48 |  |  |
| DWPWFWP5 | DOWOAS18_A | TWR (345) WAP-WLF64 & WAP-WLY72 | Oasis - Dow Chemical 345kV | 5 | $1,065,594.74 |  |  |
| DNORCDH5 | 3610__G | NORSW TO LIGSW 345 AND NORSW TO CDHSW 345 AND NORSW AUTO1 DBLCKT | Parkdale Switch - Pleasant Grove Tap 1 138kV | 1 | $1,060,464.59 |  |  |
| DTCRTHS5 | 35055__A | THSES TO FBRSW & TCRSW 345 DBLCKT | Sam Switch - Venus Switch 345kV | 3 | $1,000,578.39 |  |  |
| SENSENW8 | 943__B | ENNIS SOUTH to ENNIS SOUTH LIN _C | Shankle Switch - Ennis West Switch 138kV | 9 | $997,533.25 |  |  |
| DBUCRGP5 | 506__A | MANUAL DOUBLE RGPSW - KLNSW 345 KV & BUCSW - KLNSW 345 KV | Four Brothers Switch - Sam Switch 345kV | 5 | $933,366.55 |  |  |
| DSALHUT5 | 270__A | SALSW - HUTTO 345KV | Temple Switch - Knob Creek Switch 345kV | 6 | $865,592.88 |  |  |
| DRESMCL8 | I_DUPS_RESNIK1_1 | I_DUPS - RESNIK & MCCAMPBE 2 138KV | Dupont Switch - Ingleside - Resnik 138kV | 8 | $781,295.69 |  |  |
| BASE CASE | I_KALO | Basecase | I_KALO GTC | 7 | $763,932.58 |  |  |
| DSCOTKW5 | 6215__A | SCOSW TO TKWSW 345 DBLCKT | Bluff Creek Switch - China Grove Switch 138kV | 4 | $723,962.29 |  |  |
| SMDOOAS5 | BCVPSA03_A | MEADOW to OASIS LIN A | Bigvue - Power Systems Arco Cogen 138kV | 8 | $688,321.02 |  |  |
| SWOLPAL8 | MIDW_OZONA1_1 | PALOUSE to Wolfcamp LIN 1 | Midway Lane - Ozona 69kV | 9 | $652,180.36 |  |  |
| SP5CAG8 | D5_S1_1 | CAGNON to CAGNON LIN 1 | Leon Creek - Howard 138kV | 4 | $642,707.70 |  |  |
| DTCRTHS5 | 35045__A | THSES TO FBRSW & TCRSW 345 DBLCKT | Sam Switch - Files Valley Switch 345kV | 9 | $634,350.83 |  |  |
| DBIGSCH5 | PALOUS_WOLFCA1_1 | Big Hill - Schneeman Draw & Big Hill - Schneeman Draw 2 | Palouse - Wolfcamp 138kV | 12 | $608,403.99 |  |  |
| SCARFRI8 | ATSO_SONR1_1 | Carver to Carver LIN 1 | Atlantic Sonora - Sonora 69kV | 17 | $526,994.36 |  |  |
| DBIGSCH5 | CROSSO_NORTMC1_1 | Big Hill - Schneeman Draw & Big Hill - Schneeman Draw 2 | North Mccamey - Crossover 138kV | 4 | $519,150.22 |  |  |
| SFMRRY25 | 381__A | Farmersville Switch to ROYSE SWITCH LIN _A | Farmersville Switch - Royse Switch 345kV | 6 | $502,069.69 |  |  |
| MDBGRBE5 | 36040__A | MANUAL SNDSW TO BCESW & SNDSW TO BGRSW 345 DBLCKT | Salado Switch - Knob Creek Switch 345kV | 3 | $481,557.72 |  |  |
| DLC_PG_8 | ARROZ_EL_CAM1_1 | TWR (138) GLF-PG60 & LC-NEW60 | Arroz - El Campo 138kV | 3 | $436,520.16 |  |  |
| SN_SLON5 | ALAZAN_B_DAVI1_1 | LON HILL to NELSON SHARPE LIN 1 | Barney Davis - Alazan 138kV | 6 | $430,916.94 |  |  |
| MHARNED5 | HAINE__LA_PAL1_1 | Manual dbl ckt for NEDIN-BONILLA 345kV & RIOH-PRIM138kV | Haine Drive - La Palma 138kV | 4 | $411,432.81 |  |  |
| DBIGSCH5 | SANTAR_WOLFCA1_1 | Big Hill - Schneeman Draw & Big Hill - Schneeman Draw 2 | Santa Rita - Wolfcamp 138kV | 7 | $401,939.42 |  |  |
| SPAWSAN5 | BLESSING_1382 | SAN MIGUEL 345_138 KV SWITCHYARDS to PAWNEE SWITCHING STATION LIN 1 | Blessing 345kV | 5 | $386,391.21 |  |  |
| DPAIMUR8 | 6635__G | GRAHAM SES to MURRAY and SUNECU | Morton Valley (Oncor) - Eastland 69kV | 11 | $382,271.95 |  |  |
| SFTLMES8 | CROSSO_NORTMC1_1 | FORT LANCASTER to FORT LANCASTER LIN 1 | North Mccamey - Crossover 138kV | 4 | $368,729.71 |  |  |
| DBIGKEN5 | FORTMA_YELWJC1_1 | Bighil-Kendal 345kV | Yellow Jacket - Fort Mason 138kV | 5 | $367,344.44 |  |  |
| DSALKLN5 | 315__A | SALSW TO KLNSW 345 DBLCKT | Temple Pecan Creek - Temple Switch 345kV | 3 | $362,690.73 |  |  |
| SHONF38 | HON_DEVI_1 | HONDO to HONDO CREEK SWITCHING STATION LIN 1 | Hondo Creek Switching Station - Devine Switch 69kV | 10 | $312,184.02 |  |  |
| DBUCRGP5 | FORTMA_YELWJC1_1 | MANUAL DOUBLE RGPSW - KLNSW 345 KV & BUCSW - KLNSW 345 KV | Yellow Jacket - Fort Mason 138kV | 7 | $311,420.58 |  |  |
| STARLEO8 | SOLSTICE_PST1 | LEON CREEK TNP to TARBUSH TNP LIN 1 | Solstice 138kV | 4 | $291,126.52 |  |  |
| MLNGPR25 | 16050__B | MAN_DBL_CATSW-PRLSW+LNGSW-PRLSW_345KV | Carterville - Hillger Sub 138kV | 3 | $279,051.84 |  |  |
| DRILKRW5 | BOW_FMR1 | RILEY TO KRWSW 345 DBLCKT | Bowie 138kV | 4 | $271,275.10 |  |  |
| DVICVI89 | COLETO_VICTOR2_1 | VICTORIA - FANNIN 69 & COLETO - VICTORIA 1 138 | Coleto Creek - Victoria 138kV | 4 | $261,257.18 |  |  |
| SBIGOR45 | FORTMA_YELWJC1_1 | Big HiLL to ORSTED LIN 1 | Yellow Jacket - Fort Mason 138kV | 4 | $253,135.17 |  |  |
| SCMNCPS5 | 651__B | COMANCHE SWITCH (Oncor) to COMANCHE PEAK SES LIN _A | Comanche Tap - Comanche Switch (Oncor) 138kV | 3 | $250,284.33 |  |  |
| SHONMOO8 | BIG_FO_PLEASA1_1 | MOORE SWITCHING STATION to HONDO CREEK SWITCHING STATION LIN 1 | Big Foot - Pleasanton 138kV | 5 | $232,587.06 |  |  |
| DFOAVLO5 | BRUNI_69_1 | FOWLERTON to LOBO & AVANZADA | Bruni Sub 138kV | 7 | $219,310.47 |  |  |
| DDILCOT8 | DILLEYSW_XF1H | Dilleysw-Sanmgsw&Cotulas 138kV | Dilley Switch Aep 138kV | 6 | $218,872.70 |  |  |
| SBRAPIN8 | HAMILT_MAVERI1_1 | BRACKETTVILLE to BRACKETTVILLE LIN 1 | Hamilton Road - Maverick 138kV | 11 | $161,583.14 |  |  |
| SILLFTL8 | CARVER_TINSLE1_1 | FORT LANCASTER to FORT LANCASTER LIN 1 | Carver - Tinsley Tap 138kV | 4 | $161,578.68 |  |  |
| SGRMGRS8 | 6830__B | GRAHAM EAST to GRAHAM EAST LIN _A | Cottonwood Road Switch - Olney Pod 69kV | 7 | $150,609.85 |  |  |
| DFOAVLO5 | ASHERT_CATARI1_1 | FOWLERTON to LOBO & AVANZADA | Asherton - Catarina 138kV | 6 | $137,118.09 |  |  |
| SPAWSAN5 | BLESSI_LOLITA1_1 | SAN MIGUEL 345_138 KV SWITCHYARDS to PAWNEE SWITCHING STATION LIN 1 | Blessing - Lolita 138kV | 11 | $135,334.32 |  |  |
| DMTSCOS5 | 6240__C | DMTSW TO SCOSW 345 DBLCKT | Sacroc - Deep Creek Sub 138kV | 7 | $131,476.22 |  |  |
| DFOAVLO5 | FREER_LOBO1_1 | FOWLERTON to LOBO & AVANZADA | Lobo - Freer 69kV | 3 | $127,774.14 |  |  |
| DTHSLCS5 | 1020__A | THSES TO LCSES 345 AND THSES TO TMPRCR 345 DBLCKT | Elm Mott - Mclennan County East 138kV | 3 | $124,715.17 |  |  |
| SPAWSAN5 | BLESSI_LOLITA1_1 | SAN MIGUEL 345_138 KV SWITCHYARDS to PAWNEE SWITCHING STATION LIN 1 | Blessing - Lolita 138kV | 11 | $118,669.92 |  |  |
| SPHRHDN8 | 138_NAL_HAS_1 | PH ROBINSON to HIDDEN LAKES TNP LIN 1 | North Alvin Tnp - Hastings Tnp 138kV | 4 | $106,289.46 |  |  |
| DBUCRGP5 | 651__B | MANUAL DOUBLE RGPSW - KLNSW 345 KV & BUCSW - KLNSW 345 KV | Comanche Tap - Comanche Switch (Oncor) 138kV | 5 | $103,947.66 |  |  |
| DLONPK25 | 12020__B | DBL_PKRSW-GRSES_PKRSW-LONSW_345KV | Barton Chapel Wind Farm - Juniper Sub 138kV | 4 | $102,062.43 |  |  |
| SCROPAL8 | MIDW_OZONA1_1 | Crossover to Crossover LIN 1 | Midway Lane - Ozona 69kV | 4 | $99,062.31 |  |  |
| SVICCO28 | COLETO_VICTOR2_1 | COLETO CREEK to VICTORIA LIN 1 | Coleto Creek - Victoria 138kV | 6 | $93,573.81 |  |  |
| SGU2BRK8 | 6635__G | BRECKENRIDGE NORTH to BRECKENRIDGE NORTH LIN _A | Morton Valley (Oncor) - Eastland 69kV | 4 | $80,835.85 |  |  |
| SPAWSAN5 | RAY_L_46_1 | SAN MIGUEL 345_138 KV SWITCHYARDS to PAWNEE SWITCHING STATION LIN 1 | Sam Rayburn Switchyd - Loop 463 Sub 138kV | 3 | $77,595.12 |  |  |
| BASE CASE | VALEXP | Basecase | VALEXP GTC | 5 | $75,191.03 |  |  |
| SFLTTUD8 | 6635__G | Flat Creek Switch to TUDOR SUB LIN _C | Morton Valley (Oncor) - Eastland 69kV | 3 | $74,686.91 |  |  |
| SBIGOR55 | FORTMA_YELWJC1_1 | Big HiLL to ORSTED LIN 1 | Yellow Jacket - Fort Mason 138kV | 5 | $73,779.77 |  |  |
| BASE CASE | MCCAMY | Basecase | MCCAMY GTC | 3 | $71,615.74 |  |  |
| SRICGRS8 | 6840__B | GRAHAM SES to RICE SWITCH LIN _A | Anarene - Navy Kickapoo Switch 69kV | 5 | $70,403.08 |  |  |
| DFOAVLO5 | LARDVN_LASCRU1_1 | FOWLERTON to LOBO & AVANZADA | Laredo Vft North - Las Cruces 138kV | 4 | $68,701.17 |  |  |
| DLONEQU8 | CLARK__LON_HI1_1 | Lon_Hill - Nueces & Equistar 138 kV | Clarkwood - Lon Hill 138kV | 8 | $67,711.30 |  |  |
| BASE CASE | ZAPSTR | Basecase | ZAPSTR GTC | 3 | $66,041.76 |  |  |
| SBIGOR55 | FORTMA_YELWJC1_1 | Big HiLL to ORSTED LIN 1 | Yellow Jacket - Fort Mason 138kV | 5 | $65,498.81 |  |  |
| SHLSWH28 | 2270__B | HILLSBORO to WHITNEY LIN _A | Milford Exxon Tap - Italy 69kV | 4 | $58,959.05 |  |  |
| XPRS58 | 1561__A | PARIS SWITCH TRX PRSSW_3_1 345/138 | Rivercrest Ses - Deport Rea 138kV | 3 | $55,105.93 |  |  |
| SLCSTH25 | 505__B | LAKE CREEK SES to LAKE CREEK SES LIN _A | Tradinghouse Ses - Four Brothers Switch 345kV | 3 | $49,534.40 |  |  |
| DFOWSMG5 | FWLRTN_TILDEN_1 | FOWLRTON TO SAN MIGUEL DOUBLE CIRCUIT CONTINGENCY | Fowlerton - Tilden 138 Sub 138kV | 3 | $47,641.53 |  |  |
| SMDOPHR5 | 138_ALV_NAL_1 | MEADOW to PH ROBINSON LIN A | North Alvin Tnp - Alvin Tnp 138kV | 7 | $29,825.83 |  |  |
| BASE CASE | E_PATA | Basecase | E_PATA GTC | 3 | $28,750.64 |  |  |
| BASE CASE | FURHMAN_VANDB_1 | Basecase | Furhman - Vanderbilt Switching Station 138kV | 3 | $24,626.43 |  |  |
| SFURVAN8 | RAYBUR_FURHMAN_1 | FURHMAN to VANDERBILT SWITCHING STATION LIN 1 | Sam Rayburn Switchyd - Furhman 138kV | 12 | $22,631.97 |  |  |
| SGRIRAP5 | MELONC_SEADRF1_1 | Grissom to RAPTOR LIN 1 | Melon Creek - Sea Drift Coke 138kV | 3 | $22,373.04 |  |  |
| SLARDUS8 | LARDVN_LOBO2_1 | Dust Devil to Dust Devil LIN 1 | Lobo - Laredo Vft North 138kV | 3 | $19,844.88 |  |  |
| DWESNUE8 | CLARK__LON_HI1_1 | WESTSIDE - MCKENZIE (138) & LON_HILL - NUECES_B (138) | Clarkwood - Lon Hill 138kV | 4 | $19,783.47 |  |  |
| SMA2SAP8 | MADDUX_SAPOWE1_1 | MADDUX to SAN ANGELO POWER STATION LIN 1 | Maddux - San Angelo Power Station 138kV | 4 | $17,766.75 |  |  |
| SWALWLN8 | BEN_ELMG_1 | WALLACE SWITCH to WALLACE SWITCH LIN 1 | Ben Davis - Elmgrove 138kV | 13 | $17,223.60 |  |  |
| SFURRAY8 | VAN_VNDB_1 | FURHMAN to SAM RAYBURN SWITCHYD LIN 1 | Vanderbilt Switching Station - Vanderbilt 69 Sub 69kV | 3 | $13,741.94 |  |  |
| SBIGOR45 | FORTMA_YELWJC1_1 | Big HiLL to ORSTED LIN 1 | Yellow Jacket - Fort Mason 138kV | 4 | $12,906.60 |  |  |
| BASE CASE | KINNEY | Basecase | KINNEY GTC | 7 | $12,411.01 |  |  |
| SSUNRGR8 | 6240__C | SUN SWITCH to RANGER CAMP SWITCH LIN _B | Sacroc - Deep Creek Sub 138kV | 6 | $11,815.94 |  |  |
| SBENS_M8 | BENTS_FRTER_1B_1 | SOUTH MCALLEN to BENTSEN LIN 1 | Frontera - South Mission 138kV | 11 | $10,764.31 |  |  |
| STARLEO8 | 138_FTS_LNC_1 | LEON CREEK TNP to TARBUSH TNP LIN 1 | Leon Creek Tnp - Fort Stockton Plant 138kV | 3 | $10,588.77 |  |  |
| BASE CASE | N_TO_H | Basecase | N_TO_H GTC | 3 | $5,553.56 |  |  |
| SSTAWIC8 | 138_IH2_COT_1 | STAGHORN TNP to WICKETT TNP LIN 1 | Ih 20 Tnp - Collie Field Tap Tnp 138kV | 9 | $5,068.56 |  |  |
| SBUZHMP8 | 6217__A | BUZZARD DRAW SWITCH to HARDY MORGAN POI LIN _B | Willow Valley Switch - Gail Sub 138kV | 4 | $4,354.44 |  |  |
| DTNFBCA8 | 138_FTS_LNC_1 | TNFXTAIL TO TARBUSH to BCATOKA 138KV | Leon Creek Tnp - Fort Stockton Plant 138kV | 3 | $1,708.59 |  |  |
| DSLKSOL5 | 138_FLT_FXT_1 | Sand Lake - Solstice line 1 and 2 | Foxtail Tnp - Flat Top Tnp 138kV | 4 | $1,233.36 |  |  |
| SMA2SAP8 | MADDUX_SAPOWE1_1 | MADDUX to SAN ANGELO POWER STATION LIN 1 | Maddux - San Angelo Power Station 138kV | 4 | $312.75 |  |  |

## Generic Transmission Constraint Congestion

| GTC | Days Congestion |
| --- | --- |
| Nelson Sharpe - Rio Hondo | 26 |
| North Edinburg - Lobo | 21 |
| Wharton | 20 |
| South Texas Export Pawnee - Spruce | 18 |
| East Texas | 17 |
| Panhandle | 16 |
| South Texas Export Pawnee - Tango | 16 |
| West Texas | 15 |
| North - Houston | 15 |
| South Texas Import Katoen - Lonhill | 9 |
| Kinney | 7 |
| Valley Export | 5 |
| McCamey | 5 |
| Zapata Starr | 4 |
| Uvalde | 1 |
| South - Far West | 1 |
| South Texas Import Pawnee - Spruce | 1 |

- There was no activity on the remaining GTCs during the month.

Note: This is how many times a constraint has been activated to avoid exceeding a GTC limit, it does not imply an exceedance of the GTC occurred or that the GTC was binding.

## Manual Overrides

- None

## Congestion Costs for Calendar Year 2026

The following table represents the top twenty active constraints for the calendar year based on the estimated congestion rent attributed to the congestion. ERCOT updates this list on a monthly basis.

| Contingency | Overloaded Element | # of 5-min SCED | Estimated | Transmission |
| --- | --- | --- | --- | --- |
| MANUAL HCKSW-RAMSW 345 kV_2 | Hicks Switch 138kV | 1,363 | 51,703,803.38 |  |
| Basecase | WESTEX GTC | 10,007 | 48,049,248.51 | Permian Basin Reliability Plan (765-kV import paths) (The PUCT approved, helps improve, but not fully exit, the GTC yet.) |
| BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Longshore Switch - Prairieland Switch 345kV | 9,760 | 42,980,091.93 | Oncor_FW_81268_Longshore – Consavvy 345 kV Double-Circuit Line Rebuild (MOD 81268, 23RPG034) |
| MANUAL RNKSW TO DHMSW 345&KRWSW TO DHMSW 345 DBLCKT | Argyle - Highlands Tnp 138kV | 6,190 | 33,556,097.10 |  |
| Basecase | EASTEX GTC | 3,197 | 31,386,366.96 |  |
| SALSW TO KLNSW 345 DBLCKT | Killeen Switch - Stagecoach 138kV | 2,796 | 31,304,486.27 | ONCOR_SE_87703_Belton_Killeen_138 kV Line (via Nolanville) (MOD 87703, 24RPG001) |
| DOUBLE NVARO-LEG & NVARO-OUTSW 345 KV | Big Brown Ses - Jewett 345kV | 504 | 26,003,760.95 | ONCOR_SE_99622_PIN_OAK_SWITCH (MOD 99622, 25RPG004) |
| BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1 | Mackenzie Substation - Northeast Substation 115kV | 4,989 | 22,062,182.24 |  |
| BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Hargrove - Twin Buttes 138kV | 3,820 | 20,180,720.69 |  |
| Basecase | E_PASP GTC | 6,753 | 19,261,881.50 | San Antonio South Reliability I Project , 22RPG048 LRGV Transmission Improvement Project (21RPG017) San Antonio South Reliability II Project (23RPG032) |
| STP-Elmcreek&WAP 345kV | South Texas Project - Elmcreek 345kV | 355 | 15,792,038.58 |  |
| SALSW TO KLNSW 345 DBLCKT | Harker Heights South - Killeen Switch 138kV | 3,026 | 15,749,905.34 | ONCOR_SE_87699_Belton - Killeen 138 kV_Line (MOD 87699, 24RPG001) |
| MANUAL SINGLE SANDOW SWITCH to BADGER SWITCH 345 | Sandow Switch - Bell County East Switch 345kV | 2,202 | 15,471,465.60 |  |
| FOWLERTON to LOBO & AVANZADA | Lobo - Laredo Vft North 138kV | 5,426 | 15,369,961.62 |  |
| MAN_SGL_RGRSW-MGSES_345KV | Morgan Creek Ses - Cattleman Switch 345kV | 2,380 | 14,991,540.47 | West Texas 345-kV Infrastructure Rebuild Project (23RPG034) |
| DMTSW TO SCOSW 345 DBLCKT | Knapp - Scurry Chevron 138kV | 6,798 | 14,841,359.52 | Oncor_FW_102849_Union 138 kV Switch (MOD 102849) |
| MEADOW to OASIS LIN A | Brays - H O Clarke 138kV | 2,124 | 14,775,630.35 |  |
| KENEDSW - TULETA (138) & PETTUS - BAEZ (69) | Coleto Creek - Rosata Tap 138kV | 538 | 14,029,054.48 | AEP_TCC_UpgradeColetoCreek-Rosata (MOD 50870, 20RPG014) |
| Basecase | NE_LOB GTC | 12,744 | 13,653,842.61 | San Antonio South Reliability I Project (22RPG048) LRGV Transmission Improvement Project (21RPG017) San Antonio South Reliability II Project (23RPG032) |
| Basecase | Omega - Horse Hollow Generation Tie 345kV | 5,965 | 13,335,150.26 |  |

# System Events

## ERCOT Peak Load

The unofficial ERCOT peak load for April 2026 was 74,603 MW and occurred on 04/27/2026 during hour ending 17:00, this is 8,986 MW higher than the April 2025 demand of 65,617 MW on 04/14/2025 during hour ending 18:00.  Instantaneous peak for April 2026 was 75,263 MW. Actual instantaneous peak for the same month last year was 66,286 MW.

## Load Shed Events

- None.

## Stability Events

- None.

## Notable PMU Events

ERCOT analyzes PMU data for any significant system disturbances that do not fall into the Frequency Events category reported in section 2.1. The results are summarized in this section once the analysis has been completed.

There were no PMU events outside of those reported in section 2.1.

## DC Tie Curtailment

- None.

## TRE/DOE Reportable Events

- Geronimo submitted a DOE-417 for 4/09/2026 – Physical threat to its facility that results from actual or suspected intentional human action.

- BPUB submitted a DOE-417 for 4/16/2026 – Physical threat to its facility that results from actual or suspected intentional human action.

- AEP submitted a DOE-417 for 4/25/2026 - Unexpected Transmission loss within its area, contrary to design, of three or more Bulk Electric System Facilities caused by a common disturbance.

- Sharyland submitted a DOE-417 for 4/29/2026 – Damage or Destruction of its Facility.

## New/Updated Constraint Management Plans

- None

## New/Modified/Removed RAS

- None

## New Procedures/Forms/Operating Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 4/30/2026 | Transmission and Security Desk Operating Procedure V2 Rev 5 | 2027 |
| 4/30/2026 | Shift Supervisor V2 Rev 3 | 2026 |
| 4/30/2026 | DC Tie Desk V2 Rev 2 | 2025 |

# Emergency Conditions

## OCNs

- None

## Advisories

| Date and Time | Message |
| --- | --- |
| April 3, 2026, 11:46 AM | Space Weather Prediction Center issuing a GMD Warning of K-7 on 4/3/26 11:02 until 04/03/2026 19:00. |
| April 10, 2026, 6:27:33 PM | Advisory issued due to ERCOT’s Transient Security Assessment Tool being unavailable until 4/10/2026 18:45:32 |

## Watches

| Date and Time | Message |
| --- | --- |
| April 15, 2026, 11:35:04 AM | Due to transmission watch for the Del Rio area due to planned and forced outages in the area until 4/15/2026 15:15:06 |

## Emergency Notices

- None

# Application Performance

## TSAT/VSAT Performance Issues

| Date and Time | Message |
| --- | --- |

## Communication Issues

- None.

## Market System Issues

- None.

# Model Updates

The Downstream Production Change (DPC) process allows ERCOT to make changes in the one-line Network Operations Model without loading a completely new model.  The purpose of this process is to allow for reliable grid operations as system conditions change between designated Network Operations Model database loads.  The DPC process is limited in scope to just those items listed below, with equipment ratings updates being the most common.  ERCOT has seen a rise in the use of the DPC process to make on-line updates to the Network Operations Model in recent years, instead of through the standard Network Operations Model Change Request process.

- Static Line ratings (Interim Update)

- Dynamic Line ratings (non-Interim Update)

- Autotransformer ratings (non-Interim Update)

- Breaker and Switch Normal status (Interim Update)

- Contingency Definitions (Interim Update)

- RAP and RAS changes or additions (Interim Update)

- Net Dependable and Reactive Capability (NDCRC) values (Interim Update)

- Impedance Updates (non-Interim)

A total of 62 DPCs were implemented in April 2026. 582 DPCs have been implemented year to date. DPCs submitted by TDSPs are mainly updates to transmission element ratings. DPCs submitted by ERCOT are mainly updates to manual contingency definitions.

| Transmission Operator | Number of DPCs |
| --- | --- |
| AEP TEXAS COMPANY (TDSP) | 7 |
| BRAZOS ELECTRIC POWER CO OP INC (TDSP) | 0 |
| BROWNSVILLE PUBLIC UTILITIES BOARD (TDSP) | 0 |
| BRYAN TEXAS UTILITIES (TDSP) | 0 |
| CENTERPOINT ENERGY HOUSTON ELECTRIC LLC (TDSP) | 6 |
| CITY OF AUSTIN DBA AUSTIN ENERGY (TDSP) | 0 |
| CITY OF COLLEGE STATION (TDSP) | 0 |
| CITY OF GARLAND (TDSP) | 0 |
| CPS ENERGY (TDSP) | 5 |
| CROSS TEXAS TRANSMISSION LLC (TSP)) | 0 |
| DENTON MUNICIPAL ELECTRIC (TDSP) | 0 |
| ELECTRIC TRANSMISSION TEXAS LLC (TDSP) | 2 |
| ERCOT | 2 |
| LCRA TRANSMISSION SERVICES CORPORATION (TDSP) | 32 |
| LONE STAR TRANSMISSION LLC (TSP) | 0 |
| ONCOR ELECTRIC DELIVERY COMPANY LLC (TDSP) | 6 |
| PEDERNALES ELECTRIC CO OP INC (TDSP) | 0 |
| RAYBURN COUNTRY CO OP DBA RAYBURN ELECTRIC (TDSP) | 0 |
| SHARYLAND UTILITIES LP (TDSP) | 1 |
| SOUTH TEXAS ELECTRIC CO OP INC (TDSP) | 0 |
| TEXAS MUNICIPAL POWER AGENCY (TDSP) | 0 |
| TEXAS-NEW MEXICO POWER CO (TDSP) | 1 |
| WIND ENERGY TRANSMISSION TEXAS LLC (TSP) | 0 |

# Appendix A: Real-Time Constraints

The following is a complete list of constraints activated in SCED. Full contingency descriptions can be found in the Standard Contingencies List located on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

| Year | Month | Contingency Name | Overloaded Element | From Station | To Station | Count of Days |
| --- | --- | --- | --- | --- | --- | --- |
| 2026 | April | BASE CASE | NELRIO | n/a | n/a | 26 |
| 2026 | April | BASE CASE | NE_LOB | n/a | n/a | 21 |
| 2026 | April | DFOAVLO5 | NLARSW_PILONC1_1 | NLARSW | PILONCIL | 21 |
| 2026 | April | DMTSCOS5 | 6437__F | SCRCV | KNAPP | 20 |
| 2026 | April | MSSNDBG5 | 421__A | BCESW | SNDSW | 20 |
| 2026 | April | BASE CASE | WHARTN | n/a | n/a | 20 |
| 2026 | April | SCARFRI8 | ATSO_SONR1_1 | SONR | ATSO | 20 |
| 2026 | April | DBAKCED5 | 6965__A | LNGSW | PRLSW | 19 |
| 2026 | April | BASE CASE | E_PASP | n/a | n/a | 18 |
| 2026 | April | SFURVAN8 | RAYBUR_FURHMAN_1 | FURHMAN | RAYBURN | 18 |
| 2026 | April | BASE CASE | EASTEX | n/a | n/a | 17 |
| 2026 | April | MHARNED5 | BURNS_HEIDLBRG_1 | MV_BURNS | MV_HBRG4 | 17 |
| 2026 | April | SBRAPIN8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 17 |
| 2026 | April | BASE CASE | E_PATA | n/a | n/a | 16 |
| 2026 | April | SBENS_M8 | BENTS_FRTER_1B_1 | FRONTERA | S_MISSIN | 16 |
| 2026 | April | BASE CASE | PNHNDL | n/a | n/a | 16 |
| 2026 | April | MRGRMGS5 | 6945__A | MGSES | CATSW | 16 |
| 2026 | April | DBIGSCH5 | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 15 |
| 2026 | April | BASE CASE | N_TO_H | n/a | n/a | 15 |
| 2026 | April | BASE CASE | WESTEX | n/a | n/a | 15 |
| 2026 | April | SLHLLCS5 | 1025__B | FROWS | MCLSW | 14 |
| 2026 | April | SWALWLN8 | BEN_ELMG_1 | BNDVS | ELMGROVE | 14 |
| 2026 | April | SPAWSAN5 | BLESSI_LOLITA1_1 | BLESSING | LOLITA | 14 |
| 2026 | April | SSTAWIC8 | 138_IH2_COT_1 | IH20 | TNCOLIET | 14 |
| 2026 | April | SPAWSAN5 | BLESSI_LOLITA1_1 | LOLITA | BLESSING | 14 |
| 2026 | April | SPAWSAN5 | COLETO_VICTOR2_1 | COLETO | VICTORIA | 14 |
| 2026 | April | SBWDDBM5 | LPLMK_LPLNE_1 | LPLMK | LPLNE | 14 |
| 2026 | April | MPRLCO25 | 6960__A | PRLSW | CONSW | 14 |
| 2026 | April | DVENFTS5 | 505__B | FBRSW | THSES | 13 |
| 2026 | April | DSALHUT5 | 421__A | BCESW | SNDSW | 13 |
| 2026 | April | DCHBJO25 | CBY_AT3H | CBY | CBY | 12 |
| 2026 | April | DFOAVLO5 | BRUNI_69_1 | BRUNI | BRUNI | 12 |
| 2026 | April | DSALKLN5 | 630__B | KLNSW | HHSTH | 12 |
| 2026 | April | DMTSCOS5 | 6240__C | SACRC | DPCRK | 12 |
| 2026 | April | SLHLTHS5 | 1025__B | FROWS | MCLSW | 12 |
| 2026 | April | DCDHTVW5 | 3180__A | FCRSW | CDHSW | 11 |
| 2026 | April | SMDOPHR5 | 138_ALV_NAL_1 | TNNALVIN | ALVIN | 11 |
| 2026 | April | DPAIMUR8 | 6635__G | MRVLY | ESTLD | 11 |
| 2026 | April | SMDOOAS5 | BCVPSA03_A | PSA | BCV | 10 |
| 2026 | April | DBUCRGP5 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 10 |
| 2026 | April | DBUCRGP5 | 505__B | FBRSW | THSES | 10 |
| 2026 | April | BASE CASE | HHGTOM_1 | HHGT | OMEGA | 10 |
| 2026 | April | SN_SLON5 | ALAZAN_B_DAVI1_1 | ALAZAN | B_DAVIS | 10 |
| 2026 | April | DLONEQU8 | CLARK__LON_HI1_1 | LON_HILL | CLARK_WD | 10 |
| 2026 | April | SVICCO28 | COLETO_VICTOR2_1 | COLETO | VICTORIA | 10 |
| 2026 | April | DRESMCL8 | I_DUPS_RESNIK1_1 | I_DUPSW | RESNIK | 10 |
| 2026 | April | DBAKCED5 | LAKENA_SAMATH1_1 | LAKENASW | SAMATHIS | 10 |
| 2026 | April | SHONF38 | HON_DEVI_1 | HONDOCK | DEVINESW | 10 |
| 2026 | April | SBUZHMP8 | 6217__A | WLVSW | GAILS | 9 |
| 2026 | April | DFOAVLO5 | ASHERT_CATARI1_1 | CATARINA | ASHERTON | 9 |
| 2026 | April | DTCRTHS5 | 35045__A | SAMSW | FVLSW | 9 |
| 2026 | April | DRNS_TB5 | THWZEN71_A | ZEN | THW | 9 |
| 2026 | April | SGRMGRS8 | 6830__B | CRDSW | OLNEY | 9 |
| 2026 | April | SHONMOO8 | BIG_FO_PLEASA1_1 | BIG_FOOT | PLEASANT | 9 |
| 2026 | April | SENSENW8 | 943__B | ENWSW | SHKSW | 9 |
| 2026 | April | BASE CASE | I_KALO | n/a | n/a | 9 |
| 2026 | April | SWOLPAL8 | MIDW_OZONA1_1 | OZONA | MIDW | 9 |
| 2026 | April | DFOAVLO5 | LARDVN_LASCRU1_1 | LARDVNTH | LASCRUCE | 8 |
| 2026 | April | DWAP_OB5 | MDOPHR99_A | MDO | PHR | 8 |
| 2026 | April | DTCRTHS5 | 35065__A | FVLSW | FTSSW | 8 |
| 2026 | April | SMDOOAS5 | BG_GT_37_A | GT | BG | 8 |
| 2026 | April | DBIGSCH5 | SANTAR_WOLFCA1_1 | WOLFCAMP | SANTARIT | 8 |
| 2026 | April | MRNKDHM5 | 587__A | ARGYL | LWSVH | 8 |
| 2026 | April | SBIGOR55 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 7 |
| 2026 | April | BASE CASE | KINNEY | n/a | n/a | 7 |
| 2026 | April | DSALHUT5 | 270__A | KNBSW | TMPSW | 7 |
| 2026 | April | SPAWSAN5 | BLESSING_1382 | BLESSING | BLESSING | 7 |
| 2026 | April | DLONPK25 | 12020__B | BRTSW | JUNPR | 7 |
| 2026 | April | SPAWSAN5 | RAY_L_46_1 | RAYBURN | L_463S | 7 |
| 2026 | April | SPAWSAN5 | RAY_L_46_1 | L_463S | RAYBURN | 7 |
| 2026 | April | DWESNUE8 | CLARK__LON_HI1_1 | LON_HILL | CLARK_WD | 7 |
| 2026 | April | DDILCOT8 | DILLEYSW_XF1H | DILLEYSW | DILLEYSW | 7 |
| 2026 | April | SBIGOR55 | FORTMA_YELWJC1_1 | FORTMA | YELWJCKT | 7 |
| 2026 | April | SPAWSAN5 | MAGRUD_VICTOR2_1 | VICTORIA | MAGRUDER | 7 |
| 2026 | April | MLWSWDE5 | 587__A | ARGYL | LWSVH | 7 |
| 2026 | April | DBUCRGP5 | 651__B | CMNSW | CMNTP | 6 |
| 2026 | April | SFTLMES8 | CROSSO_NORTMC1_1 | NORTMC | CROSSOVE | 6 |
| 2026 | April | SPHRHDN8 | 138_NAL_HAS_1 | TNNALVIN | HASTINGS | 6 |
| 2026 | April | DRILKRW5 | BOW_FMR1 | BOW | BOW | 6 |
| 2026 | April | DCHBJO25 | CBY_AT1H | CBY | CBY | 6 |
| 2026 | April | SSUNRGR8 | 6240__C | SACRC | DPCRK | 6 |
| 2026 | April | SRICGRS8 | 6840__B | NVKSW | ANARN | 6 |
| 2026 | April | MHCKRA25 | HCKSW_MR2L | HCKSW | HCKSW | 6 |
| 2026 | April | DSCOTKW5 | 6215__A | BCKSW | CGRSW | 6 |
| 2026 | April | DBUCRGP5 | 506__A | SAMSW | FBRSW | 6 |
| 2026 | April | SMA2SAP8 | MADDUX_SAPOWE1_1 | MADDUX | SAPOWER | 6 |
| 2026 | April | SMA2SAP8 | MADDUX_SAPOWE1_1 | SAPOWER | MADDUX | 6 |
| 2026 | April | SFMRRY25 | 381__A | FMRVL | RYSSW | 6 |
| 2026 | April | MCONPRL5 | 6470__E | PCTSW | FRSTP | 6 |
| 2026 | April | DBIGSCH5 | CROSSO_NORTMC1_1 | NORTMC | CROSSOVE | 6 |
| 2026 | April | DBIGKEN5 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 6 |
| 2026 | April | XPRS58 | 1561__A | DPREA | RCSES | 5 |
| 2026 | April | MLNGPR25 | 16050__B | CRTRVLLE | HILGR | 5 |
| 2026 | April | SLARDUS8 | LARDVN_LOBO2_1 | LOBO | LARDVNTH | 5 |
| 2026 | April | DWPWFWP5 | DOWOAS18_A | DOW | OAS | 5 |
| 2026 | April | DSLKSOL5 | 138_FLT_FXT_1 | TNFXTAIL | FLAT_TOP | 5 |
| 2026 | April | SGU2BRK8 | 6635__G | MRVLY | ESTLD | 5 |
| 2026 | April | SCROPAL8 | MIDW_OZONA1_1 | OZONA | MIDW | 5 |
| 2026 | April | DLOFOAV5 | ASHERT_CATARI1_1 | ASHERTON | CATARINA | 5 |
| 2026 | April | DLOFOAV5 | ASHERT_CATARI1_1 | CATARINA | ASHERTON | 5 |
| 2026 | April | DSALHUT5 | 455__A | BGRSW | SNDSW | 5 |
| 2026 | April | DFOWSMG5 | FWLRTN_TILDEN_1 | FOWLRTON | TILDEN | 5 |
| 2026 | April | BASE CASE | VALEXP | n/a | n/a | 5 |
| 2026 | April | BASE CASE | MCCAMY | n/a | n/a | 5 |
| 2026 | April | XVE2N58 | 945__B | GLNHT | STERT | 5 |
| 2026 | April | DGRMGRS8 | 6830__B | CRDSW | OLNEY | 4 |
| 2026 | April | SILLFTL8 | CARVER_TINSLE1_1 | CARVER | TINSLEY | 4 |
| 2026 | April | SBRAHAM8 | ESCOND_GANSO1_1 | GANSO | ESCONDID | 4 |
| 2026 | April | DYETRJU8 | MADDUX_SAPOWE2_1 | MADDUX | SAPOWER | 4 |
| 2026 | April | DVICVI89 | COLETO_VICTOR2_1 | COLETO | VICTORIA | 4 |
| 2026 | April | SHLSWH28 | 2270__B | ITALY | MEXTP | 4 |
| 2026 | April | SBIGOR45 | FORTMA_YELWJC1_1 | FORTMA | YELWJCKT | 4 |
| 2026 | April | SMDOOAS5 | GN_PZ_08_A | GN | PZ | 4 |
| 2026 | April | STARLEO8 | 138_FTS_LNC_1 | LEONCRK | FTST | 4 |
| 2026 | April | DELMTEX5 | BLESSING_1382 | BLESSING | BLESSING | 4 |
| 2026 | April | DNORSD85 | 3610__G | PGTP1 | PDSES | 4 |
| 2026 | April | SFMRRYS5 | 400__A | FMRVL | RYSSW | 4 |
| 2026 | April | SP5CAG8 | D5_S1_1 | HOWARD | LEON_CRK | 4 |
| 2026 | April | SBRAHAM8 | ESCOND_GANSO1_1 | ESCONDID | GANSO | 4 |
| 2026 | April | SBCESN35 | 455__A | BGRSW | SNDSW | 4 |
| 2026 | April | SBIGOR45 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 4 |
| 2026 | April | DFOAVLO5 | FREER_LOBO1_1 | LOBO | FREER | 4 |
| 2026 | April | MHARNED5 | HAINE__LA_PAL1_1 | LA_PALMA | HAINE_DR | 4 |
| 2026 | April | STARLEO8 | SOLSTICE_PST1 | SOLSTICE | SOLSTICE | 4 |
| 2026 | April | SHLSWH28 | 2270__B | MEXTP | ITALY | 4 |
| 2026 | April | BASE CASE | ZAPSTR | n/a | n/a | 4 |
| 2026 | April | SKLNSAL5 | 271__A | KLNSW | SALSW | 3 |
| 2026 | April | BASE CASE | MAXWEL_WHITIN1_1 | MAXWELL | WHITING | 3 |
| 2026 | April | MKRWDHM5 | EXCSW_MR1L | EXCSW | EXCSW | 3 |
| 2026 | April | SMOOPEA8 | PALDRO_DILLEY_1 | PALODURO | DILLEYSW | 3 |
| 2026 | April | DTCRTHS5 | 35055__A | SAMSW | VENSW | 3 |
| 2026 | April | DTHSFBR5 | 35055__A | SAMSW | VENSW | 3 |
| 2026 | April | SLCSTH25 | 505__B | FBRSW | THSES | 3 |
| 2026 | April | DLC_PG_8 | ARROZ_EL_CAM1_1 | ARROZ | EL_CAMPO | 3 |
| 2026 | April | DTHSLCS5 | 1020__A | ELMOT | MCTYE | 3 |
| 2026 | April | DSALKLN5 | 315__A | TMPCR | TMPSW | 3 |
| 2026 | April | MDBGRBE5 | 36040__A | KNBSW | SALSW | 3 |
| 2026 | April | BASE CASE | FURHMAN_VANDB_1 | FURHMAN | VANBLTSS | 3 |
| 2026 | April | UCOLCOL1 | BLESSI_LOLITA1_1 | BLESSING | LOLITA | 3 |
| 2026 | April | DMLSENT5 | ELKTN_MR3L | ELKTN | ELKTN | 3 |
| 2026 | April | DCOTWR25 | FARMLAND_LONGD_1 | FARMLAND | W_LD_345 | 3 |
| 2026 | April | SSNYCGR8 | SNYDR_FMR1 | SNYDR | SNYDR | 3 |
| 2026 | April | DSALHUT5 | 713T713_1 | LAMPAS | NARUNA | 3 |
| 2026 | April | DILLFR89 | MIDW_OZONA1_1 | OZONA | MIDW | 3 |
| 2026 | April | DTNFBCA8 | 138_FTS_LNC_1 | FTST | LEONCRK | 3 |
| 2026 | April | SFLTTUD8 | 6635__G | MRVLY | ESTLD | 3 |
| 2026 | April | SGRIRAP5 | MELONC_SEADRF1_1 | SEADRFTC | MELONCRE | 3 |
| 2026 | April | SFTLMES8 | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 3 |
| 2026 | April | SFURRAY8 | VAN_VNDB_1 | VANBLTSS | VANBLT69 | 3 |
| 2026 | April | MSBCEBG5 | 421__A | BCESW | SNDSW | 3 |
| 2026 | April | SCMNCPS5 | 651__B | CMNSW | CMNTP | 3 |
| 2026 | April | SCSDNK8 | BCVPSA03_A | PSA | BCV | 3 |
| 2026 | April | DLONPK25 | 6375__A | GRSES | GRMES | 2 |
| 2026 | April | SBENRAI8 | BENTS_FRTER_1B_1 | S_MISSIN | FRONTERA | 2 |
| 2026 | April | DVICCO89 | COLETO_VICTOR1_1 | COLETO | VICTORIA | 2 |
| 2026 | April | SGBYSD25 | GBYLYD70_A | LYD | GBY | 2 |
| 2026 | April | SBRAHAM8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 2 |
| 2026 | April | DRAPFA59 | MELONC_SEADRF1_1 | SEADRFTC | MELONCRE | 2 |
| 2026 | April | DBLW2JC5 | WAPWLY72_A | WLY | WAP | 2 |
| 2026 | April | DNORSD85 | 3150__A | OKCLS | CDCSW | 2 |
| 2026 | April | DSTPHLJ5 | BLESSING_1382 | BLESSING | BLESSING | 2 |
| 2026 | April | DCC1DUKE | BURNS_HEIDLBRG_1 | MV_BURNS | MV_HBRG4 | 2 |
| 2026 | April | MBIKBHC8 | DT_PK_91_A | DT | PK | 2 |
| 2026 | April | DTHWZEN5 | MDOPHR99_A | MDO | PHR | 2 |
| 2026 | April | MBONMAN5 | WESLCO_HIDLBRG_1 | MV_HBRG4 | MV_WESL4 | 2 |
| 2026 | April | DSAMFBR5 | 35045__A | SAMSW | FVLSW | 2 |
| 2026 | April | DTRCFOR5 | 3610__G | PGTP1 | PDSES | 2 |
| 2026 | April | SCARFRI8 | ATSO_OZNC1_1 | ATSO | OZNC | 2 |
| 2026 | April | SLKAWFS8 | BOW_FMR1 | BOW | BOW | 2 |
| 2026 | April | XCRD58 | CRD_CRD2 | CRD | CRD | 2 |
| 2026 | April | SBRAPIN8 | ESCOND_GANSO1_1 | GANSO | ESCONDID | 2 |
| 2026 | April | SWCPYT8 | LAN_CT_PAVLOV1_1 | LAN_CTY | PAVLOV | 2 |
| 2026 | April | SWMMLCS8 | 1025__B | FROWS | MCLSW | 2 |
| 2026 | April | BASE CASE | 138_FTS_LNC_1 | FTST | LEONCRK | 2 |
| 2026 | April | SDUKNED8 | HEC_NEDIN2_1 | HEC | NEDIN | 2 |
| 2026 | April | BASE CASE | RAYBUR_FURHMAN_1 | FURHMAN | RAYBURN | 2 |
| 2026 | April | DVANELT8 | VAN_VNDB_1 | VANBLTSS | VANBLT69 | 2 |
| 2026 | April | DKLNRGP5 | 506__A | SAMSW | FBRSW | 2 |
| 2026 | April | MCATPRL5 | 6965__A | LNGSW | PRLSW | 2 |
| 2026 | April | DWAP_BI5 | BI_JN_64_A | JN | BI | 2 |
| 2026 | April | SBRAESC8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 2 |
| 2026 | April | DBAKCED5 | HARGRO_TWINBU1_1 | TWINBU | HARGROVE | 2 |
| 2026 | April | SPAWSAN5 | LOOP_VICTORIA_1 | VICTORIA | L_463S | 2 |
| 2026 | April | DRNS_TB5 | MDOPHR99_A | MDO | PHR | 2 |
| 2026 | April | SFTLMES8 | MIDW_OZONA1_1 | OZONA | MIDW | 2 |
| 2026 | April | SMCEABS8 | MKLT_TRNT1_1 | TRNT | MKLT | 2 |
| 2026 | April | DCEDERE5 | NLARSW_UNITEC1_1 | NLARSW | UNITEC | 2 |
| 2026 | April | DDNEDBP5 | NLARSW_UNITEC1_1 | NLARSW | UNITEC | 2 |
| 2026 | April | DWPWFWP5 | 155T217_1 | BELLSO | PT | 2 |
| 2026 | April | DRAZSA89 | 2585_1 | DOWNIES | MOORE | 2 |
| 2026 | April | DTHSFBR5 | 35065__A | FVLSW | FTSSW | 2 |
| 2026 | April | SVENFTS5 | 505__B | FBRSW | THSES | 2 |
| 2026 | April | DSCOTKW5 | 6474__B | SUNSW | RGRSW | 2 |
| 2026 | April | SPEBTRU8 | 940__A | ENWSW | TMPTN | 2 |
| 2026 | April | XPEA89 | DILLEYSW_XF1H | DILLEYSW | DILLEYSW | 2 |
| 2026 | April | DMCEBUT8 | MKLT_TRNT1_1 | TRNT | MKLT | 2 |
| 2026 | April | SPAWCAL5 | SMG_ELMCRK1_1 | SANMIGL | ELMCREEK | 2 |
| 2026 | April | DBIGKEN5 | TREADW_YELWJC1_1 | TREADWEL | YELWJCKT | 2 |
| 2026 | April | DGDLBLT5 | 325__A | BLFSW | TMPCR | 2 |
| 2026 | April | DVENFTS5 | 506__A | SAMSW | FBRSW | 2 |
| 2026 | April | DDILPE89 | BIG_FO_PLEASA1_1 | BIG_FOOT | PLEASANT | 2 |
| 2026 | April | DFOWSMG5 | GEO_SIG_1 | GEOWEST | SIGMOR | 2 |
| 2026 | April | SPAWSAN5 | LOOP_VICTORIA_1 | L_463S | VICTORIA | 2 |
| 2026 | April | SBIGOR45 | MADDUX_TREADW1_1 | MADDUX | TREADWEL | 2 |
| 2026 | April | DLOFOAV5 | NLARSW_PILONC1_1 | NLARSW | PILONCIL | 2 |
| 2026 | April | BASE CASE | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 2 |
| 2026 | April | SBLURDH8 | 2270__B | MEXTP | ITALY | 2 |
| 2026 | April | MLNGPR25 | 5010__A | PRMSW | RCKSW | 2 |
| 2026 | April | DFVLFTS5 | 505__B | FBRSW | THSES | 2 |
| 2026 | April | DSCOTKW5 | 6437__F | SCRCV | KNAPP | 2 |
| 2026 | April | SFLTLNG8 | 6635__G | MRVLY | ESTLD | 2 |
| 2026 | April | XGRS58 | 6635__G | MRVLY | ESTLD | 2 |
| 2026 | April | DKOCLO89 | CLARK__LON_HI1_1 | LON_HILL | CLARK_WD | 2 |
| 2026 | April | DHONHON8 | DEV_NATA_1 | DEVINESW | NATALISS | 2 |
| 2026 | April | DKLNRGP5 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 2 |
| 2026 | April | SILLFTL8 | HAMILT_MAXWEL1_1 | MAXWELL | HAMILTON | 2 |
| 2026 | April | SCRDJON5 | HOOD_DECRDVA_1 | DCDAM | HOD | 2 |
| 2026 | April | SI_2RES8 | I_DUPS_RESNIK3_3 | I_DUPSW | RESNIK | 2 |
| 2026 | April | SZENTHW5 | THWZEN98_A | ZEN | THW | 2 |
| 2026 | April | SFBRTHS5 | 35055__A | SAMSW | VENSW | 2 |
| 2026 | April | DSAMFVL5 | 505__B | FBRSW | THSES | 2 |
| 2026 | April | SBNBPK25 | 6005__A | PKRSW | BNBSW | 2 |
| 2026 | April | DTVWJON5 | 6033__A | CPSES | MBDSW | 2 |
| 2026 | April | DCPSES12 | 35065__A | FVLSW | FTSSW | 1 |
| 2026 | April | STHSVE65 | 505__B | FBRSW | THSES | 1 |
| 2026 | April | SCRDJON5 | 651__B | CMNSW | CMNTP | 1 |
| 2026 | April | DABPAB98 | 6635__G | MRVLY | ESTLD | 1 |
| 2026 | April | SSCLWF18 | 6840__B | NVKSW | ANARN | 1 |
| 2026 | April | DSWETKW5 | 6945__A | MGSES | CATSW | 1 |
| 2026 | April | XJN58 | BI_AT5 | BI | BI | 1 |
| 2026 | April | SCITWEI8 | CLARK__LON_HI1_1 | LON_HILL | CLARK_WD | 1 |
| 2026 | April | DBAKCED5 | CROSSO_PALOUS1_1 | PALOUSE | CROSSOVE | 1 |
| 2026 | April | DWAP_OB5 | DT_PK_91_A | PK | DT | 1 |
| 2026 | April | SMDOOAS5 | GV_HOC19_A | HOC | GV | 1 |
| 2026 | April | BASE CASE | I_FW_S | n/a | n/a | 1 |
| 2026 | April | DTWLCED5 | LVOK_SANTIA1_1 | SANTIAGO | LVOK | 1 |
| 2026 | April | BASE CASE | MDOPHR99_A | MDO | PHR | 1 |
| 2026 | April | SMV_PAR8 | RIOHND_ERIOHND_1 | MV_RIOHO | RIOHONDO | 1 |
| 2026 | April | XHLS289 | ROC_ROCK_1 | ROCKETT | ROCKETSW | 1 |
| 2026 | April | DSALHUT5 | SNDSW_MR1H | SNDSW | SNDSW | 1 |
| 2026 | April | DRAZSA89 | UVALDE_W_BATE1_1 | UVALDE | W_BATESV | 1 |
| 2026 | April | SWORBRD8 | 138_WIC_STG_1 | WICKETT | STAGHORN | 1 |
| 2026 | April | DSSPMNS5 | 1650__C | MNTTP | SLBLF | 1 |
| 2026 | April | DNORCDH5 | 3610__G | PGTP1 | PDSES | 1 |
| 2026 | April | DBWNRGP5 | 505__B | FBRSW | THSES | 1 |
| 2026 | April | STCRTHS5 | 505__B | FBRSW | THSES | 1 |
| 2026 | April | DCDHTVW5 | 6200__D | SHRSW | PRKRW | 1 |
| 2026 | April | SBEAOR8 | ARROZ_EL_CAM1_1 | ARROZ | EL_CAMPO | 1 |
| 2026 | April | STANPAW5 | BLESSI_LOLITA1_1 | BLESSING | LOLITA | 1 |
| 2026 | April | DFOAVLO5 | CATARI_PILONC1_1 | PILONCIL | CATARINA | 1 |
| 2026 | April | SMDOOAS5 | DT_PK_91_A | PK | DT | 1 |
| 2026 | April | DBWNRGP5 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 1 |
| 2026 | April | SOXYIN28 | I_DUPP_I_DUPS2_1 | I_DUPP1 | I_DUPSW | 1 |
| 2026 | April | SNEWGLF8 | LAN_CT_PAVLOV1_1 | LAN_CTY | PAVLOV | 1 |
| 2026 | April | SLC2CAS8 | LCRANE_RIOPEC1_1 | RIOPECOS | LCRANE | 1 |
| 2026 | April | MANGGRI5 | MELONC_SEADRF1_1 | SEADRFTC | MELONCRE | 1 |
| 2026 | April | DCENRAP5 | NLARSW_UNITEC1_1 | NLARSW | UNITEC | 1 |
| 2026 | April | DELMSAN5 | PAWNEE_SPRUCE_1 | PAWNEE | CALAVERS | 1 |
| 2026 | April | SSANEL25 | PAWNEE_SPRUCE_1 | PAWNEE | CALAVERS | 1 |
| 2026 | April | DSNG_TB5 | THWZEN71_A | ZEN | THW | 1 |
| 2026 | April | DBUCRGP5 | CMNSW_MR1H | CMNSW | CMNSW | 1 |
| 2026 | April | SVICCOL8 | COLETO_VICTOR1_1 | COLETO | VICTORIA | 1 |
| 2026 | April | SHONF38 | DEV_NATA_1 | DEVINESW | NATALISS | 1 |
| 2026 | April | DCPSES12 | FORTMA_YELWJC1_1 | FORTMA | YELWJCKT | 1 |
| 2026 | April | SMDOPHR5 | G138_8A_1 | HDNLAKES | PHR | 1 |
| 2026 | April | DFALREV8 | GATEWT_WORMSE1_1 | GATEWTP | WORMSER | 1 |
| 2026 | April | DNUEGIL8 | MCKENZ_WESTSI1_1 | MCKENZIE | WESTSIDE | 1 |
| 2026 | April | DRNS_TB5 | NB_THW97_A | THW | NB | 1 |
| 2026 | April | SFURVAN8 | RAY_L_46_1 | RAYBURN | L_463S | 1 |
| 2026 | April | DOASSEB5 | WAPWLY72_A | WLY | WAP | 1 |
| 2026 | April | MHARNED5 | WESLCO_HIDLBRG_1 | MV_HBRG4 | MV_WESL4 | 1 |
| 2026 | April | DGRSLO25 | 12020__B | BRTSW | JUNPR | 1 |
| 2026 | April | SSTAPYO8 | 138_HRT_BPT_1 | BRDSPRYT | HARPOONT | 1 |
| 2026 | April | DFERGRM8 | 34T267_1 | SANDMO | CTECBU | 1 |
| 2026 | April | SFBRTHS5 | 35045__A | SAMSW | FVLSW | 1 |
| 2026 | April | XBOM358 | 6175__A | BOMSW | WFSSW | 1 |
| 2026 | April | SVEAW_L5 | 6217__A | WLVSW | GAILS | 1 |
| 2026 | April | DSALKLN5 | 713T713_1 | LAMPAS | NARUNA | 1 |
| 2026 | April | SCOMCRS8 | 875__D | ENPOI | PRPTP | 1 |
| 2026 | April | DFOAVLO5 | FRE_BRUN_1 | BRUNI | FREERS | 1 |
| 2026 | April | SMDOOAS5 | G138_8A_1 | PHR | HDNLAKES | 1 |
| 2026 | April | DROMCEN5 | GARZA_XF1H | GARZA | GARZA | 1 |
| 2026 | April | XJOR158 | JOR_AT2H | JOR | JOR | 1 |
| 2026 | April | SFURVAN8 | LOOP_VICTORIA_1 | L_463S | VICTORIA | 1 |
| 2026 | April | DRIZACE5 | NLARSW_UNITEC1_1 | NLARSW | UNITEC | 1 |
| 2026 | April | SGEOORN8 | ORNGROV_69_1 | ORNGROV | ORNGROV | 1 |
| 2026 | April | MSNDWEY5 | SNDSW_MR1L | SNDSW | SNDSW | 1 |
| 2026 | April | SVLGLO8 | SN_STR26_A | SN | STR | 1 |
| 2026 | April | BASE CASE | UVALDE | n/a | n/a | 1 |
| 2026 | April | SMOOPEA8 | UVALDE_W_BATE1_1 | W_BATESV | UVALDE | 1 |
| 2026 | April | DRICCOR8 | VAN_VNDB_1 | VANBLTSS | VANBLT69 | 1 |
| 2026 | April | SELMTH25 | 1025__B | FROWS | MCLSW | 1 |
| 2026 | April | SWORBRD8 | 138_PYT_STG_1 | STAGHORN | PYOTE | 1 |
| 2026 | April | SWDDMNS5 | 1561__A | DPREA | RCSES | 1 |
| 2026 | April | XPRS58 | 1650__D | TALTP | MNTTP | 1 |
| 2026 | April | DTHSFBR5 | 35045__A | SAMSW | FVLSW | 1 |
| 2026 | April | DNORCDH5 | 3610__E | MRTP2 | PGTP1 | 1 |
| 2026 | April | SNORCDH5 | 3610__G | PGTP1 | PDSES | 1 |
| 2026 | April | SPRCLHS8 | 3650__A | LHSES | SATP1 | 1 |
| 2026 | April | DFVLFTS5 | 506__A | SAMSW | FBRSW | 1 |
| 2026 | April | DRILKRW5 | 6085__E | WFSSW | NSTAR | 1 |
| 2026 | April | DSCOTKW5 | 6240__C | SACRC | DPCRK | 1 |
| 2026 | April | XSCO258 | 6437__F | SCRCV | KNAPP | 1 |
| 2026 | April | MCONPRL5 | 6470__H | FRSTP | GLSCN | 1 |
| 2026 | April | DKLNRGP5 | 651__B | CMNSW | CMNTP | 1 |
| 2026 | April | SHLSWDB8 | 810__G | RDHSW | BLUMS | 1 |
| 2026 | April | SCBEDYN8 | BLESSING_1382 | BLESSING | BLESSING | 1 |
| 2026 | April | XFER85 | CARVER_TINSLE1_1 | CARVER | TINSLEY | 1 |
| 2026 | April | SCARFRI8 | FDR_OZNC_1 | OZNC | FRIEND_R | 1 |
| 2026 | April | SMDOOAS5 | GG_MYK91_A | GG | MYK | 1 |
| 2026 | April | SMDOOAS5 | GN_TC_37_A | TC | GN | 1 |
| 2026 | April | DWESNUE8 | KOCH_H_LON_HI1_1 | LON_HILL | KOCH_HF | 1 |
| 2026 | April | XLO2N58 | LON_HI_SERDEV1_1 | LON_HILL | LON_HILL | 1 |
| 2026 | April | SSANOWL8 | MIDW_OZONA1_1 | OZONA | MIDW | 1 |
| 2026 | April | SMCEESK8 | MKLT_TRNT1_1 | TRNT | MKLT | 1 |
| 2026 | April | DBAKSOL5 | NEVILL_NORTMC_1 | NEVILLSW | NORTMC | 1 |
| 2026 | April | BASE CASE | RAY_L_46_1 | RAYBURN | L_463S | 1 |
| 2026 | April | DRAZSA89 | READIN_UVALDE1_1 | UVALDE | READING | 1 |
| 2026 | April | SORNLON8 | SND_ORAN_1 | ORNGROV | SNDIEGS | 1 |
| 2026 | April | SCOMKEN8 | 115T123_1 | KENDAL | KERRST | 1 |
| 2026 | April | DZORHAY5 | 254T331_1 | CRANMI | SATTLE | 1 |
| 2026 | April | DBUCRGP5 | 281__A | THSES | LHLSW | 1 |
| 2026 | April | DBUCRGP5 | 325__A | BLFSW | TMPCR | 1 |
| 2026 | April | SSGRJEW5 | 325__A | BLFSW | TMPCR | 1 |
| 2026 | April | SLPRTRS8 | 1480__A | LPRSW | GDLTP | 1 |
| 2026 | April | SPRSPAR8 | 1545__A | FLTSW | PRSSW | 1 |
| 2026 | April | DPRSPAC5 | 1561__A | DPREA | RCSES | 1 |
| 2026 | April | DFMRCYC5 | 385__A | TTRSW | MNSES | 1 |
| 2026 | April | STCRTHS5 | 506__A | SAMSW | FBRSW | 1 |
| 2026 | April | MANGGRI5 | BIGTRE_V_DUPS1_1 | V_DUPSW | BIGTRE | 1 |
| 2026 | April | SHONMOO8 | BIG_FOOT_69A1 | BIG_FOOT | BIG_FOOT | 1 |
| 2026 | April | SLAQLOB8 | BRUNI_69_1 | BRUNI | BRUNI | 1 |
| 2026 | April | SN_SAJO5 | BURNS_HEIDLBRG_1 | MV_BURNS | MV_HBRG4 | 1 |
| 2026 | April | DFRIILL8 | CARVER_TINSLE1_1 | CARVER | TINSLEY | 1 |
| 2026 | April | DSTPREF5 | CKT_3124_1 | STP | HLJ | 1 |
| 2026 | April | BASE CASE | CROSSTRL_TL_1 | CROSSTRL | WKN_BKR | 1 |
| 2026 | April | SCOTDI29 | DILLEYSW_XF1H | DILLEYSW | DILLEYSW | 1 |
| 2026 | April | SFURRAY8 | FURHMAN_VANDB_1 | FURHMAN | VANBLTSS | 1 |
| 2026 | April | BASE CASE | LOOP_VICTORIA_1 | L_463S | VICTORIA | 1 |
| 2026 | April | DBAKCED5 | LVOK_SANTIA1_1 | SANTIAGO | LVOK | 1 |
| 2026 | April | DCENFRE5 | NLARSW_UNITEC1_1 | NLARSW | UNITEC | 1 |
| 2026 | April | DBUCRGP5 | TREADW_YELWJC1_1 | TREADWEL | YELWJCKT | 1 |
| 2026 | April | SBE2ASH8 | TURTLECK_WCRYS_1 | TURTLCRK | WCRYSTS | 1 |
| 2026 | April | SBLURDH8 | 1275__A | WDBSW | HLSBR | 1 |
| 2026 | April | DSALHUT5 | 445__A | BLHSW | AUSTRO | 1 |
| 2026 | April | DLONPK25 | 6635__G | MRVLY | ESTLD | 1 |
| 2026 | April | SRICGRS8 | 6840__A | ANARN | CRDSW | 1 |
| 2026 | April | SDANBLE8 | BLESSING_69A1 | BLESSING | BLESSING | 1 |
| 2026 | April | MRAMBN25 | HCKSW_MR2L | HCKSW | HCKSW | 1 |
| 2026 | April | DTVWJON5 | HOOD_DECRDVA_1 | DCDAM | HOD | 1 |
| 2026 | April | BASE CASE | I_PASP | n/a | n/a | 1 |
| 2026 | April | DLCRKIN8 | LCRANE_RIOPEC1_1 | RIOPECOS | LCRANE | 1 |
| 2026 | April | DNORCAS8 | LCRANE_RIOPEC1_1 | RIOPECOS | LCRANE | 1 |
| 2026 | April | SHA2MAX8 | MAXWEL_WHITIN1_1 | MAXWELL | WHITING | 1 |
| 2026 | April | SMOOPEA8 | READIN_UVALDE1_1 | UVALDE | READING | 1 |
| 2026 | April | SFTLMES8 | SANTAR_WOLFCA1_1 | WOLFCAMP | SANTARIT | 1 |
| 2026 | April | MLONOR58 | SND_ORAN_1 | ORNGROV | SNDIEGS | 1 |
| 2026 | April | DBAKSOL5 | SOLSTICE_PST1 | SOLSTICE | SOLSTICE | 1 |
| 2026 | April | SZENTH35 | THWZEN71_A | ZEN | THW | 1 |
| 2026 | April | DVLYANA5 | 1561__A | DPREA | RCSES | 1 |
| 2026 | April | STVWCRT5 | 3180__A | FCRSW | CDHSW | 1 |
| 2026 | April | DSAMFBR5 | 35065__A | FVLSW | FTSSW | 1 |
| 2026 | April | DNORCDH5 | 3610__K | WILMR | MLFRD | 1 |
| 2026 | April | DFRIILL8 | 463T463_1 | BEVO | DIMMIT | 1 |
| 2026 | April | XSNY89 | 6690__E | SNYDR | SSFTP | 1 |
| 2026 | April | SSCLWF28 | 6840__B | NVKSW | ANARN | 1 |
| 2026 | April | DKG_NB_5 | BCVPSA03_A | PSA | BCV | 1 |
| 2026 | April | DRAPFA59 | BIGTRE_V_DUPS1_1 | V_DUPSW | BIGTRE | 1 |
| 2026 | April | DLOFOAV5 | BRUNI_69_1 | BRUNI | BRUNI | 1 |
| 2026 | April | SBE2ASH8 | CARIZOSPG_BEVO_1 | BEVO | CARIZOS | 1 |
| 2026 | April | SWCPYT8 | LANCTYR1_1 | LAN_CTY | LAN_CTY | 1 |
| 2026 | April | STANPAW5 | MAGRUD_VICTOR2_1 | VICTORIA | MAGRUDER | 1 |
| 2026 | April | DHIWARC8 | MORRIS_WESTSI1_1 | MORRIS | WESTSIDE | 1 |
| 2026 | April | BASE CASE | NLARSW_UNITEC1_1 | NLARSW | UNITEC | 1 |
| 2026 | April | SRVRSLK5 | SLKSW_AX1L | SLKSW | SLKSW | 1 |
| 2026 | April | SBE2ASH8 | WCR_CARI_1 | WCRYSTS | CARIZOS | 1 |
| 2026 | April | MRNKDHM5 | W_DENT_T2H | W_DENT | W_DENT | 1 |
| 2026 | April | DPHRAL58 | 138_ALV_NAL_1 | TNNALVIN | ALVIN | 1 |
| 2026 | April | SGILTRI8 | 211T147_1 | GILLCR | MCNEIL_ | 1 |
| 2026 | April | DCPSES12 | 35045__A | SAMSW | FVLSW | 1 |
| 2026 | April | DKLNRGP5 | 505__B | FBRSW | THSES | 1 |
| 2026 | April | SSUNSNY8 | 6474__B | SUNSW | RGRSW | 1 |
| 2026 | April | DLNCSWE5 | 6635__G | MRVLY | ESTLD | 1 |
| 2026 | April | SGRSJUN8 | 6635__G | MRVLY | ESTLD | 1 |
| 2026 | April | SGRMGRS8 | 6830__C | OLNEY | GRAHM | 1 |
| 2026 | April | XFTS89 | ALPINE_BRONCO1_1 | BRONCO | ALPINE | 1 |
| 2026 | April | SSCJFS8 | BCVPSA03_A | PSA | BCV | 1 |
| 2026 | April | SRICEL_8 | CLMVLT_EL_CAM1_1 | EL_CAMPO | CLMVLTAP | 1 |

Current Wind Generation Record: 28,751 MW on 03/14/2026 at 23:00 | Current Wind Penetration Record: 69.15% on 04/10/2022 at 01:43

Current Solar Generation Record: 33,477 MW on 03/21/2026 at 11:20 | Current Solar Penetration Record: 67.27% on 03/21/2026 at 10:52