| PGRR Number | 145 | PGRR Title | Batch Zero Process for Large Load Interconnections |
| --- | --- | --- | --- |
| Date of Decision |  | June 2, 2026 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Urgent |  |
| Estimated Impacts |  | Batch Zero and Withdrawal-Limited Private Use Network (WLPUN): Cost/Budgetary: $3.6M-$4.5M Annual Recurring Operations and Maintenance (O&M) Project Duration: No project required Provisional Controllable Load Resource (PCLR): Cost/Budgetary: Between $300K and $400K Project Duration: 8 to 12 months |  |
| Proposed Effective Date |  | Batch Zero and WLPUN: July 11, 2026 PCLR: Upon system implementation |  |
| Priority and Rank Assigned |  | Batch Zero and WLPUN: Not applicable PCLR: Priority – 2027; Rank – 450 |  |
| Planning Guide Sections Requiring Revision |  | 3.1.2, Regional Planning Group Project Submission 3.1.2.1, All Projects 3.1.3, Project Evaluation 5.3.5 ERCOT Quarterly Stability Assessment 6.6.1 Modeling of Large Loads Not Co-Located with a Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG) 6.6.2 Modeling of Large Loads Co-Located with an Existing Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG) 6.6.2.1, Modeling of Large Loads within a Withdrawal-Limited Private Use Network (new) 6.6.3 Modeling of Large Loads Co-Located with a Proposed Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG) 9, Large Load Additions at New or Modification of Existing Load Interconnection(s) 9.1, Introduction 9.2.1, Applicability of the Large Load Interconnection Study Process 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in Batch Zero (new) 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero (new) 9.2.1.3, Load not Included in Batch Zero (new) 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads (new) 9.2.2, Submission of Large Load Project Information and Initiation of the Large Load Interconnection Study (LLIS) 9.2.2.1, Additional Information Required for Provisional Controllable Load Resources (PCLRs) (new) 9.2.2.2, Additional Information Required for Withdrawal-Limited Private Use Networks (WLPUNs) (new) 9.2.3, Modification of Large Load Project Information 9.2.4, Load Commissioning Plan 9.2.5, Required Interconnection Equipment 9.3, Interconnection Study Procedures for Large Loads 9.3.1, Large Load Interconnection Study (LLIS) 9.3.2, Large Load Interconnection Study Scoping Process 9.3.2.1, Treatment of Provisional Controllable Load Resources (PCLRs) in the Batch Zero Interconnection Study (new) 9.3.2.2, Treatment of Withdrawal-Limited Private Use Networks (WLPUNs) in the Batch Zero Interconnection Study (new) 9.3.3, Large Load Interconnection Study Description and Methodology (delete) 9.3.4, Large Load Interconnection Study Elements (delete) 9.3.4.1, Steady-State Analysis (delete) 9.3.4.2, System Protection (Short-Circuit) Analysis (delete) 9.3.4.3, Dynamic and Transient Stability Analysis (delete) 9.4, LLIS Report and Follow-up 9.4.1, Additional Commitments for Provisional Controllable Load Resources (PCLRs) (new) 9.4.2, Additional Commitments for Withdrawal-Limited Private Use Networks (WLPUNs) (new) 9.5, Interconnection Agreements and Responsibilities 9.5.1, Interconnection Agreement for Large Loads not Co-Located with a Generation Resource Facility (delete) 9.5.2, Interconnection Agreement for Large Loads Co-Located with One or More Generation Resource Facilities (delete) 9.5.3, Treatment of Provisional Controllable Load Resources (PCLRs) in the Batch Zero Refinement Study (new) 9.5.4, Treatment of Withdrawal-Limited Private Use Networks (WLPUNs) in the Batch Zero Refinement Study (new) 9.6, Initial Energization and Continuing Operations for Large Loads 9.6.1, Additional Energization and Operation Requirements for Provisional Controllable Load Resources (PCLRs) (new) 9.6.2, Additional Energization and Operation Requirements for Withdrawal-Limited Private Use Networks (WLPUNs) (new) 9.7, Required Disclosures (new) 9.8, Legacy Interconnection Study Procedures for Large Loads (new) 9.8.1, Legacy Large Load Interconnection Study (LLIS) (new) 9.8.2, Legacy Large Load Interconnection Study Scoping Process (new) 9.8.3, Legacy Large Load Interconnection Study Description and Methodology (new) 9.8.4, Legacy Large Load Interconnection Study Elements (new) 9.8.4.1, Legacy Steady-State Analysis (new) 9.8.4.2, Legacy System Protection (Short-Circuit) Analysis (new) 9.8.4.3, Legacy Dynamic and Transient Stability Analysis (new) 9.9, Legacy LLIS Report and Follow-up (new) 9.10, Legacy Interconnection Agreements and Responsibilities (new) 9.10.1, Legacy Interconnection Agreement for Large Loads not Co-Located with a Generation Resource Facility (new) 9.10.2, Legacy Interconnection Agreement for Large Loads Co-Located with One or More Generation Resource Facilities (new) |  |
| Related Documents Requiring Revision/Related Revision Requests |  | Nodal Protocol Revision Request (NPRR) 1325, Related to PGRR145, Batch Zero Process for Large Load Interconnections |  |
| Revision Description |  | This Planning Guide Revision Request (PGRR) creates a transitional Batch Zero for ERCOT to study on a system-wide basis the reliability impacts of Large Loads that meet certain study maturity and commitment criteria. |  |
| Reason for Revision |  | Strategic Plan Objective 1 – Be an industry leader for grid reliability and resilience Strategic Plan Objective 2 - Enhance the ERCOT region’s economic competitiveness with respect to trends in wholesale power rates and retail electricity prices to consumers Strategic Plan Objective 3 - Advance ERCOT, Inc. as an independent leading industry expert and an employer of choice by fostering innovation, investing in our people, and emphasizing the importance of our mission General system and/or process improvement(s) Regulatory requirements ERCOT Board/PUCT Directive (please select ONLY ONE – if more than one apply, please select the ONE that is most relevant) |  |
| Justification of Reason for Revision and Market Impacts |  | This PGRR establishes a transitional Batch Zero for ERCOT to evaluate, on a system-wide basis, the reliability impacts of Large Load interconnection requests that meet certain study maturity and commitment criteria. Batch Zero is necessary as ERCOT intends to transition the Large Load interconnection process from an individual study-based approach to a batch study-based approach that allocates available transmission capacity for studied and committed Large Loads and, to the extent feasible, results in an actionable transmission plan. Under the current Large Load Interconnection Study (LLIS) process, Transmission Service Providers (TSPs) conduct individual interconnection studies for each Large Load before submitting them to ERCOT for review and approval. Although the LLIS process represents an improvement over historical interconnection processes, it has proved inadequate in managing an unprecedented volume of Large Load interconnection requests. This rapid increase has introduced structural challenges, such as the need for coordination across TSPs, repeated restudies, and a growing backlog of requests. These issues have led to prolonged interconnection timelines and heightened uncertainty for Interconnecting Large Load Entities (ILLEs), TSPs, and ERCOT. To address these structural challenges, ERCOT is developing a new Large Load interconnection process referred to as a “Batch Study” process. Under the Batch Study process, ERCOT will study Large Loads that meet qualifying requirements on a system-wide basis. The process will allow ERCOT to allocate available transmission capacity and plan future transmission capacity for each Large Load evaluated in a Batch Study while maintaining a focus on reliability. ERCOT intends to submit a separate PGRR in the future to implement an ongoing Batch Study process. In the near-term, ERCOT will conduct a one-time transitional Batch Zero Process that will categorize based on study maturity and commitment criteria Large Loads seeking interconnection to the ERCOT system. These Large Loads will be either (1) base load, (2) studied load, or (3) load to be studied in a future batch. Batch Zero will have two study phases, a Batch Zero Interconnection Study and a Batch Zero Refinement Study. During the Batch Zero Interconnection Study, ERCOT will conduct a system-wide steady-state study and a stability screening study. ERCOT will provide the results of the Batch Study to Interconnecting DSPs and Interconnecting TSPs, who will communicate to ILLEs their megawatt (MW) allocations for Years 1 through 6. ILLEs will then have 30 days to execute an interconnection agreement that meets requirements based on the PUCT’s criteria in Project No. 58481, Rulemaking to Implement Large Load Interconnection Standards Under PURA § 37.0561. ERCOT will then conduct a Batch Zero Refinement Study that results in a final list of recommended Transmission Facility improvements, a description of the need for those Transmission Facility improvements, cost estimates for those Transmission Facility improvements, and any alternate improvements formally considered by ERCOT. ERCOT shall submit the final report for Regional Planning Group (RPG) Project Review by June 1, 2027. This final report shall serve as ERCOT’s independent review in accordance with Protocol Section 3.11.4.6, Processing of Tier 2 Projects, or Protocol Section 3.11.4.7, Processing of Tier 1 Projects, unless ERCOT decides to create an updated final report based on comments received during the RPG Project Review. To ensure future alignment with 16 TAC § 25.370, ERCOT Large Load Forecasting Criteria, ERCOT has incorporated within this PGRR the interconnection standards set forth in the PUCT Staff’s February 13, 2026 recommended proposal for publication. ERCOT recognizes that this PGRR could require some additional revisions to 16 TAC §25.370(g) to align with the proposal herein and is engaged with PUC Staff to ensure that the appropriate policy determinations in this revision effort are appropriately reflected in both ERCOT's requirements and the PUCT's rules. ERCOT intends to update the interconnection standards included in the PGRR after the PUCT publishes the proposal for publication. ERCOT’s inclusion of the draft interconnection standards in this PGRR should not be construed as express support for any specific provision. Should ERCOT have any comments, they will be submitted under Project No. 58481. |  |
| ROS Decision |  | On 4/2/26, ROS voted unanimously to table PGRR145. All Market Segments participated in the vote. On 5/7/26, ROS voted to grant PGRR145 Urgent status; to recommend approval of PGRR145 as amended by the 5/2/26 ERCOT comments; and to forward to TAC PGRR145 and the 3/4/26 Impact Analysis. There were two abstentions from the Independent Power Marketer (IPM) (Tenaska) and Municipal (CPS Energy) Market Segments. All Market Segments participated in the vote. |  |
| Summary of ROS Discussion |  | On 4/2/26, ERCOT Staff provided an overview of PGRR145, the proposed approval timeline, the numerous workshops related to PGRR145, and the potential for additional redlines related to Controllable Load Resource (CLR) and ‘bring your own generation’ (“BYOG”) options. Participants posed questions regarding the overall timeline and potential risks of “year 6” allocations for load exceeding what can reasonably connect. On 5/7/26, ERCOT Staff presented on the series of Batch Study Process workshops and the evolution of PGRR145 and NPRR1325 through multiple rounds of ERCOT comments; as well as budgetary impacts associated with the various PGRR145 and NPRR1325 options. Participants discussed recent activity under PUCT Project No. 59142, Review of ERCOT’s Interconnection Processes for Large Loads, regarding financial security, and ERCOT noted plans for additional formal comments to address PUCT guidance within Section 9.2.1.1. Participants requested additional review from ERCOT of how existing RPG projects could be leveraged in the LLIS process. |  |
| TAC Decision |  | On 5/13/26, TAC voted unanimously to table PGRR145. All Market Segments participated in the vote. On 5/19/26, TAC voted to recommend approval of PGRR145 as recommended by ROS in the 5/7/26 ROS Report as amended by the 5/18/26 ERCOT comments and the 5/18/26 Revised Impact Analysis with a recommended effective date of the day following PUCT approval for Batch Zero and WLPUN and upon system implementation for PCLR with a recommended priority of 2027 and rank of 450. There was one abstention from the Cooperative (GSEC) Market Segment. All Market Segments participated in the vote. |  |
| Summary of TAC Discussion |  | On 5/13/26, participants reviewed the items below and discussed remaining issues related to eligibility and financial security. ERCOT requested PGRR145 be tabled to allow time for additional formal comments to provide further clarifications and administrative cleanups to PGRR145. On 5/19/26, participants reviewed the items below and discussed the appropriate eligibility criteria, study details, and deadlines for inclusion within Batch Zero. |  |
| TAC Review/Justification of Recommendation |  | Revision Request ties to Reason for Revision as explained in Justification Impact Analysis reviewed and impacts are justified as explained in Justification Opinions were reviewed and discussed Comments were reviewed and discussed (if applicable) Other: (explain) |  |
| ERCOT Board Decision |  | On 6/2/26, the ERCOT Board voted unanimously to recommend approval of PGRR145 as recommended by TAC in the 5/19/26 TAC Report with a recommended effective date of July 11, 2026 for Batch Zero and WLPUN and upon system implementation for PCLR. |  |

| Opinions |  |
| --- | --- |
| Credit Review | Not applicable |
| Independent Market Monitor Opinion | IMM has no opinion on PGRR145. |
| ERCOT Opinion | ERCOT supports approval of PGRR145. |
| ERCOT Market Impact Statement | ERCOT Staff has reviewed PGRR145 and believes the market impact for PGRR145, along with NPRR1325, effectively and reliably facilitates the transition of the Large Load interconnection process from an individual study-based approach to a Batch Study-based approach that allocates available transmission capacity for studied and committed Large Loads and, to the extent feasible, results in an actionable transmission plan. |

| Sponsor |  |
| --- | --- |
| Name | Agee Springer |
| E-mail Address | agee.springer@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4508 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Cory Phillips |
| E-Mail Address | cory.phillips@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Schaper Energy Consulting 030526 | Raised concerns with the proposed Section 9.2.1.4 and proposed revisions allowing Batch Zero inclusion for any projects meeting the current requirements of Sections 9.4 and 9.5 by July 15, 2026 |
| Reliant Energy 030926 | Proposed additional redlines to allow a Large Load co-located with a new Generation Resource that was included in a Full Interconnection Study (FIS) to be eligible for inclusion in Batch Zero as base Load not subject to additional study |
| Crusoe 030926 | Proposed additional redlines to address concerns with the proposed dates, prioritization methodology, and perceived conflicts with financial security and interconnection agreement requirements between PGRR145 and PUCT Project No. 58481 |
| Rose City Partners 031026 | Expressed support for the 3/5/26 Schaper Energy Consulting comments |
| Schaper Energy Consulting 031126 | Raised concerns with the proposed Section 9.2.1.4 and proposed revisions allowing Batch Zero inclusion for any projects meeting the current requirements of Sections 9.4 and 9.5 by July 15, 2026 |
| ERCOT 031726 | Proposed additional redlines based on formal comments and stakeholder discussions |
| Lancium 031926 | Proposed additional redlines to the 3/17/26 ERCOT comments modifying the consideration deadline from December 15, 2025 to March 4, 2026 and resolve a perceived inconsistency between the Batch Study process and information already submitted as part of the Regional Transmission Plan (RTP) process |
| Skybox Datacenters 031926 | Proposed additional edits to the 3/17/26 ERCOT comments to clarify language and address perceived duplicative requirements |
| Schaper Energy Consulting 031926 | Proposed additional edits to the 3/17/26 ERCOT comments to address a perceived "air gap" between March 4, 2026, and July 10, 2026 as well as compliance burden on customers energizing before December 31, 2027, under proposed Project No. 58481 interconnection standards |
| IREN 031926 | Proposed additional redlines to the 3/17/26 ERCOT comments including new sections to address available capacity allocation between projects within Batch Zero |
| Oncor 032026 | Proposed additional redlines to the 3/17/26 ERCOT comments to improve and clarify requirements |
| Crusoe 032026 | Proposed additional redlines to the 3/17/26 ERCOT comments to modify the proposed cutoff date within paragraph (3) of Section 9.2.1.4 from March 4, 2026 to June 1, 2026 |
| Joint Commenters 032026 | Proposed additional redlines to the 3/17/26 ERCOT comments to modify the proposed cutoff date within paragraph (3) of Section 9.2.1.4 from March 4, 2026 to June 3, 2026 |
| CenterPoint Energy 032026 | Proposed additional redlines to the 3/17/26 ERCOT comments to (i) emphasize the continued, highly coordinated collaboration needed between ERCOT and Transmission and/or Distribution Service Providers (TDSPs) for Batch Zero success, (ii) clarify roles and responsibilities for engineering studies and data exchange between ERCOT, ILLE and TDSP(s), and (iii) opine that a utility’s accounting and treatment of financial security and potential refund does not belong in the Planning Guide and should be addressed by the PUCT |
| Joint Commenters II 032026 | Proposed additional redlines to the 3/17/26 ERCOT comments including new paragraphs within Section 9.2.1.2 to include within Batch Zero projects which have (i) received an ERCOT Large Load interconnection number and have satisfied the criteria to be included in the ERCOT 2026 RTP, or (ii) received a Large Load interconnection number and indicated in its intermediate agreement that it can be studied as a CLR or with a planned co-located Generation Resource |
| Vistra 032026 | Proposed additional redlines to the 3/17/26 ERCOT comments to address compatibility with Senate Bill 6 (SB6) and PUCT Project No. 58481 along with miscellaneous issues, clean-ups, and clarifications |
| Eolic 032026 | Proposed additional redlines to the 3/19/26 Lancium comments to incorporate PUCT Project No. 58480, Rulemaking to Establish Large Load Forecasting Criteria, language into Section 9.2.1.4 |
| TEBA (a-b) 032026 | Raised topics for continued discussion relating to the Batch Study and opined that ERCOT needs to expeditiously approve the existing RPG studies so as not to stall the needed transmission expansion and move forward with Batch Zero |
| Satoshi Energy 032026 | Proposed additional redlines to the 3/17/26 ERCOT comments to modify the proposed cutoff date within paragraph (3) of Section 9.2.1.4 from March 4, 2026 to July 10, 2026 along with references back to PUCT Project No. 58481 |
| Black Mountain 032026 | Proposed additional redlines to the 3/17/26 ERCOT comments to add paragraphs into Section 9.2.1.4 to include projects with substantial technical progress and near-term execution readiness in Batch Zero |
| 3-Waters Technical Services 032026 | Raised concerns with the historical weather baselines used in the study process not adequately accounting for increasing climatic variability |
| Sandow 032026 | Proposed additional redlines to the 3/17/26 ERCOT comments to propose several options for expedited interconnection treatment for projects with co-located generation |
| Emerald AI 032026 | Recommended that CLR rules be included in Batch Zero policies |
| AEP 032026 | Proposed additional redlines to the 3/17/26 ERCOT comments to modify proposed dates and clarify the necessary interaction between ERCOT and TDSPs within the batch process |
| Monarch Energy 032026 | Proposed additional redlines to the 3/17/26 ERCOT comments to explicitly recognize executed binding financial commitments through TDSP-accepted mechanisms (including financial security for long-lead equipment and services of CIAC) as comparable to executed Interconnection Agreement |
| Crow Holdings 032026 | Proposed additional redlines to the 3/17/26 ERCOT comments to delete paragraph (1)(d) of Section 9.2.1.1 and provide an alternative paragraph listing criterion for inclusion in Batch Zero |
| ZEG 032026 | Proposed additional redlines to the 3/17/26 ERCOT comments to make the power flow auxiliary files including contingency files associated with the Batch Zero Interconnection Study cases available in the Market Information System (MIS) Secure area |
| Engie 032626 | Proposed additional redlines to the 3/17/26 ERCOT comments to modify the proposed cutoff date within paragraph (3) of Section 9.2.1.4 from March 4, 2026 to July 10, 2026 |
| Tract 032726 | Proposed additional redlines to the 3/17/26 ERCOT comments to allow projects with completed studies by July 2026 to qualify for Batch Zero, to require a refund of Batch Zero fees under certain conditions, to remove non-refundable fee and security language, and to clarify that the refinement study process cannot increase ILLE costs |
| Crusoe 032726 | Proposed additional redlines to the 3/20/26 Crusoe comments relating to financial commitment and Subsynchronous Oscillation (SSO) and quarterly stability assessment sequencing |
| Schaper Energy Consulting 032726 | Restated concerns raised in the 3/19/26 Schaper Energy Consulting comments and proposed additional redlines to the 3/17/26 ERCOT comments to replace interconnection standards within Section 9.2.1.1 to match legacy requirements for those loads not subject to additional restudy |
| Schaper Energy Consulting 040226 | Raised concerns with assertions that the existing Section 9.5 language is insufficient and warned against retroactive disruption to previously completed studies and agreements |
| Eolic 040326 | Proposed additional redlines to the 3/17/26 ERCOT comments to better leverage prior TSP work and legacy standards |
| ERCOT 040426 | Proposed additional redlines to the 3/17/26 ERCOT comments in response to stakeholder feedback, along with minor corrections |
| Cipher Digital 040826 | Proposed additional redlines to the 3/26/26 Engie comments to clarify the mechanism for refunding financial security within Batch Zero |
| Engine No1 040826 | Proposed additional redlines to the 4/4/26 ERCOT comments presenting options for bring your own generation ("BYOG") within Batch Zero |
| LCRA 040826 | Proposed additional redlines to the 4/4/26 ERCOT comments addressing eligibility, study processes, and timeline updates for Large Load interconnections |
| Oncor 040826 | Recommended that Large Loads addressed by RPG projects be recognized as base load not subject to additional study in the Batch Zero Process if the RPG projects were submitted prior to December 15, 2025 and received RPG acceptance or ERCOT endorsement on or before July 15, 2026 |
| CenterPoint Energy 040826 | Proposed additional redlines to the 4/4/26 ERCOT comments to clarify and reiterate key concepts |
| Vistra 040926 | Responded to the 4/4/26 ERCOT comments, proposed additional redlines, and provided preliminary comments regarding the PUCT's Proposal for Publication (PFP) in Project No. 58481 |
| ERCOT 041726 | Proposed additional redlines to the 4/4/26 ERCOT comments introducing the Provisional Controllable Load Resource (PCLR) concept |
| CyrusOne 041726 | Proposed additional redlines to the 4/4/26 ERCOT to better align Batch Zero with SB6 and ensure fair treatment of net-metered Large Loads |
| Reliant 041726 | Proposed additional redlines to the 4/17/26 ERCOT comments to narrowly clarify the deadline for ERCOT to receive a notarized attestation of an executed intermediate agreement from the Interconnecting Distribution Service Provider (DSP) and for a Large Load to receive ERCOT approval of a steady state or stability study |
| TCPA 042126 | Endorsed the 4/9/26 Vistra comments |
| Joint Commenters 042126 | Proposed additional redlines to the 4/17/26 ERCOT comments providing additional eligibility details within Section 9.2.1.2 |
| CenterPoint Energy 042226 | Proposed additional redlines to the 4/8/26 CenterPoint Energy comments to provide a clear path for projects < 75 MW to energize outside of the Batch Zero process |
| Skybox Datacenters 042226 | Responded to the 4/17/26 ERCOT comments and recommended that base load eligibility be defined using objective, study-based criteria, rather than a fixed endorsement-date cutoff |
| Wise Energy Resources 042226 | Endorsed the 4/21/26 Joint Commenters comments |
| ERCOT 042326 | Proposed additional redlines to the 4/17/26 ERCOT comments in response to stakeholder feedback, along with minor corrections |
| Luminary Strategies 042326 | Proposed additional redlines to the 4/23/26 ERCOT comments to reinsert the Section 9.2.1.2 language proposed within the 4/21/26 Joint Commenters comments |
| Schaper Energy Consulting 042426 | Requested ERCOT seek additional clarification from the PUCT regarding standards load customers should reference regarding financial security |
| Oncor 042726 | Proposed additional redlines to the 4/23/26 ERCOT comments allowing date the RPG project should have had its EIR completed to be utilized in the study validity assessment process, in which RPG projects are assessed against other RPG projects and against load requests that met Sections 9.9 and 9.10 by July 10, 2026 |
| LCRA 042726 | Proposed additional redlines to the 4/23/26 ERCOT comments to clarify language within 9.2.1.1 and Section 9.2.1.4 |
| PUCT Staff 042926 | Expressed support for the 4/23/26 ERCOT comments and provided responses to stakeholder requests for additional clarity around financial commitment requirements proposed in Project No. 58481 |
| Vesper Energy Development 042926 | Endorsed the 4/21/26 Joint Commenters comments |
| Skybox Datacenters 043026 | Endorsed the 4/27/26 Oncor comments |
| TEBA 043026 | Proposed additional redlines to the 4/23/26 ERCOT comments to incorporate and consolidate other stakeholder comments |
| Rowan 043026 | Proposed additional redlines to the 4/23/26 ERCOT comments including adjustments to site control and project timing rules |
| ERCOT 043026 | Proposed additional redlines to the 4/23/26 ERCOT comments in response to stakeholder feedback, along with minor corrections |
| Monarch Energy 043026 | Proposed additional redlines to the 4/30/26 ERCOT comments clarifying eligibility requirements within Section 9.2.1.1 |
| Data Center Coalition 050126 | Proposed additional redlines to the 4/30/26 ERCOT comments clarifying eligibility requirements within Section 9.2.1.4 and Section 9.7.1 |
| Eolic 050126 | Proposed additional redlines to the 4/30/26 ERCOT comments clarifying treatment of Transmission Project Information Tracking (TPIT) reports |
| Schaper Energy Consulting 050226 | Responded to the 4/30/26 ERCOT comments and provided discussion topics for further refinements |
| ERCOT Comments 050226 | Proposed additional redlines to the 4/30/26 ERCOT comments introducing the Withdrawal-Limited Private Use Network (WLPUN) concept |
| United Cooperative Services 050426 | Proposed additional redlines to the 5/2/26 ERCOT comments providing additional eligibility details within Section 9.2.1.2 |
| Sailfish Investors 050426 | Proposed additional redlines to the 5/4/26 United Cooperative Services comments adding Discretionary Service Agreement to the list of eligible agreements |
| Eolic 050426 | Proposed additional redlines to the 5/2/26 ERCOT comments clarifying language within Section 9.3.1 and Section 9.3.2 |
| Eolic II 050426 | Endorsed the 5/4/26 United Cooperative Services comments and the 5/4/26 Sailfish Investors comments |
| AEPSC 050526 | Proposed additional redlines to the 5/2/26 ERCOT comments clarifying language within Section 9.2.1.1 and Section 9.3.2 |
| Cholla 050526 | Proposed additional redlines to the 5/2/26 ERCOT comments to modify the proposed cutoff date within paragraph (3) of Section 9.2.1.4 from March 4, 2026 to July 10, 2026 |
| LCRA 050626 | Proposed additional redlines to the 5/2/26 ERCOT comments addressing eligibility, study processes, and timeline updates for Large Load interconnections |
| TEBA 050626 | Proposed additional redlines to the 4/30/26 TEBA comments incorporating comments from other stakeholders and suggesting an alternative to the WLPUN concept |
| Vistra 050626 | Proposed additional redlines to the 5/2/26 ERCOT comments suggesting clarifications and improvements throughout |
| Tract 050626 | Posted the Tract comments posted to PUCT Project 59142 to facilitate stakeholder discussion |
| Mesquite 050626 | Proposed additional redlines to the 4/30/26 ERCOT comments to include a signed and executed purchase and sales agreement as an allowable method of demonstrating site control |
| AEPSC 050626 | Proposed additional redlines to the 5/5/26 AEPSC comments to elaborate further on a narrow approach regarding RPG studies for Batch Zero |
| Sierra Club 051126 | Raised discussion topics for TAC, the ERCOT Board, and PUCT consideration |
| Eolic 051126 | Proposed additional redlines to the 5/2/26 ERCOT comments related to Transmission Project Information Tracking (TPIT) utilization, minimum load allocation, leveraging RPG studies, and suggested revisions from the United Cooperative Services 5/4/26 comments |
| ERCOT 051126 | Proposed additional redlines to the 5/2/26 ERCOT comments in response to stakeholder feedback and PUCT guidance, along with minor corrections |
| Schaper Energy Consulting 051226 | Proposed additional redlines to the 5/11/26 ERCOT comments modifying site approval language within Section 9.2.1.1 |
| Vesper Energy Development 051226 | Proposed additional redlines to the 5/11/26 ERCOT comments modifying eligibility language within Section 9.2.1.2 |
| Vistra 051226 | Proposed additional redlines to the 5/11/26 carrying over proposals from the 5/6/26 Vistra comments |
| Intersect USA 051226 | Presented a summary of potential revisions for stakeholder consideration |
| Eolic 051226 | Proposed additional redlines to the 5/11/26 ERCOT comments related to TPIT utilization, zoning/site permits, contribution in aid of construction (“CIAC”), and financial security |
| Monarch Energy 051426 | Proposed additional redlines to the 5/11/26 ERCOT comments clarifying eligibility requirements within Section 9.2.1.1 |
| Data Center Coalition 051426 | Raised discussion topics related to the treatment of SB 6 net-metered projects within Batch Zero |
| ERCOT 051526 | Proposed additional redlines to the 5/11/26 ERCOT comments in response to stakeholder feedback, along with minor corrections |
| Reliant 051626 | Proposed additional redlines to the 5/15/26 ERCOT comments to extend the study submission deadline and broaden the inclusion criteria only for Large Loads associated with a WLPUN or a PCLR. |
| Cholla 051726 | Proposed additional redlines to the 5/16/26 Reliant comments to modify the proposed cutoff date within paragraph (3) of Section 9.2.1.4 from March 4, 2026 to March 17, 2026 |
| Vistra 051726 | Proposed additional redlines to the 5/15/26 ERCOT comments carrying over proposals from the 5/6/26 Vistra comments |
| TEBA 051726 | Proposed additional redlines to the 5/15/26 ERCOT comments incorporating some of the suggested revisions from the 5/6/26 AEPSC comments |
| Agentic 051826 | Proposed additional redlines to the 5/17/26 Cholla comments to expand PCLR and WLPUN study flexibility and better utilize co-located generation in Batch Zero |
| BKV 051826 | Endorsed the 5/17/26 Vistra comments |
| Wise Energy Resources 051826 | Endorsed the 5/16/26 Reliant comments |
| Eolic 051826 | Proposed additional redlines to the 5/16/26 Reliant comments related to TPIT utilization and to incorporate and consolidate other stakeholder comments |
| Sailfish Investors 051826 | Expressed support for the 5/16/26 Reliant comments but recommends that any WLPUN/PCLR-specific language be implemented in a manner that does not appear to narrow, condition or otherwise limit the separate eligibility pathway |
| Monarch Energy 051826 | Proposed additional redlines to the 5/15/26 ERCOT comments clarifying eligibility requirements within Section 9.2.1.1 |
| Luminary Strategies 051826 | Endorsed the 5/16/26 Reliant comments, the 5/16/26 Cholla comments, the 5/17/26 Vistra comments, and the 5/18/26 Agentic comments |
| ERCOT 051826 | Proposed additional redlines to the 5/15/26 ERCOT comments revising Section 9.2.1.4 to clarify the Large Loads that must be considered when ERCOT determines whether a Large Load has complete and valid studies |
| Satoshi Energy 051926 | Proposed additional redlines to the 5/2/26 ERCOT comments to align eligibility requirements with on-the-ground development timelines |
| Cypress Creek Energy 051926 | Proposed additional redlines to the 5/15/26 ERCOT comments revising the WLPUN qualification criteria to clarify that multiple high-voltage connections to the same TSP substation or common switchyard do not disqualify a large load from WLPUN status, provided the common switchyard qualification is met and the Point of Interconnections (POIs) are within 400 yards of each other |
| Cholla 052226 | Proposed additional redlines to modify the proposed cutoff date within paragraph (3) of Section 9.2.1.4 from March 4, 2026 to March 17, 2026 |
| Cholla 052626 | Detailed the procedural history of Project Venus, provided further justification for the requested revisions in the 5/22/26 Cholla comments, and requested the Board direct ERCOT to issue a report on RTP-derived Oncor project sets related to Batch Zero treatment |

Market Rules Notes

Please note the baseline Planning Guide language in the following section(s) has been updated to reflect the incorporation of the following PGRR(s) into the Planning Guide:

- PGRR127, Addition of Proposed Generation to the Planning Models (incorporated 4/1/26)

  - Section 3.1.3

- PGRR139, Related to NPRR1314, Planning Guide Glossary Transition (incorporated 6/1/26)

  - Section 2.1

  - Section 2.2

Please note that the following PGRR(s) also propose revisions to the following Section(s):

- PGRR139, Related to NPRR1314, Planning Guide Glossary Transition

  - Section 2.1

  - Section 2.2

- PGRR140, Related to NPRR1317, Creation of Non-Settled Generator (NSG) and Clarification of the Types, Usage, and Registration of Distributed Generation

  - Section 5.3.5

- PGRR141, Large Load Interconnection Study Reform for Substantiated Load

  - Section 9.3.1

- PGRR144, Dynamic Model Submission and Review Requirements for Large Loads including Large Electronic Loads

  - Section 9.2.1

  - Section 9.3.4.3

  - Section 9.6

- PGRR146, Rename Quarterly Stability Assessment and Modify the Assessment Schedule

  - Section 5.3.5

Proposed Guide Language Revision

### 3.1.2	Regional Planning Group Project Submission

(1)	Transmission projects that are proposed for RPG Review, pursuant to Protocol Section 3.11.4.1, Project Submission, shall be submitted according to the provisions outlined in Section 3.1.2.1, All Projects.

#### 3.1.2.1	All Projects

(1)	The submittal of each transmission project (60 kV and above) for RPG Project Review, except for the Transmission Facility improvements submitted based on Section 9.5, Batch Zero Study Refinement and Delivery of Transmission Plan, should include the following elements:

(a)	The proposed project description including expected cost, feasible alternative(s) considered, transmission topology and Transmission Facility modeling parameter data, and all study cases used to generate results supporting the need for the project in electronic format (powerflow data should be in PTI Power System Simulator for Engineering (PSS/E) RAWD format).  Also, the submission should include accurate maps and one-line diagrams showing locations of the proposed project and feasible alternatives;

(b)	Identification of the SSWG, Dynamics Working Group (DWG), or Regional Transmission Plan powerflow cases used as a basis for the study and any associated changes that describe and allow accurate modeling of the proposed project;

(c)	Description and data for all changes made to the SSWG base cases or Regional Transmission Plan cases used to identify the need for the project, such as Resource unavailability and area peak load forecast;

(d)	A description of the reliability and/or economic problem that is being solved;

(e)	Information that supports any load values that differ from the load forecast used in the base cases identified in item (b) above, including any relevant historical load information or evidence demonstrating that a submitted load value is Substantiated Load;

(f)	A description of the Subsynchronous Resonance (SSR) impact of the proposed project to the generation Facilities in the system pursuant to Protocol Section 3.22.1, Subsynchronous Resonance Vulnerability Assessment, and potential SSR Countermeasure plan for any identified SSR vulnerability, if applicable;

(g)	Desired/needed in-service date for the project, and feasible in-service date, if different;

(h)	The phone number and email address of the single point of contact who can respond to ERCOT and RPG participant questions or requests for additional information necessary for stakeholder review; and

(i)	Analysis of rejected alternatives, including cost estimates, and other factors considered in the comparison of alternatives with the proposed project.

(2)	Both transmission and distribution solutions to performance deficiencies may be considered where applicable.

(3)	If there is any other information, not included above, that the submitting party believes is relevant to consideration of the need for any submitted project, the submitting party should include that information in the project submission.

### 3.1.3	Project Evaluation

(1)	ERCOT and the RPG shall evaluate proposed transmission projects using a variety of tools and techniques as needed to ensure that the system is able to meet applicable reliability criteria in a cost-effective manner.  For most proposed projects, except for the Transmission Facility improvements submitted based on Section 9.5, Batch Zero Study Refinement and Delivery of Transmission Plan, several alternatives will be identified to meet the reliability criteria or other performance improvement objectives that the proposed project is designed to meet.  The project alternative with the expected lowest cost over the life of the project is generally recommended, subject to consideration of the expected long-term system needs in the area, including, as applicable, any evidence of Substantiated Load, and subject to consideration of the relative operational impacts of the alternatives.

(2)	In some cases, one alternative may be to dispatch the system in such a way that all reliability requirements are met, even without the proposed transmission project or any transmission alternative, resulting in a less efficient dispatch than what would be required to meet the reliability requirements if the proposed project was in place.  Consideration of the merits of this alternative relative to the proposed transmission project is more complex.  To facilitate the discussion and consideration of these alternatives, ERCOT has adopted certain definitions and practices, described in paragraph (4) of Protocol Section 3.11.2, Planning Criteria, and Sections 3.1.3.1, Definitions of Reliability-Driven and Economic-Driven Projects, and 3.1.3.2, Reliability-Driven Project Evaluation below.

(3)	In conducting an independent review of any project, ERCOT may, in its discretion, make adjustments to the planning case to ensure that the case reaches a solution.  When conducting an independent review of any project classified as Tier 1 pursuant to Protocol Section 3.11.4, Regional Planning Group Project Review Process, ERCOT must provide reasonable advance notice to the RPG of any proposed adjustments and an opportunity for stakeholder comment on them.

(4)	As part of its independent review of any project classified as Tier 1 pursuant to Protocol Section 3.11.4, except for the Transmission Facility improvements submitted based on Section 9.5, ERCOT shall:

(a)	Perform a generation sensitivity analysis.  The generation sensitivity analysis will evaluate the effect that proposed Generation Resources and/or ESRs in or near the study area will have on a recommended transmission project.  Generation Resources and ESRs that have signed Standard Generation Interconnection Agreements (SGIAs) but were not included in the study cases because they did not meet all of the requirements for inclusion in the cases pursuant to Section 6.9, Addition of Proposed Generation to the Planning Models, will be included in the sensitivity analysis.  ERCOT shall not consider the results of the generation sensitivity analysis in determining project need during its independent review of the project; and

(b)	Evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations.  The results of this evaluation shall be included in the final recommendations in the independent review.

(5)	ERCOT’s independent review shall incorporate and consider historical load and any Substantiated Load.

#### 3.1.3.1	Definitions of Reliability-Driven and Economic-Driven Projects

(1)	Proposed transmission projects are categorized for evaluation purposes into two types:

(a)	Reliability-driven projects; and

(b)	Economic-driven projects.

(2)	The differentiation between these two types of projects is based on whether a simultaneously-feasible, security-constrained generating unit commitment and dispatch is expected to be available for all hours of the planning horizon that can resolve the system reliability issue that the proposed project is intended to resolve.  If it is not possible to simulate a dispatch of the Generation Resources and ESRs such that all reliability criteria are met without the project, and the addition of the project allows the reliability criteria to be met, then the project is classified as a reliability-driven project.  If it is possible to simulate a dispatch of the Generation Resources and ESRs in such a way that all reliability criteria are met without the project, but the project may allow the reliability criteria to be met at a lower total cost, then the project is classified as an economic-driven project.  When performing a simulation of the generating unit commitment and dispatch, only contingencies and limits that would be considered in the operations horizon shall be simulated.

### 5.3.5	ERCOT Quarterly Stability Assessment

(1)	ERCOT shall conduct a stability assessment every three months to assess the impact of planned large generators and Large Loads subject to the requirements of Section 9.2.1, Applicability of the Batch Zero Process, connecting to the ERCOT System.

(a)	For large generators with planned Initial Synchronization in the period under study, the assessment shall derive the conditions to be studied with consideration given to the results of the FIS stability studies.

(b)	For new Large Loads and Load modifications subject to the requirements of Section 9.2.1, with planned Initial Energization in the period under study, the assessment shall derive the conditions to be studied from the most current Load Commissioning Plan and with consideration given to the results of the Large Load Interconnection Study (LLIS) stability studies performed according to Section 9.8.4.3, Legacy Dynamic and Transient Stability Analysis, or stability studies performed as part of the Batch Zero Interconnection Study as described in Section 9.3, Batch Zero Interconnection Study.

(c)	ERCOT may study conditions other than those identified in the FIS, LLIS stability studies, or Batch Zero Interconnection Studies.

(2)	Large generators that are not included in the assessment as described in this Section as a result of the IE failing to meet the prerequisites by the deadlines as listed in the table below will not be eligible for Initial Synchronization during that three-month period.  Loads described in paragraph (1)(b) above that are not included in the assessment as a result of failing to meet the prerequisites by the deadlines as listed in the table below will not be eligible for Initial Energization during that three-month period.  The timeline for the quarterly stability assessment shall be in accordance with the following table:

| Generator Initial Synchronization or Large Load Initial Energization Date | Last Day for an IE, Resource Entity, or TSP to meet prerequisites as listed in paragraphs (4) and (5) below | Completion of Quarterly Stability Assessment |
| --- | --- | --- |
| Upcoming January, February, March | Prior August 1 | End of October |
| Upcoming April, May, June | Prior November 1 | End of January |
| Upcoming July, August, September | Prior February 1 | End of April |
| Upcoming October, November, December | Prior May 1 | End of July |

(3)	If the last day for an IE, Resource Entity, or TSP to meet prerequisites or if completion of the quarterly stability assessment as shown in the above table falls on a weekend or holiday, the deadline will extend to the next Business Day.

(4)	The following prerequisites shall be satisfied prior to a large generator being included in the quarterly stability assessment:

(a)	The generator has met the requirements of Section 6.9, Addition of Proposed Generation to the Planning Models.

(b)	The IE has provided all generator data in accordance with the Resource Registration Glossary, Planning Model column, including but not limited to steady state, system protection and stability models.

(i)	The IE shall submit the final dynamic data model at least 45 days prior to the quarterly stability assessment deadline described in paragraph (2) above.  If ERCOT is unable to complete its review prior to the quarterly stability assessment deadline, ERCOT shall not include the Generation Resource, ESR or Settlement Only Generator (SOG) in that quarterly stability assessment.

(ii)	Changes to the dynamic data model after the stability study is deemed complete may subject the Generation Resource, ESR, or SOG to modification of one or more FIS study elements as defined in paragraph (9) of Section 5.3.2.5, FIS Report and Follow-up.  If ERCOT and the lead TSP(s) determine that modifications to one or more FIS study elements are required, then ERCOT shall not include the Generation Resource, ESR, or SOG in a quarterly stability assessment until the revised FIS has been completed in accordance with paragraph (4)(c)(i) below.

(iii)	If an IE submitted a final dynamic data model at least 45 days prior to the quarterly stability assessment deadline but ERCOT determines that the Generation Resource, ESR, or SOG is ineligible to be included in a quarterly stability assessment pursuant to paragraphs (4)(b)(i) or (4)(b)(ii) above, ERCOT will send a notification to the IE.

(c)	The following elements must be complete:

(i)	Final FIS studies, which the TSP must have submitted via the online RIOO system at least 45 days prior to the quarterly stability assessment deadline;

(ii)	Reactive Power Study; and

(iii)	System improvements or mitigation plans that were identified in these studies as required to meet the operational standards established in the Protocols, Planning Guide, Nodal Operating Guides, and Other Binding Documents prior to synchronizing the generator.

(d)	The data used in the studies identified in paragraph (4)(c) above is consistent with data submitted by the IE as required by Section 6.9.

(5)	The following prerequisites must be satisfied prior to the inclusion of a new Large Load or Load modification subject to the requirements of Section 9.2.1 in the quarterly stability assessment:

(a)	The Large Load has met one of the following requirements:

(i)	For quarterly stability assessments with a prerequisite deadline of May 1, 2026 or earlier, the Large Load has met the requirements of Section 9.9, Legacy LLIS Report and Follow-up, and Section 9.10, Legacy Interconnection Agreements and Responsibilities;

(ii)	For quarterly stability assessments with a prerequisite deadline of August 1, 2026, November 1, 2026, February 1, 2027, or May 1, 2027, the Large Load has met the requirements of paragraph (1) of Section 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process; or

(iii)	For quarterly stability assessments with a prerequisite deadline of August 1, 2027 or later, the Large Load has met the requirements of either paragraph (2) of Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment or paragraph (1) of Section 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process;

(b)	The Load Commissioning Plan has been updated to reflect the results of completed studies as required by paragraph (1) of Section 9.2.4, Load Commissioning Plan;

(c)	If applicable, the Interconnecting TSP has provided to ERCOT the dynamic load model it received from the Interconnecting Large Load Entity (ILLE) per paragraph (1) of Section 9.8.4.3, Legacy Dynamic and Transient Stability Analysis, and written affirmation that no changes to the project information have been communicated by the ILLE, per Section 9.2.3, Modification of Large Load Information, that would invalidate the model;

(d)	The Reactive Power Study, if required according to Protocol Section 3.15, Voltage Support, must be complete; and

(e)	The data used in the studies identified in paragraph (c) above is consistent with data used in the final LLIS studies approved per Section 9.9 or completed Batch Zero Interconnection Study as described in Section 9.3, as applicable.

(6)	At any time following the inclusion of a large generator or applicable Large Load in a stability assessment, but before the Initial Synchronization of the generator or Initial Energization of the Large Load, if ERCOT determines, in its sole discretion, that the generator or Large Load no longer meets the prerequisites described in paragraphs (4) or (5) above, or that an IE or ILLE has made a change to the design of the generator or Large Load that could have a material impact on ERCOT System stability, then ERCOT may refuse to allow Initial Synchronization of the generator or Initial Energization of the Large Load.  ERCOT shall include the generator or Large Load in the next quarterly stability assessment period that commences after identification of the material change or after the generator or Large Load meets the prerequisites specified in paragraphs (4) or (5) above, as applicable.  If ERCOT determines, in its sole discretion, that the change to the design of the generator or Large Load would not have a material impact on ERCOT System stability, then ERCOT may not refuse to allow Initial Synchronization of the generator or Initial Energization of the Large Load due to this change.

(7)	ERCOT shall post to the MIS Secure Area a report summarizing the results of the quarterly stability assessment within ten Business Days of completion.

### 6.6.1	Modeling of Large Loads Not Co-Located with a Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG)

(1)	The Interconnecting Transmission Service Provider (TSP) shall not add a new Large Load or Load modification subject to the requirements of Section 9.2.1, Applicability of the Batch Zero Process, to the Network Operations Model until the Large Load has met the requirements for inclusion in the quarterly stability assessment as described in paragraph (5) of Section 5.3.5, ERCOT Quarterly Stability Assessment.

### 6.6.2	Modeling of Large Loads Co-Located with an Existing Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG)

(1)	The addition of a new Large Load to an existing Generation Resource, ESR, or SOG, or the modification of an existing Load at the Generation Resource, ESR, or SOG, subject to the requirements of Section 9.2.1, Applicability of the Batch Zero Process, is considered a material modification of the Resource Registration as described in paragraph (8) of Section 6.8.2, Resource Registration Process.  The Resource Entity shall update the Resource Registration data to reflect the new or increased Load.

(2)	The Resource Entity shall not update the Resource Registration data to reflect the new or increased Load until the Large Load has met the requirements for inclusion in the quarterly stability assessment as described in paragraph (5) of Section 5.3.5, ERCOT Quarterly Stability Assessment.

### 6.6.2.1 	Modeling of Large Loads within a Withdrawal-Limited Private Use Network

(1)	The Resource Entity for a generator in a Withdrawal-Limited Private Use Network (WLPUN) shall include model data for the generator and the Large Load in the WLPUN during the Resource Registration process. The Large Load shall not be included in the Network Operations Model until the following requirements have been satisfied:

(a)	The Large Load has met the requirements for inclusion in the quarterly stability assessment as described in paragraph (5) of Section 5.3.5, ERCOT Quarterly Stability Assessment;

(b)	All applicable requirements of Section 6.9, Addition of Proposed Generation to the Planning Models, have been completed; and

(c)	The established MW Withdrawal limit has been recorded in the Resource Registration data pursuant to Protocol Section 3.10.7.3.1, Withdrawal-Limited Private Use Networks.

(2)	The addition of a new Large Load to an existing WLPUN, or the modification of an existing Large Load that increases the aggregate peak Demand within such a Facility, subject to the requirements of Section 9.2.1, Applicability of the Batch Zero Process, is considered a material modification of the Resource Registration as described in paragraph (8) of Section 6.8.2, Resource Registration Process.  The Resource Entity shall not update the Resource Registration data to reflect the new or increased Load until the Large Load has met the requirements for inclusion in the quarterly stability assessment as described in paragraph (5) of Section 5.3.5, ERCOT Quarterly Stability Assessment.  With the new or increased Load, the MW Withdrawal at the Point of Interconnection (POI) shall not exceed the established MW Withdrawal limit as determined in Sections 9.3.2.2(1)(a)-(c).

(3)	The addition of generation to an existing Withdrawal-Limited Private Use Network is subject to the generation interconnection process under Planning Guide Section 5, Generator Interconnection or Modification, and the requirements of Section 6.9, Addition of Proposed Generation to the Planning Models.

### 6.6.3	Modeling of Large Loads Co-Located with a Proposed Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG)

(1)	A new Large Load co-located with a proposed Generation Resource, ESR, or SOG shall be included in the data provided by the Interconnecting Entity (IE) or Resource Entity during the Resource Registration process.

(2)	The Large Load shall not be included in the Network Operations Model until the following requirements have been satisfied:

(a)	The Large Load has met the requirements for inclusion in the quarterly stability assessment as described in paragraph (5) of Section 5.3.5, ERCOT Quarterly Stability Assessment

; and

(b)	All applicable requirements of Section 6.9, Addition of Proposed Generation to the Planning Models, have been completed.

# 9	LARGE LOAD Interconnection or Modification

## 9.1	Introduction

(1)	This Section defines the requirements and processes used to facilitate new or modified Large Load interconnections with the ERCOT System. It documents the transition from a process that relied on individual Large Load interconnection studies to a new process referred to as the Batch Zero Process. The Batch Zero Process consists of a Batch Zero Interconnection Study and a Batch Zero Refinement Study. The requirements are designed to:

(a)	Facilitate studies to identify potential system limitations and determine, to the extent feasible, facilities needed to interconnect a new Large Load to or modify an existing Large Load on the ERCOT network;

(b)	Facilitate orderly and organized Large Load interconnections, while allowing ERCOT to determine whether the interconnection of the proposed Large Load would comply with North American Electric Reliability Corporation (NERC) Reliability Standards, ERCOT Protocols, ERCOT Planning and Operating Guides, Transmission Service Provider (TSP) criteria, and any Applicable Legal Authority (ALA);

(c)	Specify the communications required between Interconnecting Large Load Entities (ILLEs), TSPs, Distribution Service Providers (DSPs), Resource Entities, Interconnecting Entities (IEs), and ERCOT;

(d)	Provide the best information on future Large Load additions for use in identifying, forecasting, and analyzing short- and long-range ERCOT capabilities, demands, and reserves; and

(e)	Provide ERCOT accurate data about a Large Load subject to the provisions detailed in Section 9.2.1, Applicability of the Batch Zero Process, to ensure that ERCOT and stakeholders have the information necessary for planning purposes.

(2)	Submission of all project data, and other communications described in this Section shall be in the manner and format prescribed by ERCOT. ERCOT shall publicly post the format of such submissions on the ERCOT website.

(3)	Customer-specific 	information submitted to ERCOT by an Interconnecting DSP or Interconnecting TSP pursuant to this Section 9 is considered Protected Information under paragraph (1)(r) of Protocol Section 1.3.1.1, Items Considered Protected Information.

(4)	ERCOT shall manage an email list to facilitate communication of confidential Large Load-related information among Interconnecting DSPs, Interconnecting TSPs and ERCOT.  Membership in this email list will be limited to ERCOT and appropriate Interconnecting DSPs’ and Interconnecting TSPs’ personnel.

(5)	Where an Interconnecting DSP must submit a notarized attestation, it may designate another electric utility, Municipally Owned Utility (MOU), or Electric Cooperative (EC) to submit the notarized attestation on the Interconnecting DSP’s behalf, provided such designation is made in writing.

(6)	A Large Load studied by a TSP through individual interconnection studies that were approved by ERCOT during the interim Large Load interconnection process established on March 25, 2022 and ending December 14, 2025, is deemed to have satisfied Section 9.9, Legacy LLIS Report and Follow-up.

(7)	A Large Load that executed agreements and satisfied other required commitments with its TSP during the interim Large Load interconnection process established on March 25, 2022 and ending December 14, 2025, is deemed to have satisfied Section 9.10, Legacy Interconnection Agreements and Responsibilities.

(8)	Between July 10, 2026 and April 9, 2027, ERCOT may request supporting materials for any attestation provided by the ILLE and may perform site-readiness verifications. ILLEs shall comply with any reasonable requests from ERCOT that are communicated through the ILLE’s Interconnecting DSP or Interconnecting TSP. If ERCOT identifies information that is inconsistent with an attestation or its supporting evidence, ERCOT shall notify the ILLE through the Interconnecting DSP or Interconnecting TSP and provide the ILLE a reasonable opportunity to explain any inconsistency. If, after providing such opportunity, ERCOT determines that an attestation submitted under this Section 9 is false in any material respect, or if the ILLE fails to respond to ERCOT’s request within the time specified by ERCOT, the Large Load that is the subject of the attestation shall be removed from the Batch Zero Process. Disqualification under this paragraph is effective upon written notice from ERCOT to the ILLE, the Interconnecting DSP, and the Interconnecting TSP.

(9)	Any attestation required under this Section 9 must be a notarized attestation sworn to by the attesting party’s representative, official, officer, or other authorized person with binding authority over the attesting party, identifying the attesting individual by name and title and dated as of the date of execution.

### 9.2.1	Applicability of the Batch Zero Process

(1)	Any request to interconnect or modify a Load Facility that meets one or more of the following criteria shall be subject to an ERCOT interconnection process:

(a)	A new Large Load;

(b)	A modification of any existing Load Facility that increases the aggregate peak Demand of the Facility by 75 MW or more; or

(c)	A modification of an existing Large Load that changes or adds a Point of Interconnection (POI) or Service Delivery Point to a different electrical bus on a different electrical circuit.

(2)	ERCOT shall not evaluate Large Load interconnection requests meeting the requirements of paragraph (1) above according to the legacy Large Load Interconnection Study (LLIS) process defined in Sections 9.8-9.10 of this Planning Guide.

(3)	ERCOT shall evaluate Large Load interconnection requests meeting the eligibility criteria in Sections 9.2.1.1 or 9.2.1.2 according to the Batch Zero Process defined in Sections 9.2-9.6.

(4)	Large Loads that do not meet the eligibility criteria in Sections 9.2.1.1 or 9.2.1.2 shall be ineligible to receive approval for Initial Energization until evaluated through a future interconnection study process.

(5) 	Notwithstanding paragraph (2) above, an Interconnecting TSP may complete a LLIS that it commenced prior to the effective date of this provision if the Large Load is part of a proposed net metering arrangement for which an application was submitted to the PUCT pursuant to Public Utility Regulatory Act (PURA), Tex. Util. Code § 39.169 on or before March 4, 2026.  The LLIS shall be used solely for ERCOT’s study of the system impacts of the net metering arrangement conducted in accordance with P.U.C. Subst. R. 25.205.

### 9.2.1.1	Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process

(1)	A Large Load that meets one of the following requirements on or before July 10, 2026, will be modeled in the Batch Zero Process as base load according to paragraph (2) below and its Demand is not subject to further evaluation.

(a)	A Large Load that achieved Initial Energization before March 25, 2022;

(b)	A Large Load that achieved Initial Energization between March 25, 2022, and July 10, 2026;

(c)	A Large Load that, on or before May 1, 2026, met the qualification requirements for inclusion in the quarterly stability assessment or was included in an interim voltage-ride-through assessment;

(d)	A Large Load included in the Permian Basin Reliability Plan Study completed by ERCOT in 2024 and approved by the Public Utility Commission of Texas (PUCT) in Project No. 55718, and the Load contributed to establishing the need for one or more of the identified transmission projects;

(e)	A Large Load that has not achieved Initial Energization as of July 10, 2026, and that meets all the following requirements:

(i)	ERCOT has determined the Large Load has a complete and valid set of interconnection studies as described in Section 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads;

(ii)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has satisfied the requirements defined in Section 9.7, Required Disclosures;

(iii)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has attested to the DSP or TSP that it has ordered all equipment with a lead time of at least 18 months and will take delivery sufficiently in advance of its requested Initial Energization date so the equipment can be installed by the ILLE’s requested Initial Energization date;

(iv)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has attested to the DSP or TSP that it has issued a notice to proceed with the construction of all required interconnection Facilities;

(v)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has attested to the DSP or TSP that it is the end-use customer or, if the ILLE is a developer, it has executed a binding contract with an end-use customer for that customer to take service at the location where the developer is requesting interconnection.  If the ILLE is a developer, the contract must have a term of at least five years from the date the Large Load is expected to reach the total non-coincident peak Demand as stated in the Load Commissioning Plan (LCP);

(vi)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has posted financial security for system upgrades that are necessary to reliably serve the ILLE;

(A)	The Interconnecting DSP or the Interconnecting TSP may accept the following forms of financial security:

(1)	Cash collateral;

(2)	Corporate or parental guaranty, only if the corporation or parent corporation has a credit rating of at least “BBB-” from Standard & Poor’s, “Baa3” from Moody’s Investors Services (Moody’s), or “BBB-” from Fitch Ratings (Fitch).  If the corporation or parent corporation is rated by more than one of these agencies, creditworthiness shall be determined by the second-highest rating; or

(3)	A letter of credit issued by a major U.S. commercial bank, or a U.S. branch office of a major foreign commercial bank, with a credit rating of at least “A-” from Standard & Poor’s, “A3” from Moody’s, or “A-” from Fitch. If the issuing bank is rated by more than one of these agencies, creditworthiness shall be determined by the second-highest rating;

(B)	If the ILLE provides a corporate or parental guaranty, the Interconnecting DSP or Interconnecting TSP may require the submission of financial records or statements to determine the ILLE’s financial stability;

(C)	The Interconnecting DSP or Interconnecting TSP shall determine the financial security required for system upgrades that are necessary to reliably serve the ILLE using the following methodology:

(1) 	If the Large Load’s complete and valid set of interconnection studies as described in Section 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads, is based on an RPG project, the Interconnecting DSP or Interconnecting TSP shall determine the financial security requirement as follows. The cost estimate for the total set of Transmission Facility improvements from the report used as the basis for the RPG acceptance or ERCOT endorsement shall be divided by the total MW peak Demand of new Large Loads that contribute to establishing the need for the project to produce a cost per MW estimate. The financial security requirement for the Large Load shall be the cost per MW estimate multiplied by the peak Demand of the Large Load. If the Interconnecting DSP or Interconnecting TSP is unable to determine the total MW peak Demand of new Large Loads contributing to establishing the need for the project, the financial security requirement for the Large Load shall be $50,000 per MW peak Demand;

(2)	If the Large Load’s complete and valid set of interconnection studies as described in Section 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads, is based on meeting the requirements of Section 9.9, Legacy LLIS Report and Follow-up, and Section 9.10, Legacy Interconnection Agreements and Responsibilities, then the Interconnecting DSP or Interconnecting TSP shall determine which Transmission Facility improvements identified in the LLIS report would not be required but for the ILLE’s Large Load and set the financial security requirement as the cost estimate for those improvements. If the LLIS report identifies Transmission Facility improvements that would not be required but for the ILLE’s Large Load but does not identify a cost estimate for those improvements, then the financial security requirement will be $50,000 per MW peak Demand. If the LLIS report indicates that no Transmission Facility improvements would be required but for the ILLE’s Large Load, then the financial security requirement will be $0;

(3)	If the Large Load does not meet the qualifications of paragraphs (1) or (2) above and the Interconnecting DSP or Interconnecting TSP provides a study to ERCOT by July 24, 2026 that demonstrates to ERCOT’s satisfaction that the addition of the Large Load does not result in any planning criteria violations or the need for Transmission Facility improvements requiring review by the Regional Planning Group, then the Interconnecting DSP or Interconnecting TSP shall set the financial security requirement to $0;

(4)	If the Large Load does not meet the qualifications of paragraphs (1), (2), or (3) above, then the Interconnecting DSP or Interconnecting TSP shall set the financial security requirement as $50,000 per MW peak Demand;

(vii)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has satisfied its financial responsibility for all direct interconnection costs through contribution in aid of construction (CIAC). If the ILLE has an executed interconnection agreement or equivalent agreement before July 10, 2026, the terms of that agreement govern the manner in which direct interconnection costs are satisfied. If the ILLE does not have an executed interconnection agreement, direct interconnection costs shall be satisfied in full through CIAC, either by direct cash payment or posted financial security, on or before July 10, 2026. CIAC payments under this paragraph cannot be offset by a standard contribution or other allowance. Direct interconnection costs include all costs associated with facilities built to interconnect the ILLE to the existing ERCOT system, including radial lines and substation upgrades necessary to interconnect the new ILLE; and

(viii) 	On or before July 24, 2026, the Interconnecting DSP or the Interconnecting TSP has informed ERCOT that the ILLE has attested to the DSP or TSP that it holds one of the property interests described in subparagraphs (A) through (C) below in or relating to one or more parcels of land sufficient to accommodate the ILLE’s planned Load Facilities at the proposed Large Load location.  The attested property interest must be supported by documentary evidence.

(A)	A signed and executed lease agreement for a duration of at least five years from the date the ILLE is expected to reach the total non-coincident peak Demand as stated in its LCP;

(B)	A deed conveying such parcel(s) to the ILLE; or

(C)	A signed and executed purchase and sale agreement for such parcel(s); or

(f)	A Large Load that has not achieved Initial Energization as of July 10, 2026, and that meets all the following requirements:

(i)	ERCOT has determined the Large Load has a complete and valid set of interconnection studies as described in Section 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads;

(ii)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has attested to the DSP or TSP that the ILLE has satisfied the requirements defined in Section 9.7, Required Disclosures;

(iii)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE attested to the DSP or TSP that it has obtained all discretionary approvals required by the applicable municipality or governmental entity at the location where the ILLE is requesting interconnection.  If no such approval is required, the ILLE shall attest that no discretionary approval is required along with a statement supporting the ILLE’s conclusion.  Discretionary approvals may include but are not limited to zoning, special use permits, and conditional use permits;

(iv)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has posted financial security for system upgrades that are necessary to reliably serve the ILLE;

(A)	The Interconnecting DSP or the Interconnecting TSP may accept the following forms of financial security:

(1)	Cash collateral;

(2)	Corporate or parental guaranty, only if the corporation or parent corporation has a credit rating of at least “BBB-” from Standard & Poor’s, “Baa3” from Moody’s, or “BBB-” from Fitch. If the corporation or parent corporation is rated by more than one of these agencies, creditworthiness shall be determined by the second-highest rating; or

(3)	A letter of credit issued by a major U.S. commercial bank, or a U.S. branch office of a major foreign commercial bank, with a credit rating of at least “A-” from Standard & Poor’s, “A3” from Moody’s, or “A-” from Fitch. If the issuing bank is rated by more than one of these agencies, creditworthiness shall be determined by the second-highest rating;

(B)	If the ILLE provides a corporate or parental guaranty, the Interconnecting DSP or Interconnecting TSP may require the submission of financial records or statements to determine the ILLE’s financial stability;

(C)	The Interconnecting DSP or Interconnecting TSP shall determine the financial security required for system upgrades that are necessary to reliably serve the ILLE using the following methodology:

(1) 	If the Large Load’s complete and valid set of interconnection studies as described in Section 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads, is based on an RPG project, the Interconnecting DSP or Interconnecting TSP shall determine the financial security requirement as follows. The cost estimate for the total set of Transmission Facility improvements from the report used as the basis for the RPG acceptance or ERCOT endorsement shall be divided by the total MW peak Demand of new Large Loads that contribute to establishing the need for the project to produce a cost per MW estimate. The financial security requirement for the Large Load shall be the cost per MW estimate multiplied by the peak Demand of the Large Load. If the Interconnecting DSP or Interconnecting TSP is unable to determine the total MW peak Demand of new Large Loads contributing to establishing the need for the project, the financial security requirement for the Large Load shall be $50,000 per MW peak Demand;

(2)	If the Large Load’s complete and valid set of interconnection studies as described in Section 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads, is based on meeting the requirements of Section 9.9, Legacy LLIS Report and Follow-up, and Section 9.10, Legacy Interconnection Agreements and Responsibilities, then the Interconnecting DSP or Interconnecting TSP shall determine which Transmission Facility improvements identified in the LLIS report would not be required but for the ILLE’s Large Load and set the financial security requirement as the cost estimate for those improvements. If the LLIS report identifies Transmission Facility improvements that would not be required but for the ILLE's Large Load but does not identify a cost estimate for those improvements, then the financial security requirement will be $50,000 per MW peak Demand. If the LLIS report indicates that no Transmission Facility improvements would be required but for the ILLE’s Large Load, then the financial security requirement will be $0;

(3)	If the Large Load does not meet the qualifications of paragraphs (1) or (2) above and the Interconnecting DSP or Interconnecting TSP provides a study to ERCOT by July 24, 2026 that demonstrates to ERCOT’s satisfaction that the addition of the Large Load does not result in any planning criteria violations or the need for Transmission Facility improvements requiring review by the Regional Planning Group, then the Interconnecting DSP or Interconnecting TSP shall set the financial security requirement to $0;

(4)	If the Large Load does not meet the qualifications of paragraphs (1), (2), or (3) above, then the Interconnecting DSP or Interconnecting TSP shall set the financial security requirement as $50,000 per MW peak Demand;

(v)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has satisfied its financial responsibility for all direct interconnection costs through CIAC. If the ILLE has an executed interconnection agreement or equivalent agreement before July 10, 2026, the terms of that agreement govern the manner in which direct interconnection costs are satisfied. If the ILLE does not have an executed interconnection agreement, direct interconnection costs shall be satisfied in full through CIAC, either by direct cash payment or posted financial security, on or before July 10, 2026. CIAC payments under this paragraph cannot be offset by a standard contribution or other allowance. Direct interconnection costs include all costs associated with facilities built to interconnect the ILLE to the existing ERCOT system, including radial lines and substation upgrades necessary to interconnect the new ILLE; and

(vi) 	On or before July 24, 2026, the Interconnecting DSP or the Interconnecting TSP has informed ERCOT that the ILLE has attested to the DSP or TSP that it holds one of the property interests described in subparagraphs (A) through (C) below in or relating to one or more parcels of land sufficient to accommodate the ILLE’s planned Load Facilities at the proposed Large Load location.  The attested property interest must be supported by documentary evidence.

(A)	A signed and executed lease agreement for a duration of at least five years from the date the ILLE is expected to reach the total non-coincident peak Demand as stated in its LCP;

(B)	A deed conveying such parcel(s) to the ILLE; or

(C)	A signed and executed purchase and sale agreement for such parcel(s);

(vii)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE attested to the DSP or TSP that it has executed a binding contract with a general contractor for construction of the ILLE’s planned Load Facilities at the location where the ILLE is requesting interconnection. The contract must cover the full scope of work necessary to complete the ILLE’s planned Load Facilities; and

(viii)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE attested to the DSP or TSP that it has executed a binding contract with a substation contractor, which may include the Interconnecting DSP or TSP, for construction of all the ILLE’s substation facilities at the location where the ILLE is requesting interconnection.  The substation contractor must hold an Electrical Contractor license issued by the Texas Department of Licensing and Regulation or perform such work through licensed subcontractors. The requirement excludes facilities owned by the Interconnecting DSP or Interconnecting TSP; or

(g)	A Large Load that has not achieved Initial Energization as of July 10, 2026, and that meets all the following requirements:

(i)	The Large Load is part of a proposed net metering arrangement for which an application was submitted to the PUCT pursuant to Public Utility Regulatory Act (PURA), Tex. Util. Code § 39.169 on or before March 4, 2026;

(ii)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has satisfied the requirements defined in Section 9.7, Required Disclosures; and

(iii)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has posted financial security for system upgrades that are necessary to reliably serve the ILLE;

(A)	The Interconnecting DSP or the Interconnecting TSP may accept the following forms of financial security:

(1)	Cash collateral;

(2)	Corporate or parental guaranty, only if the corporation or parent corporation has a credit rating of at least “BBB-” from Standard & Poor’s, “Baa3” from Moody’s, or “BBB-” from Fitch. If the corporation or parent corporation is rated by more than one of these agencies, creditworthiness shall be determined by the second-highest rating; or

(3)	A letter of credit issued by a major U.S. commercial bank, or a U.S. branch office of a major foreign commercial bank, with a credit rating of at least “A-” from Standard & Poor’s, “A3” from Moody’s, or “A-” from Fitch. If the issuing bank is rated by more than one of these agencies, creditworthiness shall be determined by the second-highest rating;

(B)	If the ILLE provides a corporate or parental guaranty, the Interconnecting DSP or Interconnecting TSP may require the submission of financial records or statements to determine the ILLE’s financial stability; and

(C)	The Interconnecting DSP or Interconnecting TSP shall determine the financial security required for system upgrades that are necessary to reliably serve the ILLE using the following methodology:

(1)	The Interconnecting DSP or Interconnecting TSP shall determine which Transmission Facility improvements identified in the LLIS report would not be required but for the ILLE’s Large Load and set the financial security requirement as the cost estimate for those improvements. If the LLIS report identifies Transmission Facility improvements that would not be required but for the ILLE’s Large Load but does not identify a cost estimate for those improvements, then the financial security requirement will be $50,000 per MW peak Demand. If the LLIS report indicates that no Transmission Facility improvements would be required but for the ILLE’s Large Load, then the financial security requirement will be $0.

(2)	ERCOT shall model Large Loads meeting the requirements of paragraph (1) above in Batch Zero as follows:

(a)	A Large Load meeting the requirements of paragraph (1)(a) shall be modeled at the Large Load’s level of peak Demand reported to ERCOT in response to ERCOT’s annual request for information as part of the development of the 2026 Regional Transmission Plan (RTP) if included, otherwise the peak Demand will be as modeled in the SSWG cases.

(b)	A Large Load meeting the requirements of paragraph (1)(b) and (1)(c) shall be modeled in each year of the study at the Large Load’s level of peak Demand that is defined in one of the following documents. In the event the Large Load is represented in both documents, ERCOT shall use the document with the lower values of Demand.

(i)	The level of peak Demand reported to ERCOT in response to ERCOT’s annual request for information as part of the development of the 2026 RTP; or

(ii)	The level of peak Demand indicated in the most recent LCP, if applicable, provided to ERCOT on or before July 24, 2026. The LCP provided must be consistent with the previously completed studies and existing agreements.

(c)	A Large Load meeting the requirements of paragraphs (1)(d), (1)(e), or (1)(f) shall be modeled in each year of the study at the level of peak Demand that is defined in one of the following documents. In the event the Large Load is represented in both documents, ERCOT shall use the document with the lower values of Demand.

(i)	The level of peak Demand specified in the Large Load’s executed interconnection agreement or equivalent agreement; or

(ii)	The level of peak Demand that can be served reliably as indicated in the Large Load’s qualifying complete and valid interconnection studies, as described in Section 9.2.1.4.

(A)	For Large Loads with qualifying complete and valid interconnection studies based on Section 9.2.1.4(3)(a), 9.2.1.4(3)(c), or 9.2.1.4(4)(a)(ii)(A), the level of peak Demand that can be reliably served will be assumed to be the level modeled in the study, and the timing will be based on the date in which all of the recommended transmission improvements are planned to be in-service as indicated in the final report to RPG or in the latest Transmission Project and Information Tracking (TPIT) report.

(1) 	If the Large Load also has a complete and valid interconnection study under Section 9.2.1.4(3)(b) or 9.2.1.4(4)(a)(ii)(B), the load level for each year prior to the date in which all of the recommended transmission improvements are planned to be in-service shall be determined under paragraph (B) below.

(2) 	If the Large Load does not have a complete and valid interconnection study under paragraph (2)(c)(ii)(A)(1), the base load level for each year prior to the date in which all of the recommended transmission improvements are planned to be in-service shall be zero, and the Large Load shall be studied for allocation under Section 9.2.1.2(3).

(B)	For Large Loads with qualifying complete and valid interconnection studies based on Section 9.2.1.4(3)(b) or 9.2.1.4(4)(a)(ii)(B), the level of peak Demand that can be reliably served will be assumed to be the level as indicated in the Load Commissioning Plan (LCP) in the interconnection study report. If load level increases in the LCP are based on transmission improvement(s), the date of the Load level increases will be based on the planned in-service of the transmission improvements as indicated in the latest Transmission Project and Information Tracking (TPIT) report. If the transmission improvement is not included in the latest TPIT report, then the transmission improvement will be assumed to have an in-service date of 2034 for purposes of Batch Zero. If the transmission improvement is not included in the latest TPIT, ERCOT may request the TSP provide an estimated in-service date in lieu of assuming an in-service date of 2034.

(d)	A Large Load meeting the requirements of paragraph (1)(g) shall be modeled in each year of the study at the level of peak Demand specified in the PURA, Tex. Util. Code § 39.169 proceeding.

### 9.2.1.2	Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero

(1)	A Large Load that meets (a), (b), (c), and (d) as described in this paragraph shall be included in Batch Zero as Load subject to reliability assessment and allocation.

(a)	On or before July 10, 2026, a Large Load that meets one of the following:

(i)	The Large Load satisfied the requirement documented in paragraph (1)(e)(i) or (1)(f)(i) of Section 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process, but does not meet one or more of the other requirements documented in paragraph (1)(e) or (1)(f) of Section 9.2.1.1;

(ii)	The Large Load was included in the list established in paragraph (4) of Section 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads, but was determined to have invalid existing studies according to the methodology established in paragraphs (4)(d) and (4)(e) of that Section; or

(iii)	The Large Load has received ERCOT approval of a steady-state or stability study as described in Section 9.8, Legacy Interconnection Study Procedures for Large Loads and Section 9.9, Legacy LLIS Report and Follow-up; and

(b)	On or before July 24, 2026, the Interconnecting DSP or the Interconnecting TSP has informed ERCOT that the ILLE has attested to the DSP or TSP that it holds one of the property interests described in subparagraphs (i) through (iv) below in or relating to one or more parcels of land sufficient to accommodate the ILLE’s planned Load Facilities at the proposed Large Load location.  The attested property interest must be supported by documentary evidence.

(i)	A signed and executed lease agreement for a duration of at least five years from the date the ILLE is expected to reach the total non-coincident peak Demand;

(ii)	A deed conveying such parcel(s) to the ILLE;

(iii) 	A signed and executed purchase and sale agreement for such parcel(s); or

(iv)	A signed and executed agreement with an option to purchase or lease for such parcel(s);

(c)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has posted financial security for system upgrades equal to $50,000 per MW of its peak Demand in its most recent Load Commissioning Plan (LCP) in accordance with paragraph (2) below; and

(i)	The Interconnecting DSP or the Interconnecting TSP may accept the following forms of financial security:

(A)	Cash collateral;

(B)	Corporate or parental guaranty, only if the corporation or parent corporation has a credit rating of at least “BBB-” from Standard & Poor’s, “Baa3” from Moody’s, or “BBB-” from Fitch. If the corporation or parent corporation is rated by more than one of these agencies, creditworthiness shall be determined by the second-highest rating; or

(C)	A letter of credit issued by a major U.S. commercial bank, or a U.S. branch office of a major foreign commercial bank, with a credit rating of at least “A-” from Standard & Poor’s, “A3” from Moody’s, or “A-” from Fitch. If the issuing bank is rated by more than one of  these agencies, creditworthiness shall be determined by the second-highest rating;

(ii)	If the ILLE provides a corporate or parental guaranty, the Interconnecting DSP or the Interconnecting TSP may require the submission of financial records or statements to determine the ILLE’s financial stability.

(d)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has satisfied the requirements defined in Section 9.7, Required Disclosures.

(2)	ERCOT shall model a Large Load meeting the requirements of paragraph (1) above according to the peak Demand in the most recent LCP provided by the Interconnecting TSP on or before July 24, 2026. The LCP shall reflect an Initial Energization date of January 1, 2028, or later.

(3)	ERCOT shall model a Large Load meeting the requirements of Section 9.2.1.1(2)(c)(ii)(A)(2) according to the level of peak Demand specified in the Large Load’s interconnection agreement or equivalent agreement.  Financial security posted by the ILLE under Section 9.2.1.1 satisfies the financial security requirement for the Large Load's inclusion under this paragraph.

### 9.2.1.3	Load not Included in Batch Zero

(1)	ERCOT shall not include in Batch Zero any Large Load that does not meet requirements described in Section 9.2.1.1 or 9.2.1.2.

(2)	ERCOT shall not include any Large Load that otherwise meets the requirements described in Section 9.2.1.1 or 9.2.1.2 if the Interconnecting TSP or Interconnecting DSP fails to provide to ERCOT all information required by Section 9.2.2 on or before July 24, 2026.

### 9.2.1.4	Evaluation of Existing Interconnection Studies for Large Loads

(1)	ERCOT shall use the methodology described in this Section to assess the completeness and validity of previous studies as prescribed in Section 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process and Section 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero.

(2)	During its review, ERCOT, in consultation with the Interconnecting DSP and/or Interconnecting TSP, will determine the completeness and validity of previous studies.

(3)	ERCOT shall consider previous studies for Large Loads that have not achieved Initial Energization by July 10, 2026, to be fully complete and valid without additional review if they meet one of the criteria in paragraphs (a) through (c) below. Studies qualifying under paragraph (d) below shall be considered complete and valid only upon ERCOT’s review and acceptance of the Interconnecting TSP’s submission.

(a)	The Large Load was included in the study area of one or more studies submitted to the Regional Planning Group (RPG) before December 15, 2025, the Load contributed to establishing the need for the RPG transmission project that resolved the performance deficiency in the study area, and the proposed transmission project received RPG acceptance or ERCOT endorsement as described in Protocol Section 3.11.4.9, Regional Planning Group Acceptance and ERCOT Endorsement, on or before March 4, 2026;

(b)	The Large Load met the requirements of Section 9.9, Legacy LLIS Report and Follow-up, and Section 9.10, Legacy Interconnection Agreements and Responsibilities, on or before March 4, 2026; or

(c)	The Large Load was included in the Permian Basin Reliability Plan Study completed by ERCOT in 2024 and approved by the Public Utility Commission of Texas (PUCT) in Project No. 55718, and the Load contributed to establishing the need for the identified transmission projects.

(d)	The Large Load was the subject of an interconnection study performed outside the interim Large Load interconnection process in effect between March 25, 2022, and December 14, 2025.  The results of that study determined the Large Load could be reliably served without Transmission Facility improvements requiring review by the Regional Planning Group. The Interconnecting TSP submitted to ERCOT, on or before July 24, 2026, a notarized attestation that addresses items (i) through (v) below.  The Interconnecting TSP may also submit additional documentation demonstrating the inclusion of the Large Load in ERCOT transmission planning studies, including submissions to the RPG or other ERCOT study processes.

(i)	The date on which the ILLE executed a study agreement with the Interconnecting TSP, the Initial Energization date specified in that agreement, and the MW Demand requested by the ILLE;

(ii)	A statement that the period between the ILLE’s interconnection request and requested Initial Energization date was more than two years;

(iii)	A statement that the Interconnecting TSP performed an interconnection study for the Large Load through the TSP’s customary study process;

(iv)	A statement that the results of the interconnection study completed on or before December 15, 2025, determined the Large Load could be reliably served without Transmission Facility improvements requiring review by the Regional Planning Group; and

(v)	A statement that the ILLE has executed an interconnection agreement or equivalent agreement to proceed with interconnection on or before December 15, 2025.

(4)	ERCOT will consider previous studies for Large Loads that have not achieved Initial Energization by July 10, 2026, and that do not have studies meeting the criteria in paragraph (3) above to be fully complete and valid according to the following process:

(a)	ERCOT shall identify all Large Loads that meet all of the following criteria:

(i)	The Interconnecting TSP has, by July 24, 2026, determined the dynamic data submitted by the ILLE per paragraph (3) of Section 9.2.2, Submission of Large Load Information for Batch Zero Process, is not expected to adversely impact the results from the previous stability study; and

(ii)	The Large Load meets either of the following conditions:

(A)	The Large Load was included in one or more studies submitted to the RPG before December 15, 2025, that Load contributed to establishing the need for the RPG project, and the proposed project received RPG acceptance or ERCOT endorsement as described in Protocol Section 3.11.4.9, Regional Planning Group Acceptance and ERCOT Endorsement, on or before July 10, 2026; or

(B)	The Large Load met the requirements of Section 9.9, Legacy LLIS Report and Follow-up, and Section 9.10, Legacy Interconnection Agreements and Responsibilities, on or before July 10, 2026.

(b)	ERCOT shall create a list of all Large Loads meeting the criteria in paragraph (4)(a) above. ERCOT shall order the list according to the date each Large Load met the applicable criteria in paragraph (4)(a)(ii). The Large Load with the oldest date shall be given first position, with subsequent loads following in order of date the criteria in paragraph (4)(a)(ii) were met.

(i)	In the event a Large Load meets both the criteria in paragraph (4)(a)(ii)(A) and (4)(a)(ii)(B) or in the event the Large Load meets the criteria in paragraph (4)(a)(ii)(A) multiple times, ERCOT shall use the date that gives the Large Load the highest position in the list.

(c)	In the event two Large Loads met the criteria documented in paragraph (4)(a)(ii) on the same date, ERCOT shall use the following methodology to determine placement on the list:

(i)	If both Large Loads were included in the same RPG study, ERCOT shall give them equal placement on the list;

(ii)	If each Large Load is from a separate RPG study, the Load with the earlier RPG study submission date will receive priority;

(iii)	If one Large Load met the criteria described in paragraph (4)(a)(ii)(A) and the other met the criteria described in paragraph (4)(a)(ii)(B), the Load meeting the criteria of paragraph (4)(a)(ii)(A) will receive priority regardless of submission date; and

(iv)	If both Large Loads met the criteria described in paragraph (4)(a)(ii)(B), the Load with the earlier submission date of a TSP study to ERCOT will receive priority;

(d)	ERCOT shall begin by evaluating the Large Load(s) in the first position on the list. ERCOT shall consider the existing studies for the Large Load(s) in the first position to be valid if, in ERCOT’s sole discretion, each Large Load meeting the criteria in paragraphs (3)(a) through (3)(c) above is:

(i)	Located outside of the study area of the Large Load in the first position; or

(ii)	Located within the study area and included in the existing studies for the Large Load in the first position.

(e)	ERCOT shall evaluate each subsequent Large Load on the list in the order established in paragraphs (4)(b) and (4)(c), including any set of Large Loads sharing equal placement under paragraph (4)(c)(i). ERCOT shall consider the existing studies for the Large Load under review to be valid if, in ERCOT’s sole discretion, each Large Load meeting the criteria in paragraphs (3)(a) through (3)(c) above and each Large Load on the list already determined to have valid existing studies is:

(i)	Located outside of the study area of the Large Load under review; or

(ii)	Located within the study area and included in the existing studies for the Large Load under review.

### 9.2.2	Submission of Large Load Information for Batch Zero Process

(1)	For any Load request meeting one or more criteria defined in paragraph (1) of Section 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process, and 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero, the following actions shall be completed prior to the initiation of the Batch Zero Interconnection Study described in Section 9.3, Batch Zero Interconnection Study.

(a)	Submission of all information, including but not limited to, data required by the Interconnecting Distribution Service Provider (DSP), the Interconnecting Transmission Service Provider (TSP), and ERCOT to perform steady-state, short circuit, dynamic and transient stability analyses and any other studies the Interconnecting TSP or ERCOT deems necessary to reliably interconnect the Load;

(b)	Submission of a preliminary Load Commissioning Plan (LCP) that fully reflects the proposed project schedule; and

(c)	Written acknowledgement from the Interconnecting Large Load Entity (ILLE) of its obligations to notify and update the Interconnecting DSP and Interconnecting TSP of changes to the Large Load project information or to the load composition, technology, parameters, or development schedule as described in Section 9.2.3, Modification of Large Load Information, during the interconnection process.

[PGRR115: Insert paragraph (d) below upon system implementation of NPRR1234:] (d) Payment of the LLIS Application Fee to ERCOT as described in paragraph (4).

(2)	The Interconnecting TSP shall submit the information described in paragraphs (1)(a) through (1)(c) above on behalf of the ILLE on or before July 24, 2026.

(3)	By July 10, 2026, the ILLE must promptly provide to ERCOT and the Interconnecting TSP dynamic data including the necessary models, parameters, and supporting documentation required for accurate representation of the Large Load. The data shall be compatible with the version of the planning and operations model software, as described in the Dynamic Working Group Procedure Manual in effect on March 4, 2026. If a dynamic stability study on the Large Load has previously been performed, the Interconnecting TSP must also provide to ERCOT by July 24, 2026, a written determination as to whether the dynamic data submitted by the ILLE is expected to adversely impact the results from the previous stability study.

(a)	If ERCOT determines that dynamic data submitted by an ILLE is deficient, ERCOT shall notify the ILLE of the deficiency no later than August 7, 2026. The ILLE shall resolve the deficiency no later than August 31, 2026. Failure to cure the deficiency by August 31, 2026, shall result in removal of the associated Large Load from the Batch Zero Interconnection Study.

(4)	A Large Load that elects to be studied as a Provisional Controllable Load Resource (PCLR) pursuant to Section 9.2.2.1 or a Withdrawal-Limited Private Use Network pursuant to Section 9.2.2.2 may not elect to be studied as both.

[PGRR115: Insert paragraph (3) below upon system implementation of NPRR1234:] (5) The ILLE shall pay to ERCOT the LLIS Application Fee, as described in the ERCOT Fee Schedule prior to the commencement of the LLIS. The interconnecting TSP, Resource Entity, or Interconnecting Entity (IE) may choose to submit this fee to ERCOT on the behalf of the ILLE. Payment of the ERCOT LLIS Application Fee shall not affect the independent responsibility of the ILLE to pay for interconnection studies conducted by the interconnecting TSP or for any Distribution Service Provider (DSP) studies.

### 9.2.2.1	Additional Information Required for Provisional Controllable Load Resources (PCLRs)

(1)	A Large Load must be eligible for inclusion as Load to be studied and allocated in Batch Zero pursuant to Section 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero, to request PCLR treatment under this Section.

(2)	For a Large Load request to be studied as a PCLR in Batch Zero, the Interconnecting Large Load Entity (ILLE) must complete and notarize Part A of Protocol Section 23, Form W, Declaration of Intent and Commitment to Register as a Provisional Controllable Load Resource (PCLR). Part A must be signed by the Interconnecting Large Load Entity’s (ILLE’s) representative, official, officer, or other authorized person with binding authority over the ILLE and submitted to the Interconnecting DSP or Interconnecting TSP on or before July 10, 2026. The Interconnecting DSP or Interconnecting TSP must submit the form to ERCOT on or before July 24, 2026.

### 9.2.2.2	Additional Information Required for Withdrawal-Limited Private Use Networks (WLPUNs)

(1)	A Large Load must be eligible for inclusion as Load to be studied and allocated in Batch Zero pursuant to Section 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero, to request WLPUN treatment under this Section.

(2)	For a Large Load request to be studied as a WLPUN in Batch Zero, the Interconnecting Large Load Entity (ILLE) and the Interconnecting Entity (IE) or Resource Entity must complete, execute, and notarize Protocol Section 23, Form X, Withdrawal-Limited Private Use Network Designation. Form X must be submitted to the Interconnecting DSP or Interconnecting TSP on or before July 10, 2026. The Interconnecting DSP or Interconnecting TSP must submit the form to ERCOT on or before July 24, 2026 on behalf of the executing parties.

(3)	For a new generator to be included in a WLPUN in Batch Zero, it must meet all the following requirements:

(a)	The Full Interconnection Study (FIS) request must be submitted as described in paragraph (3) of Section 5.3.2 and deemed complete by ERCOT on or before July 10, 2026; and

(b)	As of July 10, 2026, the generation must not have met all the requirements specified in paragraph (1) of Section 6.9, Addition of Proposed Generation to the Planning Models, for ERCOT’s inclusion of the generation in the base cases created and maintained by the Steady State Working Group.

(4)	Multiple generation interconnection requests may be included in the WLPUN application provided each generator is planned to be connected to the same Point of Interconnection (POI) as the Large Load. The generation interconnection requests must have the same IE or Resource Entity.

### 9.2.3	Modification of Large Load Information

(1)	The Interconnecting TSP shall update any project information submitted per paragraph (1) of Section 9.2.2, Submission of Large Load Information for Batch Zero Process, within ten Business Days of being notified by the ILLE of a material change.

(2)	The ILLE shall notify the Interconnecting DSP and Interconnecting TSP if a change to the load composition, technology, or parameters occurs after the ILLE has provided the TSP with its initial dynamic data per paragraph (3) of Section 9.2.2, Submission of Large Load Information for Batch Zero Process. Upon such notification, the ILLE shall provide to the Interconnecting TSP updated dynamic data reflecting the change. The Interconnecting DSP and Interconnecting TSP shall promptly provide the updated dynamic data to ERCOT.

### 9.2.4	Load Commissioning Plan

(1)	The Load Commissioning Plan (LCP) shall be maintained and updated by the Interconnecting TSP and ERCOT as prescribed in Section 9 of the Planning Guide using information provided by the ILLE. The LCP must specify the load increments and timeline by which the ILLE intends to increase peak Demand. The LCP shall reflect the most currently available information about the Large Load and ILLE and shall be updated upon receipt of updated project information from the ILLE and as otherwise described in this Section.

(2)	Upon the completion of the Batch Zero Interconnection Study, as described in Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment, ERCOT shall update the LCP to reflect the amount of peak Demand that can be served reliably for each year of the Batch Zero Interconnection Study scope.

(3)	Upon the execution of an interconnection agreement prescribed by P.U.C. Subst. R. 25.194, the Interconnecting TSP shall update the LCP to reflect the executed interconnection agreement.

(4)	Following the Batch Zero Interconnection Study, the Interconnecting TSP shall update the LCP of a Large Load subject to allocation under Section 9.2.1.1(2)(c)(ii)(A)(2).

(5)	The Interconnecting TSP shall continue to maintain the LCP after Initial Energization until the Large Load reaches its full requested peak Demand, updating as needed to reflect changes in the Large Load construction and timelines.

### 9.2.5	Required Interconnection Equipment

(1)	Each Service Delivery Point for a Large Load not co-located with a Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG) interconnected at transmission voltage to the ERCOT System must have a permanent configuration consisting of one or more breakers capable of interrupting fault current to isolate the Large Load from the ERCOT System without interrupting flow on the associated transmission lines. The breakers shall be under the remote control of the applicable Transmission Operator (TO).

(2)	Each Large Load co-located with a Generation Resource, ESR, or SOG interconnected at transmission voltage to the ERCOT System must have a permanent configuration consisting of one or more breakers capable of interrupting fault current to isolate the Large Load from the ERCOT System without isolating any of the co-located generators. The breakers shall be remotely controllable at the direction of the applicable Qualified Scheduling Entity (QSE).

(3)	Large Loads submitted under the legacy Large Load Interconnection Study (LLIS) process described in Sections 9.8-9.10 with an initial LLIS submission date on or after June 1, 2025, and Large Loads meeting requirements, described in Sections 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process, and 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero, for inclusion in the Batch Zero Interconnection Study shall not have an interconnection configuration such that any category P1 or P7 event described in the North American Electric Reliability Corporation (NERC) Reliability Standard addressing transmission planning performance requirements results in more than 1,000 MW of consequential Load loss.

(a)	All Loads co-located with a Generation Resource as described in Protocol Section 10.3.2.3, Generation Netting for ERCOT-Polled Settlement Meters, shall be subject to the requirements of this paragraph.

(b)	For a Withdrawal-Limited Private Use Network (WLPUN), consequential Load loss shall be determined based on the aggregate peak Demand of the included Large Load, not the established MW Withdrawal limit at the Point of Interconnection (POI).

(4)	Large Loads submitted under the legacy LLIS process described in Sections 9.8-9.10 with an initial LLIS submission date before June 1, 2025, shall comply with the requirements of paragraph (3) of this Section if, on or after June 1, 2025, a modification to the Large Load subject to the requirements of Section 9.2.1, Applicability of the Batch Zero Process, is made.

## 9.3	Batch Zero Interconnection Study

(1)	This Section establishes the procedures for conducting a Batch Zero Interconnection Study for new or modified Large Loads, as defined by Section 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process, and Section 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero.

### 9.3.1	Batch Zero Process Overview and Timelines

(1)	The Batch Zero Interconnection Study consists of a singular, system-wide study covering steady-state analysis and stability screening analysis performed by ERCOT.

(2)	The Batch Zero Process shall be conducted according to the following timeline:

(a)	Interconnecting Distribution Service Providers (DSPs) and Interconnecting Transmission Service Providers (TSPs) must provide to ERCOT all information required by Sections 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process, 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero, and 9.2.2, Submission of Large Load Information for Batch Zero Process, on or before July 24, 2026. ERCOT will notify each Interconnecting DSP and Interconnecting TSP of how each Large Load submitted under Section 9.2.2 is included and classified in the Batch Zero Interconnection Study according to the methodology defined in Section 9.2.1, Applicability of the Batch Zero Process, on or before August 7, 2026.

(i)	If ERCOT’s classification determines that a Large Load submitted under Section 9.2.1.1 does not satisfy the base load eligibility criteria and will instead be classified under Section 9.2.1.2, the Interconnecting DSP or Interconnecting TSP, as applicable, shall notify the ILLE within two Business Days of receipt of ERCOT’s classification notice. If the ILLE believes the classification is based on incomplete or inaccurate information, the ILLE must notify ERCOT through its Interconnecting DSP or Interconnecting TSP no later than three Business Days after receiving notification. Upon receipt of such notice, ERCOT, the ILLE, and the Interconnecting DSP or Interconnecting TSP shall attempt to resolve the dispute within three Business Days. If the dispute is not resolved and the reclassification stands, the provisions of paragraphs (2)(a)(ii) through (2)(a)(iii) below apply.

(ii)	The ILLE shall have seven Business Days from the date of notification to post the financial security required by paragraph (1)(c) of Section 9.2.1.2. The Interconnecting DSP or Interconnecting TSP, as applicable, must inform ERCOT within two Business Days of the ILLE posting the required financial security.

(iii)	Failure to post the required financial security within the period specified in paragraph (2)(a)(ii) shall result in the Large Load being excluded from the Batch Zero Interconnection Study.

(b)	ERCOT shall provide the Batch Zero Interconnection Study report to all Interconnecting DSPs and Interconnecting TSPs on or before April 9, 2027. ERCOT shall also communicate updated Load Commissioning Plans (LCPs) to Interconnecting Large Load Entities (ILLEs).

(c)	Interconnecting DSPs and Interconnecting TSPs shall provide to ERCOT a list of all Large Loads for which the ILLE has met the commitment requirements, as described in Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment, on or before the deadline for a Large Load customer to execute an interconnection agreement following completion of the interconnection study as specified in P.U.C. Subst. R. 25.194.

(d)	ERCOT shall complete the Batch Zero Refinement Study and provide a Batch Zero transmission plan to the Regional Planning Group (RPG), as described in Section 9.5, Batch Zero Study Refinement and Delivery of Transmission Plan, on or before 90 days following the deadline in paragraph (c) above.

(3)	The Interconnecting TSP must complete the short-circuit study prescribed in Section 9.5.2, System Protection (Short-Circuit) Analysis, and provide a study report to ERCOT at least 60 days prior to the date specified in paragraph (2)(d) above.

### 9.3.2	Batch Zero Interconnection Study Methodology

(1)	ERCOT shall establish a study scope and methodology to assess the steady-state and stability impacts of the Large Loads subject to assessment in accordance with paragraph (1) of Section 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero, for years 2028, 2030, and 2032.

(2)	ERCOT shall present the study scope and methodology to the Regional Planning Group (RPG) and allow an opportunity for stakeholder comments.

(3)	ERCOT shall post the initial Batch Zero Interconnection Study steady-state cases and contingencies, the final Batch Zero Interconnection Study cases, the initial Batch Zero Refinement Study cases and contingencies, and the final Batch Zero Refinement Study cases on the MIS Secure area once available.

(4)	For each Large Load subject to assessment in the Batch Zero Interconnection Study, ERCOT shall identify any reliability criteria violations associated with the proposed addition in accordance with the study scope and shall endeavor to resolve any identified performance deficiencies by identifying Transmission Facility improvements for 2028, 2030, and 2032.

(a)	ERCOT shall consult with the applicable TSP(s) when identifying proposed Transmission Facility improvements.

(b)	ERCOT shall post the 2032 study steady-state start case, contingencies and initial reliability screening results for TSPs once the initial Batch Zero Interconnection Study cases become available.

(c)	TSP(s) may perform studies for their area of responsibility using the 2032 start case and submit to ERCOT any Transmission Facility improvements along with the steady-state model files, including an assessment of the construction feasibility, projected in-service date within 60 days of the postings described in paragraph (b) above.

(d)	ERCOT shall consider the Transmission Facility improvements identified by the TSPs to resolve the performance deficiencies in the Batch Zero Interconnection Study.

(e)	ERCOT in its discretion shall decide not to include any Transmission Facility improvements that may require additional studies and review that are beyond the scope and timeline of the Batch Zero Interconnection Study process.

(f)	Each TSP shall provide any Transmission Facility improvement cost estimates within 10 Business Days of ERCOT’s request.

(g)	ERCOT shall make final determinations on the Transmission Facility improvements that will be identified and recommended in the Batch Zero Interconnection Study.

(h)	ERCOT shall post the 2028 and 2030 study steady-state start cases, contingencies and initial reliability screening results for TSPs as those initial Batch Zero Interconnection Study cases become available.

(5)	ERCOT shall determine the amount of peak Demand that may be served reliably for 2028, 2030, and 2032 through full scope analysis and for 2029 and 2031 through limited scope analysis.

(6)	The amount of peak Demand allocated to a Large Load subject to assessment in accordance with paragraphs (2) or (3) of Section 9.2.1.2 shall not decrease from one year to the next within the Batch Zero Interconnection Study scope. Where the amount of peak Demand that can be served reliably in a given year is less than the amount allocated in a prior year, ERCOT shall reduce the prior year’s allocation to equal the lower amount.

(7)	If, after the application of paragraph (6) above, the allocated peak Demand for a Large Load that is subject to assessment in accordance with paragraph (2) or (3) of Section 9.2.1.2 is less than the minimum load allocation in a given year, ERCOT shall set the allocated peak Demand for that Large Load to zero MW for that year.

(a)	For Large Loads that have been requested to be studied as a PCLR, the minimum load allocation is zero.

(b)	For Large Loads that have been requested to be studied as a Withdrawal-Limited Private Use Network (WLPUN), the minimum load allocation is zero.

(c)	For Large Loads not subject to paragraph (a) or (b) above and that have requested a peak Demand in a given year that is 100 MW or less, the minimum load allocation is 90% of the requested peak Demand.

(d)	For Large Loads not subject to paragraphs (a), (b), or (c) above, the minimum load allocation is 100 MW.

(e)	If the application of this paragraph results in the allocated peak Demand for a Large Load being set to zero in any year, ERCOT shall also set the allocated peak Demand to zero for all prior years.

### 9.3.2.1	Treatment of Provisional Controllable Load Resources (PCLRs) in the Batch Zero Interconnection Study

(1)	For Large Loads subject to assessment in accordance with paragraph (2) of Section 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero, for which the ILLE requests to be studied as a PCLR in Batch Zero in accordance with paragraph (1) of Section 9.2.2.1, Additional Information Required for Provisional Controllable Load Resources (PCLRs), the maximum Low Power Consumption in a given year shall be set as the peak Demand that may be served reliably for each year as determined according to paragraph (5) of Section 9.3.2, Batch Zero Interconnection Study Methodology. The Maximum Power Consumption (MPC) shall be set at the peak Demand modeled in accordance with paragraph (2) of Section 9.2.1.2.

### 9.3.2.2	Treatment of Withdrawal-Limited Private Use Networks (WLPUNs) in the Batch Zero Interconnection Study

(1)	Large Loads subject to assessment in accordance with paragraph (2) of Section 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero, for which the ILLE requests to be studied as a WLPUN in Batch Zero in accordance with paragraph (1) of Section 9.2.2.2, Additional Information Required for Withdrawal-Limited Private Use Networks (WLPUNs), will have the following treatment in the Batch Zero Interconnection Study:

(a)	ERCOT shall model the associated Large Load and generation such that the modeled generation does not inject real or reactive power into the ERCOT System.

(b)	ERCOT shall determine the MW Withdrawal limit for each year by turning off the WLPUN generation and determining the peak Demand that may be reliably served.

(c)	The MW Withdrawal limit shall not decrease from one year to the next within the Batch Zero Interconnection Study scope. If the MW Withdrawal limit determined for a given year is less than the amount determined for a prior year, ERCOT shall reduce the prior year’s MW Withdrawal limit to equal the lower amount.

(d)	The amount of peak Demand allocated to the Large Load each year will be the lesser of the following:

(i)	The requested peak Demand;

(ii)	The established MW Withdrawal limit plus the aggregate real power rating of the WLPUN generation; and

(iii)	90% of the load level that causes instability or cascading with all of the WLPUN generation off and with no contingency.

(e)	The allocated peak Demand shall not decrease from one year to the next within the Batch Zero Interconnection Study scope. If the allocated peak Demand determined for a given year is less than the amount allocated in a prior year, ERCOT shall reduce the prior year’s allocation to equal the lower amount.

## 9.4	Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment

(1)	On or before the date specified in paragraph (2)(b) of Section 9.3.1, Batch Zero Process Overview and Timelines, ERCOT will provide to all Interconnecting Distribution Service Providers (DSPs) and Interconnecting Transmission Service Providers (TSPs):

(a)	A report summarizing the results of the Batch Zero Interconnection Study and, for each proposed Transmission Facility improvement, identifying the affected TSP(s);

(b)	An updated Load Commissioning Plan (LCP) for each Large Load that was assessed in the Batch Zero Interconnection Study that reflects the allocated peak Demand for each year of the Batch Zero Interconnection Study scope; and

(c)	An estimate of the ILLE’s security requirements for each proposed Transmission Facility improvement attributable to the ILLE’s Large Load identified in the report described in paragraph (1)(a) above.  The estimate shall be determined in a manner consistent with P.U.C. Subst. R. 25.194.

(2)	In order to accept the allocated peak Demand and schedule documented in the LCP, the ILLE must execute an interconnection agreement that meets the requirements in P.U.C. Subst. R. 25.194.  This paragraph does not apply to a Large Load subject to assessment in accordance with Sections 9.2.1.1(2)(c)(ii)(A)(2) and 9.2.1.2(3).

(3)	If the executed interconnection agreement or, for a Large Load subject to assessment in accordance with Sections 9.2.1.1(2)(c)(ii)(A)(2) and 9.2.1.2(3), the existing interconnection agreement or equivalent agreement reflects allocated peak Demand that is lower than the values in the LCP provided under paragraph (1)(b), the Interconnecting TSP shall update the LCP to reflect the values memorialized in the interconnection agreement and provide the updated LCP to ERCOT within five Business Days.

(4)	The Interconnecting DSP or Interconnecting TSP must submit to ERCOT a notarized attestation confirming that the ILLE has executed the interconnection agreement on or before the date specified in paragraph (2)(c) of Section 9.3.1.

(5)	Any Large Load for which the Interconnecting DSP, Interconnecting TSP, or its designated representative has not provided the notarized attestation mandated in paragraph (4) above by the date specified in paragraph (2)(c) of Section 9.3.1 is considered to have withdrawn from the Batch Zero Process and shall not be included in the Batch Zero Refinement Study described in Section 9.5, Batch Zero Study Refinement and Delivery of Transmission Plan. These Large Loads shall not be eligible for Initial Energization unless included in a future batch study.

(6)	Nothing in this Section shall be construed to prohibit an ILLE from negotiating and preparing an interconnection agreement described in P.U.C. Subst. R. 25.194 prior to receipt of the Batch Zero Interconnection Study results as described in paragraph (1) above.

### 9.4.1	Additional Commitments for Provisional Controllable Load Resources (PCLRs)

(1)	In addition to the information set forth in paragraph (1) of Section 9.4, ERCOT shall provide the Interconnecting DSP or Interconnecting TSP for each Large Load studied as a PCLR in the Batch Zero Interconnection Study an updated copy of the ILLE’s Form W: Declaration of Intent and Commitment to Register as a Provisional Controllable Load Resource (PCLR). ERCOT shall complete the end date field in Part B to reflect the results of the study. The updated Form W must be provided by ERCOT to the Interconnecting DSP or Interconnecting TSP on or before the date specified in paragraph (2)(b) of Section 9.3.1.

(2)	In the updated Load Commissioning Plan (LCP) provided under paragraph (1)(b) of Section 9.4, ERCOT shall, for each Large Load studied as a PCLR in the Batch Zero Interconnection Study:

(a)	Set the maximum Low Power Consumption values for the PCLR to equal the amounts of peak Demand identified in the study; and

(b)	Identify the ILLE’s initial requested amounts of peak Demand as approved Maximum Power Consumption (MPC) values, contingent on successful registration as a PCLR.

(3)	The ILLE for a Large Load studied as a PCLR must complete, sign and have notarized Part B of Form W, indicating one of the following elections:

(a)	The ILLE affirms its intent to register as a PCLR and will accept the LPC and MPC values communicated in paragraph (2) above with no modifications;

(b)	The ILLE affirms its intent to register as a PCLR with modifications to the LPC and/or MPC values communicated in paragraph (2) above. These modified values must be less than or equal to the values communicated by ERCOT in paragraph (2) above and must be reflected in the updated LCP provided to ERCOT per paragraph (3) of Section 9.4;

(c)	The ILLE withdraws its intent to register as a PCLR but will accept the maximum LPC values communicated in paragraph (2) above as its allocated peak Demand with no modifications; or

(d)	The ILLE withdraws its intent to register as a PCLR but will accept the maximum LPC values communicated in paragraph (2) above as its allocated peak Demand with modifications. These modified values must be less than or equal to the values communicated by ERCOT in paragraph (2) above and must be reflected in the updated LCP provided to ERCOT per paragraph (3) of Section 9.2.4.

(4)	The Interconnecting DSP must provide the completed Form W to ERCOT on or before the date specified in paragraph (2)(c) of Section 9.3.1.

(5)	For a Large Load studied as a PCLR, if ERCOT does not receive the signed and notarized Form W Part B that conforms with one of the elections specified in paragraph (3) above by the date specified in paragraph (2)(c) of Section 9.3.1, ERCOT will exclude that Large Load from the Batch Zero Refinement Study described in Section 9.5. That Large Load will not be eligible for Initial Energization unless it completes a future study for Large Load interconnection that meets the applicable study requirements defined in the ERCOT Planning Guide.

### 9.4.2	Additional Commitments for Withdrawal-Limited Private Use Networks (WLPUNs)

(1)	In addition to the information set forth in paragraph (1) of Section 9.4, for each Large Load studied as a Withdrawal-Limited Private Use Network (WLPUN) in the Batch Zero Interconnection Study, ERCOT shall provide an LCP that includes both the established MW Withdrawal limit and the allocated peak Demand for each year of the Batch Zero Interconnection Study scope to the Interconnecting DSP, if applicable, and Interconnecting TSP.

(2)	In order to accept the established MW Withdrawal limit and allocated peak Demand and schedule documented in the LCP, the ILLE must execute an interconnection agreement that meets the requirements in P.U.C. Subst. R. 25.194. In the event the executed interconnection agreement reflects modifications to the established MW Withdrawal limit or  allocated peak Demand that are lower than the values determined in paragraph (1) above, the Interconnecting DSP or Interconnecting TSP shall update the LCP to reflect the values memorialized in the interconnection agreement.

(3)	The Interconnecting DSP or Interconnecting TSP must submit to ERCOT a notarized attestation confirming that the ILLE has executed the interconnection agreement on or before the date specified in paragraph (2)(c) of Section 9.3.1.

(4)	The generation associated with a Large Load studied as a WLPUN must meet the requirements specified in paragraph (1) of Section 6.9, Addition of Proposed Generation to the Planning Models, for ERCOT’s inclusion of the applicable generation in the base cases created and maintained by the Steady State Working Group (SSWG) by the date specified in paragraph (2)(c) of Section 9.3.1.

(5)	Any Large Load for which the associated generation meets any of the following criteria is considered to have withdrawn from the Batch Zero Process and shall not be included in the Batch Zero Refinement Study described in Section 9.5, Batch Zero Study Refinement and Delivery of Transmission Plan. These Large Loads shall not be eligible for Initial Energization unless included in a future batch study.

(a)	The associated generation does not meet the requirements in paragraph (4) above.

(b)	After July 24, 2026, the aggregate real power rating of the associated generation decreases from what was recorded in RIOO.

(c)	After July 24, 2026, the technology type(s) of the associated generation changes from what was recorded in RIOO.

(6)	An ILLE for a Large Load studied as a WLPUN may elect one of the following:

(a)	The ILLE accepts the established MW Withdrawal limit and allocated peak Demand provided in paragraph (1) above with no modifications; or

(b)	The ILLE accepts a modified MW Withdrawal limit or peak Demand from what was provided in paragraph (1) above. Each modified value must be less than or equal to the corresponding value provided by ERCOT in paragraph (1) above and must be reflected in an updated LCP.

(7)	The established MW Withdrawal limit and allocated peak Demand determined in Section 9.3.2.2, each as adjusted by any election under paragraph (6) above, are final upon the ILLE’s execution of the interconnection agreement under paragraph (2) above.  The Resource Entity shall ensure the established MW Withdrawal limit is recorded in the Resource Registration data pursuant to Protocol Section 3.10.7.3.1, Withdrawal-Limited Private Use Networks. The Interconnecting TSP shall document the allocated peak Demand in the Load Commissioning Plan.

## 9.5	Batch Zero Study Refinement and Delivery of Transmission Plan

(1)	The Batch Zero Refinement is an activity performed by ERCOT, in consultation with the Interconnecting DSPs and Interconnecting TSPs, to update the Batch Zero Interconnection Study performed per Section 9.3, Batch Zero Interconnection Study, to only include Large Loads that met the commitment requirements per Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment. The goal of the Batch Zero Refinement Study is to determine which Transmission Facility improvements identified in the Batch Zero Interconnection Study are still needed, needed with modifications, or are no longer needed.

9.5.1	ERCOT Activities During the Batch Zero Refinement Period

(1)	After the deadline established in paragraph (2)(c) of Section 9.3.1, Batch Zero Process Overview and Timelines, for the Interconnecting Distribution Service Provider (DSP) or Interconnecting Transmission Service Provider (TSP) to notify ERCOT which Large Loads included in the initial Batch Zero Interconnection Study have met the requirements for commitment, ERCOT will initiate the Batch Zero Refinement Study.

(2)	During the Batch Zero Refinement Study period ERCOT shall update its Batch Zero Interconnection Study to evaluate if the remaining Large Loads under assessment still result in planning criteria violations and if the Transmission Facility improvements for 2028, 2030, and 2032 identified in the Batch Zero Interconnection Study require modification.

(3)	ERCOT shall communicate with applicable Interconnecting DSPs and Interconnecting TSPs during ERCOT’s evaluation. Each Interconnecting DSP and Interconnecting TSP shall promptly respond to all communications and provide recommendations to ERCOT as soon as practicable. Each Interconnecting DSP and Interconnecting TSP shall provide any Transmission Facility improvement cost estimates within 15 Business Days of ERCOT’s request.

(4)	ERCOT shall prepare a final report for the Batch Zero Refinement Study described in this Section. For each recommended Transmission Facility improvement, the final report shall include a description of the need for the improvement, cost estimates, the affected TSP, and any alternate improvements formally considered by ERCOT.

(5)	ERCOT shall submit the final report for RPG Project Review by the date specified in paragraph (2)(d) of Section 9.3.1 unless the set of Transmission Facility improvements are classified as a Tier 4 project according to Nodal Protocol Section 3.11.4.3. This final report shall serve as ERCOT’s independent review in accordance with Protocol Section 3.11.4.6 or Protocol Section 3.11.4.7, unless ERCOT decides to create an updated final report based on comments received during the RPG Project Review.

(6)	The Batch Zero Refinement Study described in this section shall not include an adjustment to the allocated peak Demand, the maximum allowed Low Power Consumption (LPC) values for any Large Load studied as a Provisional Controllable Load Resource (PCLR), the established MW Withdrawal limit and allocated peak Demand for any Large Load studied as a Withdrawal-Limited Private Use Network (WLPUN), financial security, or cost obligations for any Large Loads included in the Batch Zero Interconnection Study for which the Large Load has met the commitment requirements per Section 9.4.

9.5.2	System Protection (Short-Circuit) Analysis

(1)	The Interconnecting TSP shall perform a short-circuit analysis during the Batch Zero Refinement Study period.

(2)	The short-circuit study shall use the ERCOT base cases posted per paragraph (3) of Section 9.3.2, Batch Zero Interconnection Study Methodology, appropriate for the desired Initial Energization date and Load Commissioning Plan of the Load.

(3)	The Interconnecting TSP will determine the maximum available fault currents at the interconnection substation and for the facilities impacted by the proposed transmission additions, to determine the required facility ratings and any additional necessary transmission upgrades that were not already identified in the initial Batch Zero Interconnection Study report.

(4)	The Interconnecting TSP must provide the short-circuit study report to ERCOT on or before the date prescribed in paragraph (3) of Section 9.3.1, Batch Zero Process Overview and Timelines.

### 9.5.3	Treatment of Provisional Controllable Load Resources (PCLRs) in the Batch Zero Refinement Study

(1)	ERCOT shall evaluate Large Loads meeting the commitment requirements for Provisional Controllable Load Resources (PCLRs) defined in Section 9.4.1, Additional Commitments for Provisional Controllable Load Resources (PCLRs), in the same manner as other Large Loads included in the Batch Zero Refinement Study. The Demand level for a PCLR shall be set at the LPC as reflected in the updated Load Commissioning Plan (LCP) and interconnection agreement that meets the commitment requirements in Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment.

### 9.5.4	Treatment of Withdrawal-Limited Private Use Networks (WLPUNs) in the Batch Zero Refinement Study

(1)	For Withdrawal-Limited Private Use Networks (WLPUNs) meeting the commitment requirements defined in Sections 9.4 and 9.4.2, ERCOT shall model both the associated Large Load and the generation in the Batch Zero Refinement Study. For the purposes of this study, the modeled generation dispatch will not be capped as described in paragraph (1)(a) of Section 9.3.2.2, and the WLPUN may inject power to the ERCOT System depending on the parameters of the Large Load and associated generation.

## 9.6	Initial Energization and Continuing Operations for Large Loads

(1)	Each Large Load shall meet the conditions established by ERCOT before proceeding to Initial Energization. These conditions may include, but are not limited to:

(a)	Inclusion of the Load in the Network Operations Model in accordance with Section 6.6, Modeling of Large Loads;

(b)	Verification that all required telemetry is operational and accurate;

(c)	Completion of the requirements of Section 5.3.5, ERCOT Quarterly Stability Assessment;

(d)	Completion and approval of any required Subsynchronous Oscillation (SSO) studies, SSO Mitigation plan, SSO Countermeasures, and SSO monitoring, if required; and

(e)	Submission of a current Load Commissioning Plan (LCP) meeting the requirements of Section 9.2.4, Load Commissioning Plan.

(2)	During continuing operations:

(a)	The Interconnecting DSP, Interconnecting TSP, or, if applicable, the Resource Entity shall notify ERCOT if it identifies that a Large Load has exceeded a limit on peak Demand established in the LCP.

(b)	Pursuant to Section 9.2.3, Modification of Large Load Information, if an ILLE modifies its facilities such that a previously provided dynamic load model is invalid, the ILLE shall notify and provide an updated model to the Interconnecting Distribution Service Provider (DSP) and Interconnecting Transmission Service Provider (TSP) that provides service to the Large Load. The Interconnecting DSP or Interconnecting TSP shall subsequently provide this updated dynamic load model to ERCOT.

### 9.6.1	Additional Energization and Operation Requirements for Provisional Controllable Load Resources (PCLRs)

(1)	A Large Load that has not yet met the requirements to qualify as a Provisional Controllable Load Resource (PCLR) will be granted Initial Energization upon meeting the requirements of paragraph (1) of Section 9.6 and receiving written approval to energize from ERCOT. The Large Load shall not consume at a level greater than the maximum Low Power Consumption (LPC) amount documented in the updated Load Commissioning Plan (LCP) attested to by the ILLE per paragraph (4) of Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment.

(2)	A Large Load designated as a PCLR that has been granted Initial Energization per paragraph (1) above shall not consume above its LPC amount until:

(a)	The ILLE registers with ERCOT as a Resource Entity and designates a Qualified Scheduling Entity (QSE);

(b)	The ILLE provides all required data in the ERCOT Resource Integration and Ongoing Operations (RIOO) system and the PCLR is added to the ERCOT Network Operations Model;

(c)	The ILLE provides all required telemetry to ERCOT and the telemetry is of good quality;

(d)	The ILLE successfully completes all qualification testing required by ERCOT; and

(e)	ERCOT provides the ILLE’s QSE written confirmation that the requirements are complete.

(3)	During qualification tests required in paragraph (2)(d) above, ERCOT may permit the PCLR to operate above the LPC limit if required to facilitate the test.

### 9.6.2	Additional Energization and Operation Requirements for Withdrawal-Limited Private Use Networks (WLPUNs)

(1)	A Large Load in a Withdrawal-Limited Private Use Network (WLPUN) will be granted Initial Energization upon meeting the requirements of paragraph (1) of Section 9.6 and receiving written approval to energize from ERCOT. The Large Load shall not consume at a level of gross Demand that causes the net Demand at the Point of Interconnection (POI) to exceed the established MW Withdrawal limit.

(2)	A Large Load within a WLPUN may increase its Demand behind the Point of Interconnection (POI) commensurate with the output of the generation so long as the total consumption at the POI does not exceed the established MW Withdrawal limit only after the following conditions have been met:

(a)	The associated generation has completed the commissioning process in accordance with paragraph (1) of Planning Guide Section 5.5;

(b)	All required telemetry for each Large Load is operational and of good quality;

(c)	The established MW Withdrawal limit has been recorded in the Resource Registration data and incorporated in the ERCOT Network Operations Model pursuant to Section 3.10.7.3.1; and

(d)	ERCOT provides the Resource Entity with written confirmation that the requirements of this paragraph have been met.

## 9.7	Required Disclosures

(1)

The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP whether the ILLE is pursuing a substantially similar interconnection request for electric service in Texas, the approval of which would result in the ILLE materially changing, delaying, or withdrawing the interconnection request. The disclosure must be accompanied by a notarized attestation from the ILLE stating that the information contained in the submission is complete and accurate at the time the notarized attestation is signed. A material change or delay includes a delay of one or more years to the Large Load’s projected date to realize its requested or contracted peak Demand, a 20% or greater change in the requested or contracted peak Demand, or a change in the location for the point of interconnection.

(a)	An ILLE that is pursuing a substantially similar interconnection request for electric service the approval of which would result in the ILLE materially changing, delaying, or withdrawing the interconnection request must disclose the following information to the Interconnecting DSP or the Interconnecting TSP:

(i)	The ERCOT-assigned serial number (i.e., the Large Load interconnection number) for the substantially similar interconnection request, as applicable;

(ii)	The location, including the power region and, if in the ERCOT region, the load zone, of the substantially similar interconnection request;

(iii)	The non-coincident peak Demand of the substantially similar interconnection request;

(iv)	The anticipated timing of energization of the substantially similar interconnection request; and

(v)	The Interconnecting DSP and, if different from the Interconnecting DSP, the Interconnecting TSP associated with the substantially similar interconnection request.

(b)	An ILLE that discloses a substantially similar interconnection request under this subsection may anonymize competitively sensitive information in its disclosure to the Interconnecting DSP or the Interconnecting TSP.

(c) 	An Interconnecting DSP and an Interconnecting TSP must not sell, share, or disclose information submitted to the Interconnecting DSP or the Interconnecting TSP under this subsection other than a disclosure to the Public Utility Commission of Texas (PUCT) or ERCOT.

(d)	ERCOT may request and the ILLE must provide any competitively sensitive information ERCOT deems necessary to complete any analysis required as part of the interconnection process. ERCOT must treat disclosed competitively sensitive information as Protected Information under ERCOT Protocols.

(2)	The ILLE must submit to the Interconnecting DSP or the Interconnecting TSP the ILLE’s plans, expected timing, and progress for site-related studies and engineering services required for Large Load development before energization (e.g., geotechnical survey, water, wastewater, or gas). The submission must be accompanied by a notarized attestation from the ILLE stating that the information contained in the submission is complete and accurate at the time the attestation is signed. The ILLE must provide updates or progress reports to the Interconnecting DSP or the Interconnecting TSP when requested, but no more frequently than quarterly.

(3)	The ILLE must submit to the Interconnecting DSP or the Interconnecting TSP the ILLE’s plans, expected timing, and current progress for obtaining non-ministerial discretionary approvals from state and local regulatory authorities required for development before energization (e.g., water, air, or backup generation permits). The submission must be accompanied by a notarized attestation from the ILLE attesting that the information contained in the submission is complete and accurate at the time the attestation is signed. The ILLE must provide updates or progress reports to the Interconnecting DSP or the Interconnecting TSP when requested, but no more frequently than quarterly.

(4)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP the expected schedule, including the quarter and year, for phased energization of the requested or contracted peak demand expressed in MW, power factor (PF), and megavolt ampere reactive (MVAr) units. The schedule must be consistent with any current Load Commissioning Plan (LCP).

(5)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP whether the ILLE plans to have on-site backup generating facilities. If the ILLE plans to have on-site backup generating facilities, the ILLE must also disclose, to the extent known, the following information:

(a)	The number of backup generating units;

(b)	The nameplate capacity of each of the backup generating facilities;

(c)	The fuel source and operational characteristics of each of the backup generating facilities, including any run hour limitations and any fuel storage limitations under the existing environmental permits; and

(d)	How quickly each of the backup generating facilities can reach their full capacity to serve the Load.

(6)	The ILLE must disclose how it plans to procure power and whether the ILLE has on-site generation that will provide power to the ILLE.

## 9.8	Legacy Interconnection Study Procedures for Large Loads

(1)	This Section, previously known as Section 9.3, outlines the former procedures for conducting a Large Load Interconnection Study (LLIS) for new or modified Large Loads.  It has been replaced by the Batch Zero Process but has been retained here for reference.

### 9.8.1	Legacy Large Load Interconnection Study (LLIS)

(1)	A LLIS consists of the set of steady-state, stability, short-circuit and other relevant studies that are necessary to determine the reliability impact of a Large Load interconnection on affected Transmission Facilities and identify the Transmission Facilities that are needed to reliably interconnect the new or modified Large Load to the ERCOT System.

(2)	If an Interconnecting Entity (IE) or Resource Entity submits a large Generation Resource interconnection request, as defined in Section 5.3, Interconnection Study Procedures for Large Generators, that also includes a co-located Large Load, the Full Interconnection Study (FIS) may be used in place of a separate LLIS.  The FIS shall reflect the full requested Load amount and conform to all study requirements detailed in Sections 5.3 and 9.8, Legacy Interconnection Study Procedures for Large Loads.  For any deadlines or timelines set out in this section that conflict with the deadlines or timelines in Sections 5.2, General Provisions, and 5.3, the deadlines or timelines in Sections 5.2 and 5.3 shall govern.

(3)	During the LLIS, the interconnecting Transmission Service Provider (TSP) shall be the lead TSP unless otherwise designated by ERCOT during the study scoping process detailed in Section 9.8.2, Legacy Large Load Interconnection Study Scoping Process.

(4)	For an interconnection request involving a Large Load interconnecting at distribution voltage, the LLIS shall evaluate only the proposed Load’s transmission-level impacts, if any.  The affected Distribution Service Provider (DSP) shall provide the lead TSP with all information concerning the DSP’s facilities needed to complete any required studies.

### 9.8.2	Legacy Large Load Interconnection Study Scoping Process

(1)	ERCOT will notify the interconnecting TSP after all requirements have been met.  Within ten Business Days of this notification, the lead TSP shall schedule a kick-off meeting with ERCOT and the certificated DSP to occur soon thereafter. If the proposed project is co-located with a Generation Resource, the kick-off meeting must also include the affected Resource Entity or IE.  The lead TSP shall invite the Interconnecting Large Load Entity (ILLE) to attend the kick-off meeting.  The ILLE may attend at its option.

(2)	ERCOT will notify all other TSPs of the LLIS request.  Each TSP may evaluate if it is directly affected by the interconnection request and determine if it should participate in the LLIS.  Examples of a directly affected TSP may include, but are not limited to, a TSP whose facilities are likely to experience changes in voltage or power flow because of the Load interconnection request.

(3)	Each directly affected TSP desiring to participate in the LLIS shall promptly notify the lead TSP and ERCOT and must provide a description of the expected effect of the Load interconnection on the TSP’s facilities in its notification.  The lead TSP shall include all directly affected TSP(s) in the LLIS kickoff meeting.

(4)	At the LLIS kickoff meeting, the lead TSP will present the proposed project and facilitate a general discussion of the preliminary study scope of work for the LLIS.

(5)	Any reactive studies required under Protocol Section 3.15, Voltage Support, or Subsynchronous Oscillation (SSO) studies required under Protocol Section 3.22.1.4, Large Load Interconnection Assessment, shall be scoped simultaneously with the LLIS but do not need to be included as part of the LLIS.  The Resource Entity responsible for the reactive study shall provide it to ERCOT directly.

(6)	The lead TSP will develop a preliminary LLIS study scope within ten Business Days following the kickoff meeting.

(a)	The study scope must include all study elements required by Section 9.8.4, Legacy Large Load Interconnection Study Elements, unless ERCOT in collaboration with the TSP(s) determine that one or more studies are unnecessary.  If a study element is deemed unnecessary, the lead TSP shall provide a written technical justification for not performing the analysis in lieu of the study report.

(b)	The study scope shall specify the base cases, study assumptions, and scenarios that will be used in each LLIS element.  Any transmission facilities that will not be in service before Initial Energization of the proposed Load that may significantly impact the study results, as initially identified by the lead TSP during the project kickoff meeting, shall be documented in the study scope.  All study assumptions related to maintenance outage scenarios required under Section 4.1.1.8, Maintenance Outage Reliability Criteria, shall be explicitly identified in the study scope.

(c)	The study scope shall specify the involvement of any directly affected TSPs in the study process.  In some cases, it may be necessary for the ILLE to execute study agreements with multiple TSP(s).

(d)	The lead TSP may propose interconnection design alternatives during the scoping process.  Such alternative options shall be fully studied in all required LLIS study elements.

(7)	The lead TSP shall submit the preliminary study scope for review by ERCOT and all directly affected TSPs, including TSPs which may be directly affected due to proposed interconnection topology. Directly affected TSPs and ERCOT may provide comments on the preliminary study scope within ten Business Days of posting.

(8)	Upon closing of the comment period described in paragraph (7) above, the lead TSP shall, within ten Business Days, submit a final study scope that addresses submitted comments to the extent possible.  ERCOT in collaboration with the TSP(s) shall determine the study scope.

(9)	Within five Business Days of the lead TSP submitting the final study scope, ERCOT shall approve the final study scope or return the scope to the lead TSP with comments.  The lead TSP shall promptly address ERCOT comments and resubmit according to paragraph (8) above.

### 9.8.3	Legacy Large Load Interconnection Study Description and Methodology

(1)	The primary purpose of the LLIS is to determine whether the amount of Load being requested by the ILLE can be placed in service by the desired Initial Energization date while maintaining the reliability of the ERCOT System and ensuring compliance with all North American Electric Reliability Corporation (NERC) Reliability Standards, Protocols, this Planning Guide, and the Operating Guides.  The LLIS will also identify any transmission improvements needed to serve the full requested Load amount, including individual load increments requested by the ILLE in the initial Load Commissioning Plan (LCP).

(2)	The LLIS consists of a series of distinct study elements.  The specific elements included in a particular LLIS will be stated in the LLIS scope.

(3)	Each proposed Large Load interconnection that requests more than one physical transmission interconnection will be studied as an individual study for each interconnection to be analyzed separately from all other such requests unless otherwise agreed by the TSP(s) in the interconnection study agreement.

(4)	The LLIS process includes developing and analyzing various computer model simulations of the existing and proposed ERCOT transmission system.  The results from these simulations will be utilized by the TSP(s) to determine the impact of the proposed interconnection.

(5)	The study shall include an analysis demonstrating the adequate reliability of any temporary interconnection configurations.

9.8.4	Legacy Large Load Interconnection Study Elements

### 9.8.4.1	Legacy Steady-State Analysis

(1)	The steady-state interconnection study base case shall be created from the most recently approved Steady State Working Group (SSWG) base case appropriate for the desired Initial Energization date of the Load.  The lead TSP shall remove from the study base case all Transmission Facilities it determines may significantly impact study results that will not be in service before Initial Energization of the proposed Load, as identified in the preliminary LLIS study scope.  The steady-state analysis shall include other relevant Large Loads and any transmission upgrades included in the LCPs for those Large Loads that have a complete LLIS per paragraph (7) of Section 9.9, Legacy LLIS Report and Follow-up, and that have met the requirements of Section 9.10, Legacy Interconnection Agreements and Responsibilities.  The lead TSP may include other transmission projects and Substantiated Load in the study base case.  All modifications to the SSWG base case made as part of the study assumptions shall be documented in the LLIS report.

(2)	The lead TSP shall perform contingency analyses as required by the NERC Reliability Standards, ERCOT Nodal Protocols, this Planning Guide, and the Operating Guides to identify any additional Facilities that may be necessary to ensure that results of the system performance conform to these standards.  The study shall identify any system limitations that would prevent the ILLE from achieving the requested load in the desired timeframe.  If the study identifies system limitations, the lead TSP shall identify potential transmission system improvements necessary to achieve the requested Load.  The results of this analysis shall be shared with TSP(s) that have Facilities identified with planning criteria violations, and those affected TSP(s) will be responsible for evaluating the impact of the Large Load and the validity of the anticipated violations.

(3)	Upon completion of the steady-state study as described in paragraph (2) above, the lead TSP shall identify any modifications to the levels of Demand and timeline specified in the ILLE’s initial LCP that are needed to account for all transmission upgrades required to support the full requested amount of Load.

### 9.8.4.2	Legacy System Protection (Short-Circuit) Analysis

(1)	The short-circuit study shall use the most recently approved System Protection Working Group (SPWG) base case appropriate for the desired Initial Energization date of the Load.  The initial transmission configuration of the study area shall correspond to the configuration used in the corresponding steady-state study to the extent practicable.

(2)	The lead TSP will determine the maximum available fault currents at the interconnection substation for determining switching device interrupting capabilities and protective relay settings.

### 9.8.4.3	Legacy Dynamic and Transient Stability Analysis

(1)	The lead TSP shall not initiate the stability study prior to receiving from the ILLE dynamic load modeling information sufficient to properly model the load in the stability studies.  The TSP shall check the dynamic load information according to the procedure specified in Section 3.4.4, Load Model Data, of the Dynamics Working Group Procedure Manual.

(2)	The stability study base case shall be created from the most recently approved Dynamics Working Group (DWG) base case appropriate for the desired Initial Energization date of the Load.  The initial transmission configuration of the study area shall be consistent with the configuration used in the corresponding steady-state study to the extent practicable.

(3)	All stability studies shall be performed in accordance with NERC Reliability Standards, Protocols, this Planning Guide, and the Operating Guides.  Transient stability studies will analyze the performance of the ERCOT System in terms of angular stability, voltage stability, and excessive frequency excursions.  Additional studies may include small signal stability or critical clearing time analyses.  Such studies should incorporate reasonable and conservative assumptions regarding impacted facility operating conditions.  ERCOT in collaboration with the TSP(s) shall determine the stability analysis to be performed.

(4)	The stability study portion of the LLIS shall document any identified instability.

(5)	If the lead TSP identifies instability (other than instability identified for extreme events) in the stability portion of the LLIS, the TSP shall investigate alternative solutions, including transmission improvements, to mitigate the instability.  The lead TSP shall identify any modifications to the levels of Demand and the timeline specified in the ILLE’s initial LCP that are needed to account for all transmission upgrades required to support the full requested amount of Load.  The TSP shall implement any mitigation measure that may be needed to address a stability risk before the Initial Energization of the Large Load in accordance with Protocol Section 3.11.4, Regional Planning Group Project Review Process.

## 9.9	Legacy LLIS Report and Follow-up

(1)	This Section, previously known as Section 9.4, outlines the former procedures for informing an Interconnecting Large Load Entity (ILLE) the results of its Large Load Interconnection Study (LLIS).  It has been replaced by the Batch Zero Process but has been retained here for reference.

(2)	For each of the LLIS study elements, the lead Transmission Service Provider (TSP) shall submit a preliminary study report to ERCOT and other directly affected TSPs.  The report shall include a description of the study methodology and assumptions, findings, and recommendations.  The report shall also identify any changes to the Interconnecting ILLE’s Load Commissioning Plan (LCP) to allow for transmission upgrades in accordance with the criteria in Section 9.8.4, Legacy Large Load Interconnection Study Elements.  The lead TSP may include additional information in the study report and may combine multiple LLIS study elements into a single report.

(3)	ERCOT shall review the preliminary study report within ten Business Days and provide to the lead TSP any questions, comments, and proposed revisions necessary to ensure the report complies with the requirements in Section 9.8, Legacy Interconnection Study Procedures for Large Loads.  ERCOT may extend this review period by an additional 20 Business Days and shall notify in writing the lead and directly affected TSPs of the extension.  Directly affected TSPs may also provide questions, comments, and proposed revisions during this review period.  All comments from ERCOT and directly affected TSPs shall be provided to the lead TSP in writing.

(4)	If, after considering the responses received from ERCOT and directly affected TSPs, ERCOT in collaboration with the lead TSP determines if an additional study is required, the lead TSP shall promptly perform the additional study and submit an updated preliminary study report for review as described in paragraph (2) above.

(5)	If no additional study is required as described in paragraph (4) above, the lead TSP shall prepare a final LLIS study report that incorporates all relevant feedback received in paragraph (2) above within ten Business Days.

(6)	When complete, the lead TSP shall provide the final report for the LLIS study element(s) to ERCOT and the directly affected TSPs only.

(7)	The LLIS is deemed complete when the final report has been provided for all LLIS study elements.  Within ten Business Days following the completion of the LLIS, ERCOT shall:

(a)	Determine whether system upgrades recommended to support the full requested Load amount specified in the initial LCP are sufficient based on the report in paragraph (6) above;

(b)	Grant conditional approval for the interconnection of Load in accordance with the schedule in the final LCP, as may be revised by the TSP, as the necessary transmission upgrades identified in the LCP become operational, if ERCOT has determined pursuant to paragraph (a) above that the system upgrades recommended in the LLIS are sufficient to address the reliability risks associated with the proposed load additions;

(i)	For transmission upgrades that are subject to Regional Planning Group (RPG) review as described in Protocol Section 3.11.4, Regional Planning Group Project Review Process, ERCOT shall grant conditional approval if it determines that a project with an equivalent impact on the ability to serve the requested Load has become operational; and

(c)	Communicate the completion of the LLIS and the resulting LCP to the lead TSP and directly affected TSPs.

(8)	The lead TSP may provide a redacted copy of the final report for each LLIS study element to the ILLE upon request.  The redacted report(s) shall conform with Protocol Section 1.3, Confidentiality.

(9)	If a material change that impacts one or more LLIS study assumptions occurs before the requirements of Section 9.10, Legacy Interconnection Agreements and Responsibilities, have been met, ERCOT or the lead TSP may require one or more LLIS study elements be updated.  ERCOT in collaboration with the lead TSP shall have discretion to determine if a change impacts any LLIS study assumptions and to require a modification of the study or a restudy be performed.  Any modification of the study report shall be treated as a preliminary study and reviewed according to paragraph (2) above.

(10)	If the requirements of Section 9.10, have not been satisfied within 180 days after the communication of the completion of the LLIS by ERCOT as described in paragraph (7) above, ERCOT may notify the lead TSP that the project is subject to cancellation.  Upon receipt of this notification, the lead TSP may submit a project status update to ERCOT that includes a request for an extension and provides an opinion on whether any of the completed LLIS elements require restudy.  If no such project status update is received within 30 days from the date the notice is issued, ERCOT may consider the project canceled.

(11)	If the Large Load has not met the requirements for Initial Energization as described in paragraph (1) of Section 9.6, Initial Energization and Continuing Operations for Large Loads, within 365 days after the Initial Energization date identified in the LLIS study report, the lead TSP shall provide an opinion to ERCOT on whether any of the completed LLIS elements require restudy.  ERCOT may require one or more LLIS study elements be updated prior to approval of Initial Energization.

## 9.10	Legacy Interconnection Agreements and Responsibilities

(1)	This Section, previously known as Section 9.5, outlines the former requirements an Interconnecting Large Load Entity must meet prior to Initial Energization.  It has been replaced by the Batch Zero Process but has been retained here for reference.

9.10.1	Legacy Interconnection Agreement for Large Loads not Co-Located with a Generation Resource Facility

(1)	For a Large Load not co-located with a Generation Resource Facility, ERCOT shall not allow Initial Energization prior to receiving one of the following:

(a)	Confirmation from the interconnecting Transmission Service Provider (TSP) that:

(i)	All required interconnection agreements or equivalent service extension agreements with the Interconnecting Large Load Entity (ILLE) and, if applicable, directly affected TSP(s) have been executed;

(ii)	The interconnecting TSP has received written acknowledgement from the ILLE of the ILLE’s obligations to:

(A)	Notify the interconnecting TSP of changes to the Large Load project information or to the load composition, technology, or parameters, as described in Section 9.2.3, Modification of Large Load Information; and

(B)	Maintain Load consumption at or below the level(s) of peak Demand established in the Load Commissioning Plan (LCP);

(iii)	The interconnecting TSP has received notice to proceed with the construction of all required interconnection Facilities; and

(iv)	The interconnecting TSP and, if applicable, directly affected TSP(s) have received the financial security, applicable payments, and/or other agreements required to fund all required interconnection Facilities; or

(b)	A letter from a duly authorized person from a Municipally Owned Utility (MOU) or Electric Cooperative (EC) confirming its intent to construct and operate applicable Large Load and interconnect such Large Load to its transmission system.

9.10.2	Legacy Interconnection Agreement for Large Loads Co-Located with One or More Generation Resource Facilities

(1)	For a Large Load co-located with a Generation Resource Facility, ERCOT shall not allow Initial Energization prior to receiving one of the following:

(a)	Confirmation from the interconnecting TSP that:

(i)	All required interconnection agreements and/or equivalent service extension or other agreements with the Resource Entity, Interconnecting Entity (IE), and ILLE have been executed;

(A)	If the required agreements include a new Standard Generation Interconnection Agreement (SGIA) or an amendment to an existing SGIA, a copy of this agreement shall be provided to ERCOT once executed, per Section 5.2.8.1, Standard Generation Interconnection Agreement for Transmission-Connected Generators; or

(B)	If no new or amended agreements are required, the interconnecting TSP shall so notify ERCOT and state affirmatively it agrees to energize the new Load per the approved LLIS studies;

(ii)	The interconnecting TSP has received written acknowledgement from either the ILLE, or the Resource Entity on behalf of the ILLE, of the obligations to:

(A)	Notify the interconnecting TSP of changes to the Large Load project information or to the load composition, technology, or parameters, as described in Section 9.2.3, Modification of Large Load Information; and

(B)	Maintain Load consumption at or below the level(s) of peak Demand established in the LCP; and

(iii)	The interconnecting TSP has received notice to proceed with the construction of all required interconnection Facilities; and

(iv)	The interconnecting TSP and, if applicable, directly affected TSP(s) have received the financial security required, applicable payments, and/or other agreements to fund all required interconnection Facilities; or

(b)	A letter from a duly authorized person from a MOU or EC confirming its intent to construct and operate applicable Large Load and interconnect such Large Load to its transmission system.