| PGRR Number | 133 | PGRR Title | Clarifying Legacy Generation Breaker Control for PGRR115 Implementation |
| --- | --- | --- | --- |
| Date of Decision |  | June 2, 2026 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Urgent – to correct grey-boxed language prior to implementation of Planning Guide Revision Request (PGRR) 115, Related to NPRR1234, Interconnection Requirements for Large Loads and Modeling Standards for Loads 25 MW or Greater. |  |
| Estimated Impacts |  | Cost/Budgetary: None Project Duration: No project required |  |
| Proposed Effective Date |  | Upon system implementation of Nodal Protocol Revision Request (NPRR) 1234, Interconnection Requirements for Large Loads and Modeling Standards for Loads 25 MW or Greater |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Planning Guide Sections Requiring Revision |  | 5.2.11, Required Interconnection Equipment |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This PGRR corrects for unintentional operational risk in grey-boxed language adopted in PGRR115. |  |
| Reason for Revision |  | Strategic Plan Objective 1 – Be an industry leader for grid reliability and resilience Strategic Plan Objective 2 - Enhance the ERCOT region’s economic competitiveness with respect to trends in wholesale power rates and retail electricity prices to consumers Strategic Plan Objective 3 - Advance ERCOT, Inc. as an independent leading industry expert and an employer of choice by fostering innovation, investing in our people, and emphasizing the importance of our mission General system and/or process improvement(s) Regulatory requirements ERCOT Board/PUCT Directive (please select ONLY ONE – if more than one apply, please select the ONE that is most relevant) |  |
| Justification of Reason for Revision and Market Impacts |  | PGRR115 included one change unrelated to the interconnection of Large Loads – specifically, a revision to Section 5, Generator Interconnection or Modification, adding grey-boxed Section 5.2.11 that specifies that fault-protective breakers “be under the remote control of the applicable Transmission Operator (TO) and capable of being operated remotely to comply with an instruction from ERCOT.” The remote operation of generator breakers by a third party presents significant operational concerns for operators of power plants that were built prior to unbundling, where the determination of which breakers are at “each Point of Interconnection (POI)” may not be self-evident. It is not typical for TOs to control generation breakers, and that concern is particularly heightened for nuclear power plants, where remote operation of generator breakers by a third party (including a TO) could represent a security risk. The generator breakers must be under the control of the reactor operator. Accordingly, to avoid a potential unintended consequence of the phrasing of new Section 5.2.11, an additional paragraph (2) in Section 5.2.11 allows existing generators with a Resource Commissioning Date on or before December 31, 2025 to maintain their current configuration. These units would need to come into compliance with the new requirements in the event a modification changing or adding a POI to the facility (as described in paragraph (1)(c)(iv) of Section 5.2.1, Applicability) is made or if the Resource adds a co-located load bringing the total load to 75MW or greater. |  |
| ROS Decision |  | On 11/6/25, ROS voted to grant PGRR133 Urgent status. There was one opposing vote from the Independent Generator (Southern Power) Market Segment and one abstention from the Independent Generator (EDF Power Solutions) Market Segment. ROS then voted unanimously to table PGRR133. All Market Segments participated in both votes. On 4/2/26, ROS voted unanimously to recommend approval of PGRR133 as amended by the 1/28/26 Joint Commenters comments and to forward PGRR133 to TAC. All Market Segments participated in the vote. |  |
| Summary of ROS Discussion |  | On 11/6/25, the sponsor provided an overview of PGRR133 and the request for urgency. ERCOT Staff presented the 11/5/25 ERCOT comments. Participants discussed the appropriateness of remote control of breakers for facilities, particularly nuclear locations, and requested additional time to review the implications of PGRR133 and the unboxing of PGRR115. ERCOT Staff noted their willingness to delay the unboxing of 5.2.11 to allow time for additional discussions. On 4/2/26, participants reviewed the 1/28/26 Joint Commenters comments. |  |
| TAC Decision |  | On 4/29/26, TAC voted unanimously to recommend approval of PGRR133 as recommended by ROS in the 4/2/26 ROS Report; and the 4/22/26 Impact Analysis. All Market Segments participated in the vote. |  |
| Summary of TAC Discussion |  | On 4/29/26, there was no additional discussion beyond TAC review of the items below. |  |
| TAC Review/Justification of Recommendation |  | Revision Request ties to Reason for Revision as explained in Justification Impact Analysis reviewed and impacts are justified as explained in Justification Opinions were reviewed and discussed Comments were reviewed and discussed (if applicable) Other: (explain) |  |
| ERCOT Board Decision |  | On 6/2/26, the ERCOT Board voted unanimously to recommend approval of PGRR133 as recommended by TAC in the 4/29/26 TAC Report. |  |

| Opinions |  |
| --- | --- |
| Credit Review | Not applicable |
| Independent Market Monitor Opinion | IMM has no opinion on PGRR133. |
| ERCOT Opinion | ERCOT supports approval of PGRR133. |
| ERCOT Market Impact Statement | ERCOT Staff has reviewed PGRR133 and believes the market impact for PGRR133 modifies approved PGRR115 requirements in a way that provides a reasonable, temporary accommodation for existing generators with a Resource Commissioning Date on or before December 31, 2025 to maintain their current configuration until such time a modification changing or adding a POI to the facility is made. |

| Sponsor |  |
| --- | --- |
| Name | Monica Jha; Katie Rich; Ned Bonskowski |
| E-mail Address | Monica.Jha@vistracorp.com; Katie.Rich@vistracorp.com; ned.bonskowski@vistracorp.com |
| Company | Vistra Operations Company LLC |
| Phone Number |  |
| Cell Number | 832-215-5713; 712-313-9351; 214-288-2456 |
| Market Segment | Independent Generator |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Cory Phillips |
| E-Mail Address | cory.phillips@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 110525 | Proposed revisions to restore language in paragraph (1) and add a new paragraph (2) to grandfather existing Resources from the requirements of paragraph (1) until such time as a modification subject to Section 5.2.1 is made. |
| Vistra 110625 | Proposed additional redlines to the 11/5/25 ERCOT comments to clarify language related to remote control and to exempt nuclear Generation Resources |
| LCRA 111825 | Proposed additional redlines to the 11/6/25 Vistra comments to specify which breakers shall be under remote control of the applicable TO |
| TCPA 112425 | Expressed support for the 11/6/25 Vistra comments |
| Joint Commenters 012826 | Proposed additional clarifying redlines to the 11/18/25 LCRA comments |

Market Rules Notes

None

Proposed Guide Language Revision

[PGRR115: Insert Section 5.2.11 below upon system implementation of NPRR1234:] ### 5.2.11 Required Interconnection Equipment (1) Each POI for a Generation Resource, ESR, or SOG interconnected at transmission voltage to the ERCOT System must have a permanent configuration consisting of a station with breakers capable of interrupting fault current to sectionalize the transmission lines connecting the station to the ERCOT System. The generator interconnection breakers at a TSP switching station shall be under the remote control of the applicable Transmission Operator (TO) and capable of being operated remotely to comply with an instruction from ERCOT. (2) For a Generation Resource, ESR, or SOG with a Resource Commissioning Date on or before December 31, 2025, the applicable breakers described in paragraph (1) of this Section may be remotely controllable at the direction of the TO. The TO shall communicate with the applicable Qualified Scheduling Entity (QSE) as needed to ensure coordination. A Generation Resource, ESR, or SOG with a Resource Commissioning Date on or before December 31, 2025 shall comply with the requirements of paragraph (1) of this Section if a modification subject to the requirements of paragraph (1)(c)(iv) of Section 5.2.1, Applicability, is made, or for the addition of load that would result in the total load co-located with the Generation Resource, ESR, or SOG of 75 MW or greater.