## Slide 1: ERCOT Frequency Events May 2026 ERCOT Operations Planning PDCWG Meeting June 17, 2026

## Slide 2: 5/20/2026 23:17:35 (FME)
Notes: Multiple units tripped offline for a total of ~780 MW
Starting Frequency: 60.008 Hz
Minimum Frequency: 59.948 Hz
A-C Time : 3 seconds
Recovery Time(back to deadband): 3 minutes 43 seconds
ECRS Released: 0 MW
Trip Reason: Unknown at this time.
Contextual Information: A total of 387 MW of regulation Up was deployed during the event. Multiple units experienced data quality issues at the time of the event.

## Slide 3: 5/27/2026 12:29:39 (Non-FME)
Notes: A unit tripped offline for ~515 MW
Starting Frequency: 60.012 Hz
Minimum Frequency: 59.954 Hz
A-C Time : 3 seconds
Recovery Time(back to deadband): 3 minutes 12 seconds
ECRS Released: 0 MW
Trip Reason: Lightning struck GSU
Contextual Information: A total of 381 MW of regulation Up was deployed during the event.
Reason for no selection: Inertia caused A-B frequency value of .289 Hz

## Slide 4: Questions/Comments?