## Purpose
| 2026-06-29 | Version 17 ERCOT Public
Mapping Document Related to NERC Reliability Standards IRO-010 and TOP-003
Purpose
ERCOT ISO maintains this mapping document as required by North American Electric Reliability Corporation (NERC) Reliability Standards IRO-010 and TOP-003. This mapping document provides applicable NERC-registered entities with a list of existing Protocol and Operating Guide references that identify the data, specifications and other relevant information required by ERCOT ISO to build and maintain its models to support Real-time Monitoring, Operational Planning Analyses, Real-time Assessments, and analysis functions. The periodicity and deadlines for providing data and information, data and information formats, processes for resolving data and information conflicts, and security protocols, where applicable, are detailed within the language of the Protocols, Operating Guides, and other binding documents for their respective data specification. ERCOT ISO and the NERC-registered entities collectively coordinate revisions to the Protocols, and Operating Guides in a mutually agreeable manner by way of the ERCOT regional stakeholder processes. In the event of any inconsistency between the Protocols, Other Binding Documents, or ICCP Communications Handbook and this mapping document, the Protocols, Other Binding Documents, and ICCP Communications Handbook prevail.
Revision and Distribution Process
This mapping document will be maintained by ERCOT ISO. Substantive revisions will be distributed via market notice and posted to the ERCOT website.

## Data Requirements-Protocols
Data and Information Required for Operational Planning Analyses (OPA), Real-time Assessments (RTA), & Real Time Monitoring, & analysis functions | [8 empty] | Entities Responsible for Responding
Section | Specification(s) for data and information | OPA | RTA | RTM | Periodicity | Deadline | Format | Method/Security Protocol | ERCOT Transmission Service Provider (TSP) NERC Transmission Owner (TO) | ERCOT Distribution Service Provider (DSP) NERC Distribution Provider (DP) | ERCOT Resource Entity (RE) NERC Generator Owner (GO) | ERCOT Qualified Scheduling Entity (QSE) NERC Generator Operator (GOP) | ERCOT Transmission Operator (TO) NERC Transmission Operator (TOP)
3.1.4.4 | Management of Forced Outages or Maintenance Outages | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.1.4.4 (1) | In the event of a Forced Outage, the Resource Entity or QSE, as appropriate, or TSP must notify ERCOT by: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.1.4.4 (1)(a) | For Resource Outages: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.1.4.4 (1)(a)(i) | Changing the telemetered Resource Status to the appropriate Off-Line status as soon as practicable but no longer than 15 minutes after the Forced Outage occurs; |  | X | X | As it occurs | As soon as practicable but no longer than 15 minutes after the Forced Outage occurs | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.1.4.4 (1)(a)(ii) | Updating the COP as soon as practicable but no longer than 60 minutes after the Forced Outage occurs; and | X |  |  | As it occurs | As soon as practicable but no longer than 60 minutes after the Forced Outage occurs | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.4.4 (1)(a)(iii) | Updating the Outage Scheduler, if necessary. | X |  |  | As it occurs | As soon as practicable but no longer than 60 minutes after the Forced Outage occurs | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.4.4 (1)(b) | For Transmission Facilities Forced Outages: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.1.4.4 (1)(b)(i) | Changing the telemetered status of the affected Transmission Elements; and |  | X | X | As it occurs | As soon as practicable | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | X
3.1.4.4 (1)(b)(ii) | Updating the Outage Scheduler with the expected return-to-service time. | X |  |  | As it occurs | As soon as practicable but no longer than 60 minutes after the Forced Outage occurs | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | None | None | X
3.1.4.4(3) | For Maintenance Outages, the Resource Entity or QSE, as appropriate, or TSP shall notify ERCOT of any Resource or Transmission Facilities Maintenance Outage according to the Maintenance Outage Levels by updating the COP and Outage Scheduler. ERCOT shall coordinate the removal of facilities from service within the defined timeframes as specified by the TSP, QSE or Resource Entity in its notice to ERCOT. | X |  |  | Continually | See timing tables in 3.1.5.3 (1), 3.1.6.6 (1) & 3.1.7.1 (2) | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | None | X | X
3.1.4.5 | Notice of Forced Outage or Unavoidable Extension of Planned Maintenance Outage, or Rescheduled Due to Unforeseen Events | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.1.4.5(1) | If a Planned, Maintenance, or Rescheduled Outage is not completed within the ERCOT-approved timeframe and the Transmission Facilities or Resources are in such a condition that they cannot be restored at the Outage schedule completion date, the requesting party shall submit to ERCOT a Forced Outage (unavoidable extension) form describing the extension of the Outage and providing a revised return date. | X |  |  | As it occurs | Before Planned, Maintenance or Rescheduled outages ends | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | None | X | X
3.1.4.5(2) | Any transmission Forced Outage that occurs in Real-Time and that is expected to continue for longer than two hours must be entered into the Outage Scheduler as soon as practicable but no longer than 60 minutes after the beginning of the Outage. Any transmission Forced Outage with a duration exceeding two hours must be entered into the Outage Scheduler as soon as practicable but no longer than 150 minutes after the beginning of the transmission Forced Outage, if not already reported in the Outage Scheduler. | X |  |  | As it occurs | If outage remains longer than two hours as soon as practicable but no longer than 60 minutes after the Forced Outage occurs OR as soon as practicable but no longer than 150 minutes after the beginning of the transmission Forced Outage for any transmission Forced Outage with a duration exceeding two hours | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | None | None | X
3.1.4.5(3) | Any Resource Forced Outage that occurs in Real-Time must be entered into the Outage Scheduler as soon as practicable but no longer than 60 minutes after the beginning of the Forced Outage. | X |  |  | As it occurs | No longer than 60 minutes after the beginning of the Forced Outage | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.4.5(5) | For a Startup Loading Failure, the Resource Entity or its designee must enter a Forced Outage in the Outage Scheduler if the Resource was in an Off-Line status prior to the Startup Loading Failure or update the existing Outage for the Resource if the Resource was on Outage prior to the Startup Loading Failure. The Resource Entity or its designee must also provide a text entry in the supporting information field of the Outage Scheduler that includes the following: (a) A statement that a Startup Loading Failure occurred; (b) An explanation of the cause of the Startup Loading Failure using the best available information at the time the Outage or update to the existing Outage is entered, which must be updated if more accurate information becomes available; and (c) The start time and end time of the Startup Loading Failure portion of the Outage. Multiple consecutive startup attempts may be aggregated into a single Startup Loading Failure event with a single start and end time. | X |  |  | As it occurs | No longer than 60 minutes after the beginning of the Forced Outage | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.4.7 | Reporting of Forced Derates | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.1.4.7(1) | If a Generation Resource or ESR experiences a Forced Derate in an amount greater than ten MW, and 5% of its Seasonal net maximum sustainable rating, and the Forced Derate lasts longer than 30 minutes, the Resource Entity or its designee must enter the Forced Derate into the Outage Scheduler as soon as practicable but no longer than 60 minutes after the beginning of the Forced Derate. | X |  |  | As it occurs | No longer than 60 minutes after the beginning of the Forced Derate | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.4.7(2) | If a Forced Derate that has already been reported changes by an amount greater than ten MW and 5% of the Generation Resource’s or ESR's Seasonal net maximum sustainable rating, and the change lasts longer than 30 minutes, the Resource Entity or its designee must enter the change as a new Forced Derate into the Outage Scheduler as soon as practicable but no longer than 60 minutes after the beginning of the change. | X |  |  | As it occurs | No longer than 60 minutes after the beginning of the change | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.4.7(3) | Notwithstanding paragraphs (1) and (2) above, for any Forced Derate or change to a Forced Derate that meets the reporting criteria specified in paragraph (1) or (2) above and that is caused by ambient temperature or humidity, the Resource Entity or its designee must enter the Forced Derate into the Outage Scheduler as soon as practicable but no longer than eight hours after the beginning of the Force Derate or change. | X |  |  | As it occurs | No longer than 8 hours after the beginning of the Forced Derate or change | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.4.7(4) | The QSE must appropriately update the telemetered High Sustained Limit (HSL) and any applicable telemetry as specified in paragraph (2) of Section 6.5.5.2, Operational Data Requirements, based on the Forced Derate, as soon as practicable but no longer than 15 minutes after the beginning of a Forced Derate, if the Forced Derate is greater than ten MW and more than 5% of the Seasonal net maximum sustainable rating of the Resource and its expected or actual duration is greater than 30 minutes. Alternatively for a Forced Derate, a QSE may use the ONHOLD process described in paragraph (2) of Section 6.5.5.1, Changes in Resource Status. |  | X | X | As it occurs | As soon as reasonably practicable but no longer than 15 minutes after the Forced Derate occurs | ICCP naming convention Private WAN point-to-point connection (RTA) | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.1.4.7(5) | The QSE must update the COP as soon as practicable but no longer than 60 minutes after the beginning of a Forced Derate, if the Forced Derate is greater than 20 MW and its expected duration is greater than 120 minutes. | X |  |  | As it occurs | No longer than 60 minutes after the beginning of a Forced Derate | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.4.7(6) | Each QSE shall timely update the telemetered HSL and COP unless in the reasonable judgment of the QSE, such compliance would create an undue threat to safety, undue risk of bodily harm, or undue damage to equipment. The QSE is excused from updating the telemetered HSL and/or COP only for so long as the undue threat to safety, undue risk of bodily harm, or undue damage to equipment exists. The time for updating the telemetered HSL and/or COP begins once the undue threat to safety, undue risk of bodily harm, or undue damage to equipment no longer exists. | X | X | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.1.5.1 | ERCOT Evaluation of Planned Outage and Maintenance Outage of Transmission Facilities | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.1.5.1(1) | A TSP or Resource Entity shall request a Planned Outage or Maintenance Outage when any Transmission Facility that is part of the ERCOT Transmission Grid and defined in the Network Operations Model will be removed from its normal service. For Resource Entities within a Private Use Network, this only includes Transmission Facilities at the Point of Interconnection (POI). For TSP requests, the TSPs shall enter such requests in the Outage Scheduler. For Resource Entity requests, the Resource Entity shall enter such requests in the Outage Scheduler. Planned Outages, Maintenance Outages, or Rescheduled Outages for Electrical Buses will be treated as consequentially outaged Transmission Elements. In those cases where a TSP enters the breaker and switch statuses associated with an Electrical Bus, a downstream topology processor will evaluate the breakers and switches associated with the applicable Electrical Bus to determine if the Electrical Bus is consequentially outaged, and to thereby designate the status of the Electrical Bus. Proposed Transmission Planned Outage or Maintenance Outage information submitted by a TSP or Resource Entity in accordance with this Section constitutes a request for ERCOT’s approval of the Outage Schedule associated with the Planned Outage or Maintenance Outage. ERCOT is not deemed to have approved the Outage Schedule associated with the Planned Outage or Maintenance Outage until ERCOT notifies the TSP or Resource Entity of its approval under procedures adopted by ERCOT. ERCOT shall evaluate requests under Section 3.1.5.11, Evaluation of Transmission Facilities Planned Outage or Maintenance Outage Requests. | X |  |  | As it occurs | See timing table | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | None | X | X
3.1.5.12 | Submittal Timeline for Transmission Facility Outage Requests | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.1.5.12(1) | TSPs shall submit all requests for Planned Outages and Maintenance Outages or changes to existing approved Outages of Transmission Elements in the Network Operations Model to ERCOT no later than the minimum amount of time between the submittal of a request to ERCOT for approval of a proposed Outage and the scheduled start date of the proposed Outage, according to the following table. | X |  |  | Continually | See timing table | Outage Scheduler Encrypted via https; authenticated Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | None | X | X
3.1.6.2 | Resources Outage Plan | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.1.6.2(1) | Resource Outage plans shall include the following information: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.1.6.2(1)(a) | The primary and alternate phone number of the Resource Entity’s Single Point of Contact for Outage Coordination; | X |  |  | As known | 45 days or immediately | Outage Scheduler Encrypted via https; authenticated Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.6.2(1)(b) | The Resource identified by the name in the Network Operations Model; | X |  |  | As known | 45 days or immediately | Outage Scheduler Encrypted via https; authenticated Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.6.2(1)(c) | The net megawatts of capacity the Resource Entity anticipates will be available during the Outage (if any); | X |  |  | As known | 45 days or immediately | Outage Scheduler Encrypted via https; authenticated Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.6.2(1)(d) | The estimated start and finish dates for each Planned and Maintenance Outage; | X |  |  | As known | 45 days or immediately | Outage Scheduler Encrypted via https; authenticated Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.6.2(1)(e) | An estimate of the acceptable deviation in the Outage schedule (i.e., the earliest start date and the latest finish date for the Outage); and | X |  |  | As known | 45 days or immediately | Outage Scheduler Encrypted via https; authenticated Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.6.2(1)(f) | The nature of work to be performed during the Outage. For a Forced Outage or Forced Derate, the “nature of work” field in the Outage Scheduler shall indicate the best available information about the cause of the Forced Outage or Forced Derate at the time the Outage or derate is entered and shall be updated as soon as more accurate information becomes available. | X |  |  | As known | 45 days or immediately | Outage Scheduler Encrypted via https; authenticated Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.1.6.11 | Outage Returning Early | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.1.6.11(1) | A Resource that completes a Planned Outage early and wants to resume operation shall notify ERCOT of the early return prior to resuming service by making appropriate entries in the COP or Outage Scheduler if applicable as much in advance as practicable, but not later than at least two hours prior to beginning startup. Within two hours of receiving such request, ERCOT shall either: | X |  |  | As known | No later than 2 hours before start up | Outage Scheduler Encrypted via https; authenticated Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.6.1 | Load Resource Participation | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.6.1(1) | A Load Resource may participate by providing: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.6.1(1)(a) | Ancillary Service: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.6.1(1)(a)(i) | Regulation Up (Reg-Up) Service as a Controllable Load Resource (CLR) capable of providing Primary Frequency Response; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.6.1(1)(a)(ii) | Regulation Down (Reg-Down) Service as a CLR capable of providing Primary Frequency Response; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.6.1(1)(a)(iii) | Responsive Reserve (RRS) as a CLR qualified for Security-Constrained Economic Dispatch (SCED) Dispatch and capable of providing Primary Frequency Response, or as a Load Resource controlled by high-set under-frequency relay; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.6.1(1)(a)(iv) | ERCOT Contingency Reserve Service (ECRS) as a CLR qualified for SCED Dispatch and capable of providing Primary Frequency Response, or as a Load Resource that may or may not be controlled by high-set under-frequency relay; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.6.1(1)(a)(v) | Non-Spinning Reserve (Non-Spin) as a CLR qualified for SCED Dispatch or as a Load Resource that is not a CLR and that is not controlled by under-frequency relay; and |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.6.1(1)(a)(vi) | A Load Resource that is not a CLR cannot simultaneously provide Non-Spin and RRS in Real-Time; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.6.1(1)(b) | Energy in the form of Demand response from a CLR in Real-Time via SCED; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.6.1(1)(c) | Emergency Response Service (ERS) for hours in which the Load Resource has a Resource Status of OUTL; and |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.6.1(1)(d) | Voluntary Load response in Real-Time. |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.7 | Resource Parameters | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.7.1.1 | Generation Resource Parameters | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.7.1.1 (1) | Generation Resource Parameters that may be modified, with documented reason for change, by the QSE for immediate use upon ERCOT validation include: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.7.1.1 (1)(a) | Normal Ramp Rate curve; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.1 (1)(b) | Emergency Ramp Rate curve; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.1 (1)(c) | Minimum On-Line time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.1 (1)(d) | Minimum Off-Line time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.1 (1)(e) | Maximum On-Line time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.1 (1)(f) | Maximum daily starts; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.1 (1)(g) | Maximum weekly starts; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.1 (1)(h) | Maximum weekly energy; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.1 (1)(i) | Hot start time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.1 (1)(j) | Intermediate start time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.1 (1)(k) | Cold start time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.1 (1)(l) | Hot to intermediate time; and | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.1 (1)(m) | Intermediate to cold time. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.2 | Load Resource Parameters | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.7.1.2(1) | Resource Parameters that may be modified, with documented reason for change, by the QSE for immediate use upon ERCOT validation, which may be adjusted to reflect Distribution Losses in accordance with Section 8.1.1.2, General Capacity Testing Requirements, include the following for each of its Load Resources that is a non-Controllable Load Resource: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.7.1.2(1)(a) | Maximum interruption time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.2(1)(b) | Maximum daily deployments; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.2(1)(c) | Maximum weekly deployments; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.2(1)(d) | Maximum weekly energy; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.2(1)(e) | Minimum notice time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.2(1)(f) | Minimum interruption time; and | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.7.1.2(1)(g) | Minimum restoration time. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.8.3 | Quick Start Generation Resources | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.8.3(1) | The QSE for a Quick Start Generation Resource (QSGR) that is available for deployment by SCED and awarding of ERCOT Contingency Reserve Service (ECRS) and Non-Spinning Reserve (Non-Spin), if qualified and capable, shall set the COP Resource Status to OFFQS, and the COP Low Sustained Limit (LSL) and COP HSL values to the expected sustainable LSL and HSL for the QSGR for the hour. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.8.3(2) | The QSGR that is available for deployment by SCED and awarding of ECRS and Non-Spin, if qualified and capable, shall telemeter a Resource Status of OFFQS and a LSL of zero prior to receiving a deployment instruction from SCED. This status is necessary in order for SCED to recognize that the Resource can be Dispatched and/or awarded ECRS and Non-Spin. The status of the breaker shall be open and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system. After being deployed for energy from SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has ramped to its physical LSL. After reaching its physical LSL, the QSGR shall telemeter an LSL that reflects its physical LSL. |  | X | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.8.3(5) | For a QSGR that is physically Off-Line, the Resource Entity shall submit a Normal Ramp Rate curve and Emergency Ramp Rate curve indicating QSGR’s ability to reach its ten-minute tested output from zero output in five minutes. This is necessary to prevent SCED from deploying multiple QSGRs due to ramp limitation in the first five minutes after being Dispatched by SCED. QSGRs shall be exempt from Set Point Deviation Charges as described in Section 6.6.5.3, Resources Exempt from Deviation Charges. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.9 | Current Operating Plan (COP) | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.9(1) | Each Qualified Scheduling Entity (QSE) that represents a Resource must submit a Current Operating Plan (COP) under this Section. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.9(4) | A QSE must notify ERCOT that it plans to have a Resource On-Line by means of the COP using the Resource Status codes listed in paragraph (5)(b)(i) of Section 3.9.1, Current Operating Plan (COP) Criteria. The QSE must show the Resource as On-Line with a Resource Status of ONRUC, indicating a RUC process committed the Resource for all RUC-Committed Intervals. A QSE may only use a RUC-committed Resource during that Resource’s RUC-Committed Interval to meet the QSE’s Ancillary Service Supply Responsibility if the Resource has been committed by the RUC process to provide Ancillary Service. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.9(5) | To reflect changes to a Resource’s capability, each QSE shall report by exception, changes to the COP for all hours after the Operating Period through the rest of the Operating Day. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.9(7) | Each QSE, including QSEs representing Reliability Must-Run (RMR) Units, Firm Fuel Supply Service Resources (FFSSRs), or Black Start Resources, shall submit a revised COP reflecting changes in Resource availability as soon as reasonably practicable, but in no event later than 60 minutes after the event that caused the change. | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.9(8) | Each QSE representing a Qualifying Facility (QF) must submit a Low Sustained Limit (LSL) that represents the minimum energy available, in MW, from the unit for economic dispatch based on the minimum stable steam delivery to the thermal host plus a justifiable reliability margin that accounts for changes in ambient conditions. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.9(9) | When ERCOT issues a communication in the form of an Operating Condition Notice (OCN), Advisory, Watch, or Emergency Notice due to forecasted or actual cold or hot weather, for each Generation Resource and Energy Storage Resource (ESR) a QSE represents, the QSE shall update the COP, Real-Time telemetry, and Outage or derate reporting to reflect any Resource-specific operating limitations based on: (i) capability and availability; (ii) fuel supply or inventory concerns, including fuel switching capabilities; or (iii) environmental constraints and the impact on the Generation Resource or ESR due to the weather conditions. QSEs shall provide these updates in accordance with Sections 3.1.4, Communications Regarding Resource and Transmission Facility Outages; 3.10.7.5, Telemetry Requirements; 3.9, Current Operating Plan (COP); 3.9.1, Current Operating Plan (COP) Criteria; and Nodal Operating Guide Section 7.3, Telemetry. | X | X | X | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP Naming Convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1 | Current Operating Plan (COP) Criteria | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.9.1(1) | Each QSE that represents a Resource must submit a COP to ERCOT that reflects expected operating conditions for each Resource for each hour in the next seven Operating Days. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.9.1(2) | Each QSE that represents a Resource shall update its COP reflecting changes in availability of any Resource as soon as reasonably practicable, but in no event later than 60 minutes after the event that caused the change. Each QSE shall timely update its COP unless in the reasonable judgment of the QSE, such compliance would create an undue threat to safety, undue risk of bodily harm, or undue damage to equipment. The QSE is excused from updating the COP only for so long as the undue threat to safety, undue risk of bodily harm, or undue damage to equipment exists. The time for updating the COP begins once the undue threat to safety, undue risk of bodily harm, or undue damage to equipment no longer exists. | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.9.1(3) | Each QSE that represents a Resource shall update its COP to reflect the ability of the Resource to provide each Ancillary Service by product and sub-type. Additionally, for a COP provided for an ESR, the QSE shall ensure that the Hour Beginning Planned State of Charge (HBSOC) for any two consecutive hours shall be feasible based on the ESR’s maximum rate of charge or discharge. | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.9.1(5) | A COP must include the following for each Resource represented by the QSE: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.9.1(5)(a) | The name of the Resource; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.9.1(5)(b) | The expected Resource Status: | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.9.1(5)(b)(i) | Select one of the following for Generation Resources synchronized to the ERCOT System that best describes the Resource’s status. Unless otherwise provided below, these Resource Statuses are to be used for COP and/or Real-Time telemetry purposes, as appropriate. | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.9.1(5)(b)(i)(A) | ONRUC – On-Line and the hour is a RUC-Committed Hour; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(i)(B) | ON – On-Line Resource with Energy Offer Curve; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(i)(C) | ONOS – On-Line Resource with Output Schedule; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(i)(D) | ONTEST – On-Line blocked from SCED for operations testing (while ONTEST, a Generation Resource may be shown on Outage in the Outage Scheduler); | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(i)(E) | ONEMR – On-Line EMR (available for commitment or dispatch only for ERCOT-declared Emergency Conditions; the QSE may appropriately set LSL and High Sustained Limit (HSL) to reflect operating limits); | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(i)(F) | ONOPTOUT – On-Line and the hour is a RUC Buy-Back Hour; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(i)(G) | SHUTDOWN – The Resource is On-Line and in a shutdown sequence, and is not eligible for an Ancillary Service award. This Resource Status is only to be used for Real-Time telemetry purposes; and | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(i)(H) | STARTUP – The Resource is On-Line and in a start-up sequence and is not eligible for an Ancillary Service award, unless coming On-Line in response to a manual deployment of ERCOT Contingency Reserve Service (ECRS) or Non-Spinning Reserve (Non-Spin). This Resource Status is only to be used for Real-Time telemetry purposes. | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(i)(I) | OFFQS – Off-Line but available for SCED deployment and to provide ECRS and Non-Spin, if qualified and capable. Only qualified Quick Start Generation Resources (QSGRs) may utilize this status. | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(i)(K) | ONSC – Resource is On-Line operating as a synchronous condenser and available to provide Responsive Reserve (RRS) and ECRS, if qualified and capable, and for commitment by RUC, but is unavailable for Dispatch by SCED. For SCED, Resource Base Points will be set equal to the telemetered net real power of the Resource available at the time of the SCED execution; and |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(i)(J) | ONHOLD – Resource is On-Line but temporarily unavailable for Dispatch by SCED or Ancillary Service awards due to a valid and verifiable operational reason. This Resource Status is only to be used for Real-Time telemetry purposes. For SCED, Resource Base Points will be set equal to the telemetered net real power of the Resource available at the time of the SCED execution. |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(ii) | Select one of the following for Off-Line Generation Resources not synchronized to the ERCOT System that best describes the Resource’s status. These Resource Statuses are to be used for COP and/or Real-Time telemetry purposes, as appropriate. | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.9.1(5)(b)(ii)(A) | OUT – Off-Line and unavailable, or not connected to the ERCOT System and operating in a Private Microgrid Island (PMI); | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(ii)(B) | OFF – Off-Line but available for commitment in the Day-Ahead Market (DAM), RUC and providing Non-Spin, if qualified and capable; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(ii)(C) | EMR – Available for commitment as a Resource contracted by ERCOT under Section 3.14.1, Reliability Must Run, or under paragraph (4) of Section 6.5.1.1, ERCOT Control Area Authority, or available for commitment only for ERCOT-declared Emergency Condition events; the QSE may appropriately set LSL and HSL to reflect operating limits; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(ii)(D) | EMRSWGR - Switchable Generation Resource (SWGR) operating in a non-ERCOT Control Area, or in the case of a Combined Cycle Train with one or more SWGRs, a configuration in which one or more of the physical units in that configuration are operating in a non-ERCOT Control Area. | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(iii) | Select one of the following for Load Resources. Unless otherwise provided below, these Resource Statuses are to be used for COP and/or Real-Time telemetry purposes. | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.9.1(5)(b)(iii)(A) | OUTL – Not available; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(b)(iii)(B) | ONL – On-Line and available for Dispatch by SCED or providing Ancillary Services. | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(c) | The HSL; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(c)(i) | For Load Resources other than CLRs, the HSL should equal the expected power consumption; | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.9.1(5)(d) | The LSL; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(d)(i) | For Load Resources other than CLRs, the LSL should equal the expected Low Power Consumption (LPC); | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.9.1(5)(e) | The High Emergency Limit (HEL); | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(f) | The Low Emergency Limit (LEL); and | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(g) | Ancillary Service capability in MW for each product and sub-type. | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.9.1(5)(h) | For ESRs: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.9.1(5)(h)(i) | Minimum State of Charge (MinSOC); | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(h)(ii) | Maximum State of Charge (MaxSOC); and | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(5)(h)(iii) | HBSOC. | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.9.1(6) | For Combined Cycle Generation Resources, the above items are required for each operating configuration. In each hour only one Combined Cycle Generation Resource in a Combined Cycle Train may be assigned one of the On-Line Resource Status codes described above. | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.10.1 | Time Line for Network Operations Model Changes | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.1(3) | TSPs and Resource Entities shall submit all Network Operations Model updates that are not subject to the requirements of paragraph (4) below by the applicable deadline to submit information to ERCOT for the target date of inclusion in the production model detailed in the table below. ERCOT shall update the Network Operations Model according to the following table (see table in protocols) | X |  |  | As needed | Applicable deadline prior to inclusion in applicable ERCOT systems | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.1(4) | Resource Entities shall submit complete initial Resource Registration data for inclusion in the ERCOT Network Operations Model as described in paragraph (6) of Planning Guide Section 6.8.1, Resource Registration, by the applicable deadline for the Resource Entity to submit complete information to ERCOT for the target date of inclusion in the production model detailed in the table below. ERCOT shall update the Network Operations Model according to the following table (see table in protocols) | X |  |  | As needed | Applicable deadline prior to inclusion in applicable ERCOT systems | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6 | QSE and Resource Entity Responsibilities | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.6(1) | Resource Entities shall provide Resource Registration data pursuant to Planning Guide Section 6.8.2, Resource Registration Process, to ERCOT and to TSPs upon request. The Resource Registration data will contain information describing each Generation Resource, ESR, SOG, SOESS, and Load Resource that it represents under Section 3.10.7.2, Modeling of Resources and Transmission Loads. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(3) | For each Generation Resource and Energy Storage Resource (ESR), Resource Entities shall provide ERCOT the following temperature data: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.10.6(3)(a) | Cold weather temperature limits: | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.6(3)(a)(i) | Minimum historical ambient dry bulb temperature in degrees Fahrenheit at which the Resource has operated without a Forced Outage or Startup Loading Failure due to cold weather after at least one complete winter Peak Load Season following the Resource’s Initial Synchronization date based on the previous five calendar years of historical data; and | X |  |  | As needed | At least annually, and within 30 days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(3)(a)(ii) | Minimum historical ambient dry bulb temperature in degrees Fahrenheit at which the Resource has operated without experiencing a Forced Derate greater than 10 MW and 5% of its winter Seasonal net maximum rating due to cold weather after at least one complete winter Peak Load Season following the Resource’s Initial Synchronization date based on the previous five calendar years of historical data; and | X |  |  | As needed | At least annually, and within 30 days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(3)(a)(iii) | At least one of the following: | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.6(3)(a)(iii)(A) | Minimum ambient dry bulb temperature in degrees Fahrenheit at which the Resource was designed to operate without a Forced Derate greater than 10 MW and 5% of its winter Seasonal net maximum sustainable rating; or | X |  |  | As needed | At least once every seven years, and within 30 days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(3)(a)(iii)(B) | Minimum ambient dry bulb temperature in degrees Fahrenheit at which the Resource can operate without a Forced Derate greater than 10 MW and 5% of its winter Seasonal net maximum sustainable rating determined by an engineering analysis; and | X |  |  | As needed | At least once every seven years, and within 30 days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(3)(a)(iv) | At least one of the following: | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.6(3)(a)(iv)(A) | Minimum ambient dry bulb temperature in degrees Fahrenheit at which the Resource was designed to operate without a Forced Outage or Startup Loading Failure; or | X |  |  | As needed | At least once every seven years, and within 30 days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(3)(a)(iv)(B) | Minimum ambient dry bulb temperature in degrees Fahrenheit at which the Resource can operate without a Forced Outage or Startup Loading Failure determined by an engineering analysis. | X |  |  | As needed | At least once every seven years, and within 30 days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(3)(b) | Hot weather temperature limits: | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.6(3)(b)(i) | Maximum historical ambient dry bulb temperature in degrees Fahrenheit at which the Resource has operated without experiencing a Forced Outage or Startup Loading Failure due to hot weather after at least one complete summer Peak Load Season following the Resource’s Initial Synchronization date based on the previous five years of historical data; and | X |  |  | As needed | At least annually and within 30days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(3)(b)(ii) | Maximum historical ambient dry bulb temperature in degrees Fahrenheit at which the Resource has operated without experiencing a Forced Derate greater than 10 MW and 5% of its summer Seasonal net maximum sustainable rating due to hot weather after at least one complete summer Peak Load Season following the Resource’s Initial Synchronization date based on the previous five calendar years of historical data; and | X |  |  | As needed | At least annually and within 30days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(3)(b)(iii) | At least one of the following: | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.6(3)(b)(iii)(A) | Maximum ambient dry bulb temperature in degrees Fahrenheit at which the Resource was designed to operate without a Forced Derate greater than 10 MW and 5% of its summer Seasonal net maximum sustainable rating; or | X |  |  | As needed | At least once every seven years, and within 30 days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(3)(b)(iii)(B) | Maximum ambient dry bulb temperature in degrees Fahrenheit at which the Resource was designed to operate without a Forced Derate greater than 10 MW and 5% of its summer Seasonal net maximum sustainable rating; or | X |  |  | As needed | At least once every seven years, and within 30 days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(3)(b)(iv) | At least one of the following: | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.6(3)(b)(iv)(A) | Maximum ambient dry bulb temperature in degrees Fahrenheit at which the Resource was designed to operate without a Forced Outage or Startup Loading Failure; or | X |  |  | As needed | At least once every seven years, and within 30 days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(3)(b)(iv)(B) | Maximum ambient dry bulb temperature in degrees Fahrenheit at which the Resource can operate without a Forced Outage or Startup Loading Failure, determined by an engineering analysis. | X |  |  | As needed | At least once every seven years, and within 30 days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(4) | Each Resource Entity shall review at least annually the temperatures described in paragraphs (3)(a)(i), (3)(a)(ii), (3)(b)(i), and (3)(b)(ii) above and shall update each Resource’s Registration data within 30 days of identifying any change in these temperatures. | X |  |  | At least annually | At least annually and within 30days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(5) | Each Resource Entity shall review at least once every seven years the temperatures described in paragraphs (3)(a)(iii), (3)(a)(iv), (3)(b)(iii), and (3)(b)(iv) above and shall update each Resource’s Registration data within 30 days of identifying any change in these temperatures. | X |  |  | Every 7 years | At least once every seven years, and within 30 days of identifying any change. | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.6(6) | Resource Entities shall update each Generation Resource’s alternate fuel information within 30 calendar days of any changes to the alternate fuel information. | X |  |  | As needed | Within 30 calendar days of any changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.7.1.1 | Transmission Lines | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.7.1.1(2) | For each of its transmission lines operated as part of the ERCOT Transmission Grid, each TSP and if applicable, Resource Entity, shall provide ERCOT with the following information consistent with the ratings methodology prescribed in the ERCOT Operating Guides: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.10.7.1.1(2)(a) | Equipment owner(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.1(2)(b) | Equipment operator(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.1(2)(c) | Transmission Element name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.1(2)(d) | Line impedance; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.1(2)(e) | Normal Rating, Emergency Rating, 15-Minute Rating, Conductor/Transformer 2-Hour Rating, and Relay Loadability Rating; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.1(2)(f) | Other data necessary to model Transmission Element(s). | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.1(4) | The TSP and Resource Entity may implement protective relay and control systems and set values appropriate to de-energize faulted equipment and meet the TSP and Resource Entity obligations for public or employee safety, and when necessary to prevent in-service or premature equipment failure consistent with Good Utility Practice and accepted industry standards. The TSP and Resource Entity shall include those limits as Relay Loadability Ratings when providing ERCOT with ratings or proposed transfer limits. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.2 | Transmission Buses | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.7.1.2(2) | Each TSP and if applicable, Resource Entity, shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.10.7.1.2(2)(a) | Equipment owner(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.2(2)(b) | Equipment operator(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.2(2)(c) | The Transmission Element name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.2(2)(d) | The substation name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.2(2)(e) | A description of all transmission circuits that may be connected through breakers or switches; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.2(2)(f) | Other data necessary to model Transmission Element(s). | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.3 | Transmission Breakers and Switches | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.7.1.3(2) | Each TSP and Resource Entity shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.10.7.1.3(2)(a) | Equipment owner(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.3(2)(b) | Equipment operator(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.3(2)(c) | The Transmission Element name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.3(2)(d) | The substation name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.3(2)(e) | Connectivity; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.3(2)(f) | Normal status; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.3(2)(g) | Synchronism Check Relay phase angle limits that are applied to operator-initiated, non-automated control actions of TSP-owned transmission breakers; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.3(2)(h) | Other data necessary to model Transmission Element(s). | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.3(3) | ERCOT shall develop methods to accurately model changes in transmission line loading resulting from Load rollover schemes transferring more than ten MW. This may include modeling distribution circuit breakers, dead line sensing, or other methods that signal when the Load should be transferred from one transmission line to another transmission line. ERCOT may employ heuristic rule sets for all manual Load transfers and for automated transfers where feasible. ERCOT application software is required to model the effects of automatic or manual schemes in the field transfer Load under line outage conditions. Each TSP and as applicable, Resource Entity, shall define the Load rollover schemes under Section 3.10.7.2, Modeling of Resources and Transmission Loads, and furnish this information to ERCOT. Transmission field (right-of-way) switches must be connected to a named Electrical Bus and be included in the Network Operations Model. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.4 | Transmission, Main Power Transformers (MPTs) and Generation Step-Up Transformers | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.7.1.4(3) | Each TSP and Resource Entity shall provide ERCOT with information to accurately describe each transformer in the Network Operations Model including any tertiary Load as required by ERCOT. Each TSP and Resource Entity shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.10.7.1.4(3)(a) | Equipment owner(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.4(3)(b) | Equipment operator(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.4(3)(c) | The Transmission Element name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.4(3)(d) | The substation name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.4(3)(e) | Winding ratings, including Normal Rating, Emergency Rating, 15-Minute Rating, Conductor/Transformer 2-Hour Rating, and Relay Loadability Rating; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.4(3)(f) | Connectivity; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.4(3)(g) | Transformer parameters, including all tap parameters; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.4(3)(h) | Other data necessary to model Transmission Element(s). | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | None | None
3.10.7.1.5 | Reactors, Capacitors, and other Reactive Controlled Sources | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.7.1.5(2) | Each Market Participant shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.10.7.1.5(2)(a) | Equipment owner(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | X | X
3.10.7.1.5(2)(b) | Equipment operator(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | X | X
3.10.7.1.5(2)(c) | The Transmission Element name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | X | X
3.10.7.1.5(2)(d) | The substation name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | X | X
3.10.7.1.5(2)(e) | Voltage or time switched on; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | X | X
3.10.7.1.5(2)(f) | Voltage or time switched off; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | X | X
3.10.7.1.5(2)(g) | Associated switching device name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | X | X
3.10.7.1.5(2)(h) | Connectivity; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | X | X
3.10.7.1.5(2)(i) | Nominal voltage and associated capacitance or reactance; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | X | X
3.10.7.1.5(2)(j) | Other data necessary to model Transmission Element(s). | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | X | X | X
3.10.7.2 | Modeling of Resources and Transmission Loads | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.7.2(1) | Each Resource Entity shall provide ERCOT and its interconnecting TSP with information describing each of its Generation Resources, ESRs, SOGs, SOESSs, and Load Resources connected to the ERCOT System. All Transmission Generation Resources (TGRs), Transmission ESRs (TESRs), Settlement Only Transmission Generators (SOTGs), Settlement Only Transmission Self-Generators (SOTSGs), Settlement Only Transmission Energy Storage Systems (SOTESSs), and the non-TSP MPTs greater than ten MVA, must be modeled to provide equivalent generation injections to the ERCOT Transmission Grid. ERCOT shall coordinate the modeling of Generation Resources, ESRs, Private Use Networks, and Load Resources with their owners to ensure consistency between TSP models and ERCOT models. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.7.2(2) | Each Resource Entity representing either a Load Resource or an Aggregate Load Resource (ALR) shall provide ERCOT and, as applicable, its interconnecting DSP and TSP, with information describing each such Resource as specified in Section 3.7.1.2, Load Resource Parameters, and any additional information and telemetry as required by ERCOT, in accordance with the timelines set forth in Section 3.10.1, Time Line for Network Operations Model Changes. ERCOT shall coordinate the modeling of ALRs with Resource Entities. ERCOT shall coordinate with representatives of the Resource Entity to map Load Resources to their appropriate Load in the Network Operations Model. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.7.2(3) | Each Resource Entity representing a Distribution Generation Resource (DGR) or Distribution Energy Storage Resource (DESR) that is registered with ERCOT pursuant to Section 16.5, Registration of a Resource Entity, shall provide ERCOT, its interconnecting DSP, and the TSP that interconnects the DSP to the transmission system with information describing each of its DGR or DESR facilities, and additional information and telemetry as required by ERCOT and the interconnecting DSP. ERCOT shall coordinate with representatives of the Resource Entity to represent the registered DGR or DESR facilities at their appropriate Electrical Bus in the Network Operations Model. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.7.2(6) | ERCOT shall create a DC Tie Resource to represent an equivalent generation injection to represent the flow into the ERCOT Transmission Grid from operation of DC Ties. The actual injection flow on the DC Tie from telemetry provided by the facility owner(s) is the DC Tie Resource output. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA) | Point-to-Point Protocol (PPP) | X | None | None | None | None
3.10.7.2(10) | Each TSP shall also provide information to ERCOT describing automatic Load transfer (rollover) plans and the events that trigger which Loads are switched to other Transmission Elements on detection of Outage of a primary Transmission Element. ERCOT shall accommodate Load rollover plans in the Network Operations Model. | X | X |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | None | None | None
3.10.7.3 | Modeling of Private Use Networks | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.7.3 (1) | ERCOT shall create and use network models describing Private Use Networks according to the following: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.10.7.3(1)(a) | A Generation Entity with a Resource located within a Private Use Network shall provide data to ERCOT, for use in the Network Operations Model, for each of its individual generating unit(s) located within the Private Use Network in accordance with Section 3.3.2.1, Information to Be Provided to ERCOT, if it meets any one of the following criteria: | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.7.3(1)(a)(i) | Contains a generator greater than ten MW and is registered with the PUCT according to P.U.C. Subst. R. 25.109, Registration of Power Generation Companies and Self-Generators, as a power generation company; or | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.7.3(1)(a)(ii) | Is part of a Private Use Network which contains more than one connection to the ERCOT Transmission Grid; or | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.7.3(1)(a)(iii) | Contains generation registered to provide Ancillary Services. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) or Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.7.3(1)(b) | A Generation Entity with an SOTSG shall provide to ERCOT annually, or more often upon change, the following information for ERCOT's use in the Network Operations Model, for each of its individual generating unit(s) located within the Private Use Network: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.10.7.3(1)(b)(i) | Equipment owner(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.7.3(1)(b)(ii) | Equipment operator(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | X | None
3.10.7.3(1)(b)(iii) | TSP substation name connecting the Private Use Network to the ERCOT System; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | X | None
3.10.7.3(1)(b)(iv) | At the request of ERCOT, a description of Transmission Elements within the Private Use Network that may be connected through breakers or switches; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | X | None
3.10.7.3(1)(b)(v) | Net energy delivery metering, as required by ERCOT, to and from a the Private Use Network and the ERCOT System at the POIB; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | X | None
3.10.7.3(1)(b)(vi) | For each individual generator located within the Private Use Network, the gross capacity in MW and its reactive capability curve; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | X | None
3.10.7.3(1)(b)(vii) | Maximum and minimum reasonability limits of the Load located within the Private Use Network; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | X | None
3.10.7.3(1)(b)(viii) | Outage schedule for each generation unit located within the Private Use Network, updated as changes occur from the annually submitted information; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.7.3(1)(b)(ix) | Other interconnection data as required by ERCOT. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | X | None
3.10.7.5.1 | Continuous Telemetry of the Status of Breakers and Switches | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.7.5.1(1) | Each TSP and QSE shall be responsible for providing telemetry, as described in this subsection, to ERCOT on the status of all breakers and switches it owns or its Resource owns, respectively, used to switch any Transmission Element or Load modeled by ERCOT. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA) | Point-to-Point Protocol (PPP) | X | None | None | X | None
3.10.7.5.1(3) | Each TSP, Resource Entity, or QSE shall update the status of any breaker or switch it owns or is responsible for through manual entries, if necessary, to communicate the actual current state of the device to ERCOT, except if the change in state is expected to return to the prior state within one minute. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA) | Point-to-Point Protocol (PPP) | X | None | X | X | None
3.10.7.5.2 | Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.7.5.2(1) | Each TSP and QSE shall provide telemetry of voltages, flows, and Loads on any modeled Transmission Element it owns or its Resource Entity owns, respectively, to the extent such may be required to estimate all transmission Load withdrawals and generation injections to and from the ERCOT Transmission Grid using the State Estimator and as needed to meet the State Estimator requirements set forth in Section 3.10.9, State Estimator Requirements, with consideration given to the economic implications of inaccurate LMP results versus the cost to remedy. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA) | Point-to-Point Protocol (PPP) | X | None | None | X | None
3.10.7.5.2(8) | Each TSP shall designate which telemetered measurement of the POIB voltage shall be utilized to determine compliance with Voltage Set Point instructions, and then update the designation as necessary in the Network Operations Model by submitting a NOMCR. Each TSP shall telemeter this POI kV bus measurement to ERCOT. If the TSP cannot provide a kV bus measurement at the POI, the TSP may propose an alternate location subject to ERCOT approval. |  |  | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | None
3.10.7.5.3 | Required Telemetry of Voltage and Power Flow | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.7.5.3(1) | QSEs, Resource Entities and TSPs as indicated in each subsection below shall provide power operation data to ERCOT, including, but not limited to: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.10.7.5.3(1)(a) | Real-Time generation data from QSEs; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.10.7.5.3(1)(b) | Planned and Forced Outage information from QSEs; | X |  |  | As soon as reasonably practicable | If Forced outages remains longer than two hours | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
3.10.7.5.3(1)(c) | Network data from TSPs and QSEs , including: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.10.7.5.3(1)(c)(i) | Breaker and line switch status of all ERCOT Transmission Grid devices; | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA) | Point-to-Point Protocol (PPP) | X | None | None | X | None
3.10.7.5.3(1)(c)(ii) | Line flow MW and MVAr; | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA) | Point-to-Point Protocol (PPP) | X | None | None | X | None
3.10.7.5.3(1)(c)(iii) | Breaker and switch status connected to any Resource; | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA) | Point-to-Point Protocol (PPP) | X | None | None | X | None
3.10.7.5.3(1)(c)(iv) | Transmission Facility voltages; and | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA) | Point-to-Point Protocol (PPP) | X | None | None | None | None
3.10.7.5.3(1)(c)(v) | Transformer MW, MVAr and tap; | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA) | Point-to-Point Protocol (PPP) | X | None | None | None | None
3.10.7.5.3(1)(d) | Real-Time generation and Load Resource meter data from QSEs; | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA) | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.10.7.5.3(1)(e) | Real-Time generation meter splitting signal from QSEs; | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA) | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.10.7.5.3(1)(f) | Transmission Facility Planned and Forced Outage information from TSPs; | X |  |  | Continually and As it occurs | Planned: per section 3.1.5.3 of the Protocols Forced: If outages remains longer than two hours | Outage Scheduler Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | None | None | None
3.10.7.5.3(1)(g) | Network transmission data (model and constraints) from TSPs; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Network Operations Model Change Request (NOMCR) Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | None | None | None
3.10.7.5.3(1)(h) | Resource modeling data, including any Resource owned transmission equipment data from Resource entity; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | None | None
3.10.8.1 | Dynamic Ratings Delivered via ICCP | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.8.1(1) | The TSP shall supply the following, via ICCP, updated at least every ten minutes: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.10.8.1(1)(a) | Normal Rating; and |  | X | X | At least every ten minutes | Ten minutes | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | None
3.10.8.1(1)(b) | Optionally Emergency Rating and/or 15-Minute Rating (required when Emergency Rating is provided). |  | X | X | At least every ten minutes | Ten minutes | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | None
3.10.8.5 | Transmission Service Provider Responsibilities Related to Dynamic Ratings | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.10.8.5(1) | Each TSP shall: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.10.8.5(1)(a) | Provide ERCOT with tables of ratings for different ambient temperatures for Transmission Elements, as requested by ERCOT. | X |  |  | As needed | Within 2 months | Network Operations Model Change Request (NOMCR) Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | None | None | None
3.10.8.5(1)(b) | Submit within two months a temperature adjusted rating table when a request is received from ERCOT unless multiple requests are made by ERCOT within the two-month period or unusual circumstances prevent the request from being accommodated in a timely fashion. Such circumstances must be explained to ERCOT in writing and must be posted by ERCOT on the MIS Secure Area within five Business Days of receipt. | X |  |  | As needed | Within 2 months | Network Operations Model Change Request (NOMCR) Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | X | None | None | None | None
3.10.8.5(1)(c) | Provide Real-Time temperatures for each Weather Zone in which the TSP has existing dynamically rated transmission equipment, or alternatively provide rating updates for each temperature-adjusted line rating updated at least once every ten minutes. |  | X | X | At least every ten minutes | Within 2 months | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | None
3.13 | Renewable Production Potential Forecasts | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.13(1) | ERCOT shall produce forecasts of Renewable Production Potential (RPP) for Wind-powered Generation Resources (WGRs) and PhotoVoltaic Generation Resources (PVGRs) to be used as an input into the Day-Ahead Reliability Unit Commitment (DRUC) and Hour-Ahead Reliability Unit Commitment (HRUC). ERCOT shall produce the forecasts using information provided by WGR/PVGR Entities, meteorological information, and Supervisory Control and Data Acquisition (SCADA). WGR and PVGR Entities shall install telemetry at their respective Resources and transmit the ERCOT-specified site-specific meteorological information to ERCOT. WGR and PVGR Entities shall also provide detailed equipment status at the WGR/PVGR facility as specified by ERCOT to support the RPP forecast. ERCOT shall post forecasts for each WGR and PVGR to the Qualified Scheduling Entities (QSEs) representing WGRs and/or PVGRs on the Market Information System (MIS) Certified Area. QSEs shall use the ERCOT-provided forecasts for WGRs/PVGRs throughout the Day-Ahead and Operating Day for applicable markets and Reliability Unit Commitments (RUCs). Similar requirements for run-of-the-river hydro must be developed as needed. | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate / ICCP naming convention Private WAN point-to-point connection | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
3.14.5 | Firm Fuel Supply Service | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.14.5(5)(b) | After receiving preliminary approval or instruction from ERCOT, the QSE shall: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.14.5(5)(b)(i) | Immediately provide a final estimate for completing the restocking of fuel; or |  |  | X | After preliminary approval or instruction from ERCOT | Immediately of such preliminary approval or instruction from ERCOT | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.14.5(5)(b)(ii) | Within 24 hours, notify the ERCOT control room with an updated estimated timeline to complete the restocking of the fuel. |  |  | X | After preliminary approval or instruction from ERCOT | No later than 24 hours of such preliminary approval or instruction from ERCOT | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.15 | Voltage Support | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.15(15) | All WGRs must provide a Real-Time SCADA point that communicates to ERCOT the number of wind turbines that are available for real power and Reactive Power injection into the ERCOT Transmission Grid. WGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following: |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | X | X | None
3.15(15)(a) | The number of wind turbines that are not able to communicate and whose status is unknown; and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | X | X | None
3.15(15)(b) | The number of wind turbines out of service and not available for operation. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | X | X | None
3.15(16) | All PhotoVoltaic Generation Resources (PVGRs) must provide a Real-Time SCADA point that communicates to ERCOT the capacity of PhotoVoltaic (PV) equipment that is available for real power and Reactive Power injection into the ERCOT Transmission Grid. PVGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following: |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | X | X | None
3.15(16)(a) | The capacity of PV equipment that is not able to communicate and whose status is unknown; and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | X | X | None
3.15(16)(b) | The capacity of PV equipment that is out of service and not available for operation. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | X | X | None
3.15.3 | Generation Resource and Energy Storage Resource Requirements Related to Voltage Support | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
3.15.3(4) | Each Generation Resource and ESR providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the automatic voltage control mode unless specifically directed to operate in manual mode by ERCOT, or when the unit is telemetering its Resource Status as STARTUP, SHUTDOWN, or ONTEST, or the QSE determines a need to operate in manual mode due to an undue threat to safety, undue risk of bodily harm, or undue damage to equipment at the generating plant. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.15.3(7) | Each QSE shall send to ERCOT, via telemetry, the AVR and Power System Stabilizer (PSS) status for each of its Generation Resources providing VSS. Each QSE shall send to ERCOT via telemetry the AVR status for each of its ESRs providing VSS. For AVRs, an “On” status will indicate the AVR is on and set to regulate the Resource’s terminal voltage in the voltage control mode, and an “Off” status will indicate the AVR is off or in a manual mode. For PSS, an “On” status will indicate the service is enabled and ready for service, and an “Off” status will indicate it is off or out of service. Each QSE shall monitor the status of its Generation Resources’ and ESRs’ regulators and stabilizers, and shall report status changes to ERCOT. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
3.15.3(10) | The Resource Entity for an IRR synchronized to the ERCOT System that is not capable of providing Reactive Power when not producing real power shall: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.15.3(10)(d) | Send to ERCOT, via telemetry, an AVR status of “Off” when the IRR is synchronized to the ERCOT System and not producing Reactive Power. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | X | X | None
3.15.3(11) | The Resource Entity for an IRR synchronized to the ERCOT System that is capable of providing any net Reactive Power when not producing real power shall: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
3.15.3(11)(e) | Send to ERCOT, via telemetry, an AVR status of “On” when the IRR is synchronized to the ERCOT System, not producing real power, and reactive control is working properly; and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | X | X | None
4.4.4 | DC Tie Schedules | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
4.4.4(8) | A QSE exporting from ERCOT and/or importing to ERCOT through a DC Tie shall: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
4.4.4(8)(b) | Submit e-Tags for all proposed transactions; and | X |  |  | As needed | 15 minutes before the schedule ramps | OATI Encrypted via https; authenticated Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
5.4 | QSE Security Sequence Responsibilities | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
5.4(1) | During the Security Sequence, each Qualified Scheduling Entity (QSE) must: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
5.4(1)(a) | Submit its Current Operating Plan (COP) and update its COP as required in Section 3.9, Current Operating Plan (COP); | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
5.4(1)(e) | Submit an updated COP before 1430 in the Day-Ahead and | X |  |  | As needed | Before 1430 in the Day-Ahead | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
6.4.6 | Resource Status | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
6.4.6(1) | ERCOT shall use the telemetered Resource Status for all applications requiring status of Resources during the Operating Hour, including SCED and Load Frequency Control (LFC). QSEs shall provide ERCOT with accurate telemetry of the current capability of each Resource including the Resource Status, Ancillary Service capability for each Ancillary Service, Ramp Rates, HSL, and LSL. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.4.6(2)(a) | Each QSE shall provide the Real-Time operating status of each Resource to ERCOT by telemetry using the status codes in the COP for Real-Time as described in Section 3.9, Current Operating Plan (COP); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.4.8 | Notification of Forced Outage of a Resource | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
6.4.8(1) | In the event of a Forced Outage of a Resource, the telemetered status of the Resource automatically notifies ERCOT of the event. In the event of a Forced Outage, the telemetered Resource Status shall be changed to the appropriate Off-Line status as soon as practicable but no longer than 15 minutes after the Forced Outage occurs. |  | X | X | As needed | As soon as reasonably practicable but no longer than 15 minutes after the Forced Outage occurs | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | X | X | None
6.4.8(2) | In the event of a Forced Outage or an impending Forced Outage, the Resource Entity or its designee shall inform ERCOT of the following in the Outage Scheduler: | X |  |  | As needed | As soon as reasonably practicable but no longer than 60 minutes after the Forced Outage occurs | Outage Scheduler Encrypted via https; authenticated Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | X | None
6.4.8(2)(a) | Time of expected change in Resource Status or rating; | X |  |  | As needed | As soon as reasonably practicable but no longer than 60 minutes after the Forced Outage occurs | Outage Scheduler Encrypted via https; authenticated Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | X | None
6.4.8(2)(b) | Text message describing the nature of the Forced Outage or de-rating updated as new information becomes available; and | X |  |  | As needed | As soon as reasonably practicable but no longer than 60 minutes after the Forced Outage occurs | Outage Scheduler Encrypted via https; authenticated Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | X | None
6.4.8(2)(c) | The expected minimum and maximum duration of the Forced Outage or de-rating. | X |  |  | As needed | As soon as reasonably practicable but no longer than 60 minutes after the Forced Outage occurs | Outage Scheduler Encrypted via https; authenticated Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | X | X | None
6.4.8(3) | In the event of a Forced Outage, the QSE must update the Resource’s COP as soon as practicable but no longer than 60 minutes after the Forced Outage occurs. | X |  |  | As needed | No later than 60 minutes after the event | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
6.4.8(4) | Each QSE shall timely update the telemetered Resource Status and COP unless in the reasonable judgment of the QSE, such compliance would create an undue threat to safety, undue risk of bodily harm, or undue damage to equipment. The QSE is excused from updating the telemetered Resource Status and/or COP only for so long as the undue threat to safety, undue risk of bodily harm, or undue damage to equipment exists. The time for updating the telemetered Resource Status and/or COP begins once the undue threat to safety, undue risk of bodily harm, or undue damage to equipment no longer exists. | X | X | X | As soon as reasonably practicable and as needed | No later than 60 minutes after the event and as needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP Naming Convention Private WAN point-to-point connection (RTA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.1 | Changes in Resource Status | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
6.5.5.1(1) | Each QSE shall notify ERCOT via telemetry of a change in Resource Status that is not related to a Forced Outage as soon as practicable but no longer than 15 minutes after the change in status occurs and through changes in the Current Operating Plan (COP) as soon as practicable but no longer than 60 minutes after the change in status of the Resource occurs. | X | X | X | As needed / 2 seconds | As soon as practicable but no longer than 15 minutes after the change in status occurs / As soon as practicable but no longer than 60 minutes after the change in status of the Resource occurs. | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.1(2) | When an On-Line Resource is experiencing an event that may affect its availability and/or capability and that requires further actions to stabilize the Resource and/or determine the impact of the event, the QSE may change the Resource Status to ONHOLD within 15 minutes of experiencing an event. Following this Resource Status change, the telemetered HSL and any other applicable telemetry of the Resource as specified in paragraph (2) of Section 6.5.5.2, Operational Data Requirements, shall be updated as soon as practicable but no longer than 15 minutes after the change in Resource Status to ONHOLD. After the QSE has determined the impact of the event, the QSE shall change the Resource Status to its updated status as soon as practicable but no longer than 60 consecutive minutes of being in the ONHOLD status. |  | X | X | As needed / 2 seconds | As soon as practicable but no longer than 15 minutes after the change in Resource Status to ONHOLD. | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.1(3) | Each QSE shall promptly inform ERCOT when the operating mode of the Automatic Voltage Regulator (AVR) or Power System Stabilizer (PSS) for the QSE’s Generation Resource or ESR is changed while the Resource is On-Line. The QSE shall also provide the Resource’s AVR or PSS status logs to ERCOT upon request. For each Generation Resource that is On-Line but not producing real power and is not capable of providing Reactive Power, each QSE must still telemeter its AVR status to ERCOT but is not required to provide verbal notifications of its AVR status changes to ERCOT during these operating conditions. |  | X | X | As needed | As soon as practicable | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.1(4) | Each QSE shall immediately report to ERCOT and the TSP any inability of the QSE’s Generation Resource or ESR required to meet its reactive capability requirements in these Protocols. |  | X | X | As needed | As soon as practicable | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.1(5) | Each QSE shall timely update the telemetered Resource Status unless in the reasonable judgment of the QSE, such compliance would create an undue threat to safety, undue risk of bodily harm, or undue damage to equipment. The QSE is excused from updating the telemetered Resource Status only for so long as the undue threat to safety, undue risk of bodily harm, or undue damage to equipment exists. The time for updating the telemetered Resource Status begins once the undue threat to safety, undue risk of bodily harm, or undue damage to equipment no longer exists. |  | X | X | As needed / 2 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2 | Operational Data Requirements | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
6.5.5.2(2) | A QSE representing a Generation Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time telemetry data to ERCOT for each Generation Resource. | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
6.5.5.2(2)(a) | Net real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered gross real power and conversion constants determined by the Resource Entity and provided to ERCOT through the Resource Registration process. Net real power represents the actual generation of a Resource for all real power dispatch purposes, including use in Security-Constrained Economic Dispatch (SCED), High Dispatch Limit (HDL), and Low Dispatch Limit (LDL), and is consistent with telemetered HSL, LSL, and Frequency Responsive Capacity (FRC); | X | X | X | As needed / 2 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(b) | Gross real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered real power, which may include Supervisory Control and Data Acquisition (SCADA) metering, and conversions constants determined by the Resource Entity and provided to ERCOT through the Resource Registration process; | X | X | X | As needed / 2 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(c) | Gross Reactive Power (in Megavolt-Amperes reactive (MVAr)); | X | X | X | As needed / 2 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(d) | Net Reactive Power (in MVAr); | X | X | X | As needed / 2 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(e) | Power to standby transformers serving plant auxiliary Load; | X | X | X | As needed / 10 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(f) | Status of switching devices in the plant switchyard not monitored by the TSP or DSP affecting flows on the ERCOT Transmission Grid; | X | X | X | As needed / 10 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(h) | Generation Resource breaker and switch status; | X | X | X | As needed / 2 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(i) | HSL (Combined Cycle Generation Resources) shall: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
6.5.5.2(2)(i)(i) | Submit the HSL of the current operating configuration; and |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(i)(ii) | When providing ECRS, update the HSL as needed, to be consistent with Resource performance limitations of ECRS provision; |  |  | X | 2 seconds | As needed | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(j) | For Resources with capacity that is not capable of providing Primary Frequency Response (PFR), the current FRC of the Resource; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(k) | High Emergency Limit (HEL), under Section 6.5.9.2, Failure of the SCED Process; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(l) | Low Emergency Limit (LEL), under Section 6.5.9.2; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(m) | LSL; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(n) | Configuration identification for Combined Cycle Generation Resources; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(o) | For Resources with capacity that is not capable of providing PFR, the high and low limits in MW of the Resource’s capacity that is frequency responsive; |  |  | x | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(p) | For RRS, including any sub-categories of RRS, the physical capability (in MW) of the Resource to provide RRS; |  |  | x | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(q) | For Ancillary Services other than RRS, a blended Normal Ramp Rate (in MW/min) that reflects the physical capability of the Resource to provide that specific type of Ancillary Service; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(r) | Five-minute blended Normal Ramp Rates (up and down);
6.5.5.2(2)(s) | The designated Master QSE of a Generation Resource that has been split to function as two or more Split Generation Resources shall provide Real-Time telemetry for items (a), (b), (c), (d), (e), (g), and (h) above, PSS and AVR status for the total Generation Resource in addition to the Split Generation Resource the Master QSE represents; and |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(2)(t) | The telemetered MW of power augmentation capacity that is not On-Line for Resources that have power augmentation capacity included in HSL. |  |  | x | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(3) | For each Intermittent Renewable Resource (IRR), the QSE shall set the HSL equal to the current net output capability of the facility. The net output capability should consider the net real power of the IRR generation equipment, IRR generation equipment availability, weather conditions, and whether the IRR net output is being affected by compliance with a SCED Dispatch Instruction. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(5) | For each Aggregate Generation Resource (AGR), the QSE shall telemeter the number of its generators online. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(6) | A QSE representing a Load Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time data to ERCOT for each Load Resource and ERCOT shall make the data available, in accordance with ERCOT Protocols, NERC standards and policies, and Governmental Authority requirements, to the Load Resource’s host TSP or DSP at the TSP’s or DSP’s expense. The Load Resource’s net real power consumption, Low Power Consumption (LPC) and Maximum Power Consumption (MPC) shall be telemetered to ERCOT using a positive (+) sign convention: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
6.5.5.2(6)(a) | Load Resource net real power consumption (in MW); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(6)(c) | Load Resource breaker status, if applicable; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(6)(d) | LPC (in MW); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(6)(e) | MPC (in MW); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(6)(f) | The Load Resource’s Ancillary Service self-provision (in MW) for RRS and/or provided via under-frequency relay; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(6)(g) | The status of the high-set under-frequency relay, if required for qualification. The under-frequency relay for a Load Resource providing Non-Spin shall be disabled and the status of that relay shall indicate it as disabled or unarmed; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(6)(h) | For a Controllable Load Resource (CLR) providing Non-Spin, the Scheduled Power Consumption that represents zero Ancillary Service deployments; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(6)(i) | For a single-site CLR with registered maximum Demand response capacity of ten MW or greater, net Reactive Power (in MVAr); |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(6)(j) | Resource Status |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(6)(k) | For an Aggregate Load Resource (ALR) providing Non-Spin, the “Scheduled Power Consumption Plus Two Hours,” representing the QSE’s forecast of the CLR's instantaneous power consumption for a point two hours in the future; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(6)(l) | For an RRS, including any sub-categories of RRS, the next Operating Hour’s current physical capability (in MW) of the Resource to provide RRS; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(6)(m) | For Ancillary Service products other than RRS, a blended Normal Ramp Rate (in MW/min) that reflects the current physical capability of the Resource’s ability to provide a particular Ancillary Service product; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(6)(n) | For a CLR, 5-minute blended Normal Ramp Rates (up and down). |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(9) | A QSE providing any Regulation Service shall provide telemetry indicating the appropriate status of Resources providing Reg-Up or Reg-down, including status indicating whether the Resource is temporarily blocked from receiving Reg-Up and/or Reg-Down deployments from the QSE. This temporary blocking will be indicated by the enabling of the Raise Block Status and/or Lower Block Status telemetry points. |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(9)(a) | Raise Block Status and Lower Block Status are telemetry points used in transient unit conditions to communicate to ERCOT that a Resource’s ability to adjust its output has been unexpectedly impaired. |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | X | X | None
6.5.5.2(9)(e) | The Resource limits and Ancillary Service telemetry shall be updated as soon as practicable. Raise Block Status and Lower Block Status will then be disabled. |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | X | X | None
6.5.5.2(11) | Each QSE shall report the current configuration of combined-cycle Resources that it represents to ERCOT. The telemetered Resource Status for a Combined Cycle Generation Resource may only be assigned a Resource Status of OFF if no generation units within that Combined Cycle Generation Resource are On-Line. |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(12) | A QSE representing Combined Cycle Generation Resources shall provide ERCOT with the possible operating configurations for each power block with accompanying limits. Combined Cycle Train power augmentation methods may be included as part of one or more of the registered Combined Cycle Generation Resource configurations. Power augmentation methods may include: (a) Combustion turbine inlet air cooling methods; (b) Duct firing; (c) Other ways of temporarily increasing the output of Combined Cycle Generation Resources; and (d) For Qualifying Facilities (QFs), an LSL that represents the minimum energy available for Dispatch by SCED, in MW, from the Combined Cycle Generation Resource based on the minimum stable steam delivery to the thermal host plus a justifiable reliability margin that accounts for changes in ambient conditions. | X |  |  | various | As needed | Resource Registration Encrypted via https; authenticated via Digital Certificate | Hypertext Transfer Protocol Secure (HTTPS) | None | None | None | X | None
6.5.5.2(14) | A QSE representing an Energy Storage Resource (ESR) shall provide the following Real-Time telemetry data to ERCOT for each ESR: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
6.5.5.2(14)(a) | Maximum State of Charge (MaxSOC), in MWh; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(14)(b) | Minimum State of Charge (MinSOC), in MWh; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(14)(c) | State of Charge (SOC), in MWh; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(14)(d) | Maximum Operating Discharge Power Limit, in MW; and |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.5.2(14)(e) | Maximum Operating Charge Power Limit, in MW. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.7.1.7 | Real-Time Weather and Dynamic Rating Processor | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
6.5.7.1.12 | Resource Limits | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
6.5.7.1.12(2)(a) | Normal Ramp Rate based on the values telemetered by the QSE to ERCOT, which represents the current ability of the Resource to follow a SCED Base Point instruction; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.7.1.12(2)(b) | Emergency Ramp Rate based on the values telemetered by the QSE to ERCOT; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.7.1.13 | Data Inputs and Outputs for the Real-Time Sequence and SCED | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
6.5.7.1.13(1) | Inputs: The following information must be provided as inputs to the Real-Time Sequence and SCED. ERCOT may require additional information as required, including: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
6.5.7.1.13(1)(a) | Real-Time data from TSPs including status indication for each point if that data element is stale for more than 20 seconds; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | None
6.5.7.1.13(1)(a)(i) | Transmission Electrical Bus voltages; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | None
6.5.7.1.13(1)(a)(ii) | MW and MVAr pairs for all transmission lines, transformers, and reactors; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | None
6.5.7.1.13(1)(a)(iii) | Actual breaker and switch status for all modeled devices; and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | None
6.5.7.1.13(1)(a)(iv) | Tap position for auto-transformers; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | None
6.5.7.1.13(1)(c) | Transmission Element ratings from TSPs; | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
6.5.7.1.13(1)(c)(i) | Data from the Network Operations Model: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
6.5.7.1.13(1)(c)(i)(A) | Transmission lines – Normal, Emergency, and 15-Minute Ratings (MVA); and | X | X | X | As needed | At least 3 months prior to the physical equipment changes | ICCP Naming Convention Private WAN point-to-point connection (RTA) / NOMCR Encrypted via https; authenticated via Digital Certificate (OPA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | X | None | None | None | None
6.5.7.1.13(1)(c)(i)(A) | Transformers and Auto-transformers – Normal, Emergency, and 15-Minute Ratings (MVA) and tap position limits; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | ICCP Naming Convention Private WAN point-to-point connection (RTA) / NOMCR Encrypted via https; authenticated via Digital Certificate (OPA) | Hypertext Transfer Protocol Secure (HTTPS); Point-to-Point Protocol (PPP) | X | None | None | None | None
6.5.7.1.13(1)(c)(ii) | Data from QSEs: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
6.5.7.1.13(1)(c)(ii)(A) | Generator Step-Up (GSU) transformers tap position; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.7.1.13(1)(c)(ii)(B) | Resource HSL (from telemetry); and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.7.1.13(1)(c)(ii)(C) | Resource LSL (from telemetry); and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.7.1.13(1)(d) | Real-Time weather, from Wind-powered Generation Resources (WGRs), and where available from TSPs or other sources. ERCOT may elect to obtain other sources of weather data and may utilize such information to calculate the dynamic limit of any Transmission Element. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | X | None
6.5.7.7 | Voltage Support Service | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
6.5.7.7(6) | Each interconnecting TSP, or the TSP’s agent, shall telemeter via ICCP the Real-Time Voltage Set Point to ERCOT at the Point of Interconnection Bus (POIB) for each Generation Resource and ESRs interconnected to the TSP’s system required to provide VSS. Each interconnecting TSP, or the TSP’s agent shall modify the telemetered Voltage Set Point to match any verbal Voltage Set Point instructions as soon as practicable. ERCOT shall telemeter the Real-Time desired Voltage Set Point and the TSP-designated POIB kV measurement via ICCP to each QSE representing a Generation Resource or an ESR. Each QSE representing a Generation Resource or an ESR shall provide in Real-Time the desired Voltage Set Point and the associated POIB kV measurement provided by ERCOT to the Resource Entity for that Generation Resource or an ESR. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | None
6.5.9.5 | Block Load Transfers between ERCOT and Non-ERCOT Control Areas | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
6.5.9.5(1)(h) | SCADA telemetry on switching devices at BLT points that are deemed necessary by ERCOT to be modeled in the Network Operations Model must be provided by the TSP registering the BLT. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | None

## Data Requirements-Op. Guide
Data and Information Required for Operational Planning Analyses (OPA), Real-time Assessments (RTA), & Real Time Monitoring, & analysis functions | [8 empty] | Entities Responsible for Responding
Section | Specification(s) for data and information | OPA | RTA | RTM | Periodicity | Deadline | Format | Method/Security Protocol | ERCOT Transmission Service Provider (TSP) NERC Transmission Owner (TO) | ERCOT Distribution Service Provider (DSP) NERC Distribution Provider (DP) | ERCOT Resource Entity (RE) NERC Generator Owner (GO) | ERCOT Qualified Scheduling Entity (QSE) NERC Generator Operator (GOP) | ERCOT Transmission Operator (TO) NERC Transmission Operator (TOP)
OG 2.2.5 | Automatic Voltage Regulators | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
OG 2.2.5(1) | A Resource Entity shall immediately notify their QSEs and its interconnecting TO of any change in Automatic Voltage Regulator (AVR) status (i.e., AVR unavailability due to maintenance or failure and when the AVR returns to normal operation). A QSE shall immediately notify ERCOT, via telemetry and verbal notification of any change in AVR status and shall supply AVR status logs to ERCOT upon request per Protocol Section 6.5.5.1, Changes in Resource Status. For each Generation Resource that is On-Line but not producing real power and is not capable of providing Reactive Power, each QSE must still telemeter its AVR status to ERCOT, but is not required to provide verbal notifications of its AVR status changes to ERCOT during these operating conditions. |  | X | X | Immediately upon occurrence | As needed | Phone Point-to-point voice communication and ICCP Naming Convention Private WAN point-to-point connection | WAN Voice / PSTN Voice; WAN; Point-to-Point Protocol (PPP) | None | None | None | X | None
OG 2.2.6 | Power System Stabilizers | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
OG 2.2.6 (2) | Resource Entities shall notify their QSEs of any change in PSS status (e.g. PSS unavailability due to maintenance or failure and when the PSS returns to normal operation). QSEs shall notify ERCOT and the TO at the POI of any change in PSS status and shall supply PSS status logs to ERCOT upon request per Protocol Section 6.5.5.1, Changes in Resource Status. |  | X | X | As soon as reasonably practicable and 2 seconds | As needed and Continuous | Phone Point-to-point voice communication and ICCP Naming Convention Private WAN point-to-point connection | WAN Voice / PSTN Voice; WAN; Point-to-Point Protocol (PPP) | None | None | None | X | None
OG 2.7.3.3 | TO/TSP Responsibilities | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
OG 2.7.3.3(4) | Each TO shall telemeter to ERCOT via ICCP the Real-Time desired Voltage Set Point and actual voltage at the POIB for each Generation Resource or ESR interconnected to its system required to provide VSS. Each TO shall modify the telemetered Voltage Set Point as soon as practicable in order to match any verbal Voltage Set Point instruction issued. |  |  | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | None | X
OG 2.7.3.3(5) | Each TO shall know the status of static transmission Reactive Power resources in its operating area and shall provide such information to ERCOT. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | None | None | None | None | X
OG 2.7.3.4 | QSE Responsibilities | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
OG 2.7.3.4(4) | Each QSE must, as soon as practicable, notify ERCOT, via telemetry and verbal notifications, when a Generation Resource or ESR experiences a change that affects its reactive capability, including any change to the operation mode of the Generation Resource’s or ESR's AVR. For each Generation Resource that is On-Line but not producing real power and is not capable of providing Reactive Power, each QSE must still telemeter its AVR status to ERCOT, but is not required to provide verbal notifications of its AVR status changes to ERCOT during these operating conditions. |  | X | X | As soon as reasonably practicable and 2 seconds |  | Phone Point-to-point voice communication and ICCP Naming Convention Private WAN point-to-point connection | WAN Voice / PSTN Voice; WAN; Point-to-Point Protocol (PPP) | None | None | None | X | None
OG 4.5.3.2 | General Procedures During EEA Operations | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
OG 4.5.3.2 (1)(f) | QSEs shall report when On-Line or available capacity is at risk due to adverse circumstances; |  |  | X | As soon as reasonably practicable | As needed | Phone Point-to-point voice communication | WAN Voice / PSTN Voice | None | None | None | X | None
OG 4.5.3.2 (1)(i) | QSEs shall not remove an On-Line Generation Resource or Energy Storage Resource (ESR) without prior ERCOT authorization unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, QSEs shall immediately inform ERCOT of the need and reason for removing the On-Line Resource from service. |  |  | X | As soon as reasonably practicable | As needed | Phone Point-to-point voice communication | WAN Voice / PSTN Voice | None | None | None | X | None
OG 4.5.3.5 | EEA Termination | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
OG 4.5.3.5(2) | QSEs and TOs shall: | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
OG 4.5.3.5(2)(c) | Report back to the ERCOT System Operator when each level is accomplished; and |  |  | X | As soon as reasonably practicable | As needed | Phone Point-to-point voice communication | WAN Voice / PSTN Voice | None | None | None | X | X
OG 6.2.4 | Protective Relay System Failure Response | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
OG 6.2.4(4) | The affected QSE or TO shall immediately notify the ERCOT Shift Supervisor via phone call and initiate prompt corrective action. These corrective actions are to address reliability issues for the systems that the QSE and TO monitor and/or operate. |  |  | X | As soon as reasonably practicable | As needed | Phone Point-to-point voice communication | WAN Voice / PSTN Voice | None | None | None | X | X
OG 6.2.4(7) | The affected QSE and TO shall promptly notify the ERCOT Shift Supervisor via phone call of the return to service of the previously identified protective relay systems. |  |  | X | As soon as reasonably practicable | As needed | Phone Point-to-point voice communication | WAN Voice / PSTN Voice | None | None | None | X | X
OG 11.2 | Remedial Action Schemes | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
OG 11.2(3)(i) | When a RAS is removed from service, the RAS Entity or a Designated Agent shall immediately notify ERCOT; | X | X | X | Immediately upon occurrence and 2 seconds | As needed | Phone Point-to-point voice communication | WAN Voice / PSTN Voice | X | None | X | X | X
OG 11.2(3)(j) | When a RAS is returned to service, the RAS Entity or its Designated Agent shall immediately notify ERCOT… | X | X | X | Immediately upon occurrence and 2 seconds | As needed | Phone Point-to-point voice communication | WAN Voice / PSTN Voice | X | None | X | X | X
OG 11.2(3)(k) | The RAS Entity shall telemeter the status indication of the following items by SCADA to ERCOT for incorporation into ERCOT systems: |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | X | X | X
OG 11.2(3)(k)(i) | Any automatic or manual arming/activation or operation of the RAS; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | X | X | X
OG 11.2(3)(k)(ii) | The in-service/out-of-service status of the RAS; and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | X | X | X
OG 11.2(3)(k)(iii) | Any additional related telemetry that already exists pertinent to the monitoring of the RAS (e.g. status indication of communications links between associated RAS equipment and the owner’s control center, arming limits of associated RAS equipment); and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | X | X | X
OG 11.3 | Automatic Mitigation Plans | Header | Header | Header |  |  |  |  | Header | Header | Header | Header | Header
OG 11.3 (3)(a) | Immediately notify ERCOT, when an AMP is removed from service and when an AMP is returned to service. ERCOT shall modify its reliability constraints to recognize the availability of the AMP; | X | X | X | Immediately upon occurrence | As needed | Phone Point-to-point voice communication | WAN Voice / PSTN Voice | X | None | None | None | X
OG 11.3 (3)(b) | Telemeter the status indication of the following items by SCADA to ERCOT for incorporation into ERCOT systems | Intro | Intro | Intro |  |  |  |  | Intro | Intro | Intro | Intro | Intro
OG 11.3 (3)(b)(i) | Any automatic or manual arming/activation or operation of the AMP; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | X
OG 11.3 (3)(b)(ii) | In-service/out-of-service status of the AMP; and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | X
OG 11.3 (3)(b)(iii) | Any additional related telemetry that already exists pertinent to the monitoring of the AMP (e.g. status indication of communications links between associated AMP equipment and the owner’s control center, arming limits of associated AMP equipment). |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection | Point-to-Point Protocol (PPP) | X | None | None | None | X

## Revision History
Effective Date | Version | Description and Reason for Change | Author(s)
2017-01-01 | 1 | Initial posting | Yvette Landin, ERCOT Staff
2017-07-03 | 2 | Protocol section 3.8.3 and 3.9.1 updated per NPRR272, Section4.4.4 updated per NPRR 818, OG section updated per NOGRR164. Corrections to protocol and OG numbering, corrections to OPA, RTA and RTM columns, corrections to security protocol columns. | Colleen Frosch, ERCOT Staff
2018-01-30 | 3 | Updated Propose tab, updates per NPRR758, added additional section 3.1.5.1, deleted 4.2.2(1), requesting same data as in 3.13(1), deleted 6.5.7.1.7(1), no data request, added intro sections, corrected various columns. | ERCOT compliance staff
2018-12-07 | 4 | Updated Data Requirements tab, updates per NPRR776, NPRR869, NOGRR167and NOGRR174, and added additional Protocol Section 3.10.7.5.2(8), 3.10.7.3(1)(b), and 6.5.7.7(6), added additional Op Guide Sections 2.7.3.3(4) and 2.7.3.3(5), added intro Sections where necessary, and an administrative edit to Protocol Section 6.5.7.1.13(1)(d). | ERCOT compliance staff
2019-08-14 | 5 | Updated Data Requirements tab, to add section 3.10.7.5.1(1) as it was missed in initial posting; updated per NPRR863 and 901. | ERCOT compliance staff
2020-01-31 | 6 | Updated Data Requirement tab per NPRR889, NPRR849, and NPRR957 | ERCOT compliance staff
2020-07-30 | 7 | Fixed typo 6.5.9.5 (1)(h), updates to section 11 per NOGRR164, updates to section 3 per NPRR953 and NPRR1019. Deleted OP 2.7.5, not used for OPA. | ERCOT compliance staff
2021-04-28 | 8 | Fixed typos on rows 77, 91, 99, and 229-231; Updated RARF (series of spreadsheets) to Resource Registration throughout per NPRR1003 Updated 3.15.3 (4) per NPRR 1001 | ERCOT compliance staff
2021-10-28 | 9 | Removed X's on rows 26, 37, 52, 60, 72, 75, 92, 98, 106, 108, 111, 116, 122, 131, 139, 150, 160, 179, 249 and marked as Intro; Removed row 117, 118, & 244 as the data required is already included; Removed row 68; Row 191, 192, 194, 196-211 updated per NPRR979; Removed RTA designation for rows 272, 274-275, 278-280; Added RTA designation for rows 296-300, and 313 Removed langage "to ensure confidentiality and integrity" from Private WAN point-to-point connection throughout | ERCOT compliance staff
2022-04-29 | 10 | Edit to line 30 per NPRR 1087 Added lines 118 (Header) & 119 Protocol 3.10.6(1) Added line 171 Protcol 3.10.7.2(1) Edit to line 171 per NPRR1016 Edit to line 172 due to protocol renumbering Edit to lines 184, 195, & 314 per NPRR1005 Added line 237 Protocol 6.4.6(2)(a) Added line 278 Protocol 6.5.5.2(7) Edit to line 325 per NOGRR212 | ERCOT compliance staff
2023-02-23 | 11 | Edit to line 3 per NPRR 1084 Protocol 3.1.4.4 Edit to line 7 per NPRR 1084 Protocol 3.1.4.5(2) Added line 8 per NPRR 1084 Protocol 3.1.4.5(3) Added line 9 per NPRR 1084 Protocol 3.1.4.5(5) Edit to line 11 per NPRR 1084 Protocol 3.1.4.7(1) Added line 12 per NPRR 1084 Protocol 3.1.4.7(2) Added line 13 per NPRR 1084 Protocol 3.1.4.7(3) Edit to line 19 per NPRR 1108 Protocol 3.1.6.2(1) Edit to line 25 per NPRR 1084 Protocol 3.1.6.2(1)(f) Edit to lines 33 & 34 per NPRR 1093 Protocols 3.6.1(1)(a)(iii) and 3.6.1(1)(a)(iv) respectively Added line 35 per NPRR 1093 Protocol 3.6.1(1)(a)(v) Added lines 74-75 & 131-151 per NPRR1132 Protocol 3.9 and Protocol 3.10.6(3-5) respectively Added line 93 per NPRR 863 Protocol 3.9.1(5)(b)(i)(L) Renumbered lines 94-98 per NPRR 863 Protocols 3.9.1(5)(b)(i)(M-Q) Edit to line 100 per NPRR 1100 Protocol 3.9.1(5)(b)(ii)(A) Edit to line 103 and 104 per NPRR 1100 Protocol 3.9.1(5)(b)(ii)(D) and 3.9.1(5)(b)(ii)(E) respectively Edit to line 110 per NPRR 1093 Protocol 3.9.1(5)(b)(iii)(E) Added lines 111 & 113 per NPRR 863 Protocols 3.9.1(5)(b)(iii)(F) and 3.9.1(5)(b)(iii)(H) respectively Renumbered line 112 per NPRR 863 Protocol 3.9.1(5)(b)(iii)(F) to 3.9.1(5)(b)(iii)(G) Edit to line 123 per NPRR 863 Protocol 3.9.1(5)(g)(iii) Added line 124 per NPRR 863 Protocol 3.9.1(5)(g)(iv) Renumbered line 125 per NPRR 863 Protocol 3.9.1(5)(g)(iv) to 3.9.1(5)(g)(v) Edit to line 180 per NPRR 973 Protocol 3.10.7.1.4 Edit to line 203 per NPRR 973 Protocol 3.10.7.2(1) Edit to line 261 Removed "and ESR", as this is still gray boxed language Edit to line 299 per NPRR 1093 Protocol 6.5.5.2(5)(c) Edit to line 304 per NPRR 1093 Protocol 6.5.5.2(5)(h) Edit to line 344 per NPRR 1093 Protocol 6.5.7.6.2.3(7) was renumbered to 6.5.7.6.2.3(8) | ERCOT compliance staff
2023-11-16 | 12 | Added lines 14, 15, and 16 per NPRR1085 Protocol 3.1.4.7(4), 3.1.4.7(5), 3.1.4.7(6) Edit to line 30 per administrative change, Protocol 3.1.6.11(1) Added line 37 per NPRR863 Protocol 3.6.1(1)(a)(iv) Edit to lines 38 and 39 - Renumbered per NPRR863 Protocol 3.6.1(1)(a)(v) and 3.6.1(1)(a)(vi) Edit to line 75 per NPRR863 Protocol 3.8.3(1) Edit to line 81 per NPRR1085 Protocol 3.9.1(2) Edit to line 102 per NPRR1085 Protocol 3.9.1(5)(b)(i)(Q) Added line 103 per NPRR1085 Protocol 3.9.1(5)(b)(i)(R) Edit to lines 107 and 108 per NPRR1085 Protocol 3.9.1(5)(b)(ii)(C) and 3.9.1(5)(b)(ii)(D) Edit to lines 115, 116, 126, 127 per NPRR1178 Protocol 3.9.1(5)(b)(iii)(E), 3.9.1(5)(b)(iii)(F), 3.9.1(5)(g)(i), 3.9.1(5)(g)(ii) respectively Edit to line 136 per NPRR1132 Protocol 3.10.6(3) Edit to lines 138-139, 141-142, 144-145, 147-148, 150-151, 153-155 per NPRR1132 Protocols 3.10.6(3)(a - b), 3.10.6(4) Added line 156 per NPRR1132 156 Protocol 3.10.6(5) Edit to line 157 - Renumbered per NPRR1132 Protocol 3.10.6(6) Edit to line 217 – Administrative Change due to spelling correction (Model instead of Mondel; each of instead of eachof) Edit to line 229 – Administrative Change due to spelling correction (providing instead of provideing) Edit to line 232 – Administrative Change due to spelling correction (Estimator requirements instead of Estimatorrequirements) Added lines 268-269 per NPRR 1138 Protocol 3.15.3(9) and 3.15.3(9)(d) Edit to line 277 – Administrative Change due to spelling correction (status instead of staus) Added lines 278-285 per NPRR1085 Protocol 6.4.8(1-4) Edit to line 287 per NPRR1085 Protocol 6.5.5.1(1) Added lines 288 and 290 per NPRR1085 Protocol 6.5.5.1(2) and 6.5.5.1(5) Added line 289 per NPRR1161 Protocol 6.5.5.1(3) Edit to lines 302, 308, 311, 321, 322 per NPRR863 Protocol 6.5.5.2(2)(i)(ii), 6.5.5.2(2)(o), 6.5.5.2(2)(p), 6.5.5.2(5)(f), 6.5.5.2(5)(g) Edit to line 369 – Administrative Change due to spelling correction (and Remedial instead of andRemedial) Edit to line 372 per NOGRR246 Operating Guide 2.2.5(1) Added lines 378-379 per NOGRR246 Operating Guide OG 2.7.3.4(4) Edit to line 390 - Administrative Change OG 11.2(3)(i) | ERCOT compliance staff
2024-06-27 | 13 | Added lines 4-11 Protocols 3.1.4.4(1), 3.1.4.4 (1)(a), 3.1.4.4 (1)(a)(i-iii), 3.1.4.4 (1)(b), 3.1.4.4 (1)(b)(i-ii) Revised Deadline for line 15 - Administrative Change Protocol 3.1.4.5(2) Removed (previously line 57) Protocol 3.7(1) - determined this language is already covered on PR 3.10.6(1) Added lines 39-43 - per NPRR1181 Protocol 3.24, 3.24(1), 3.24(1)(a-b), 3.24(2) Removed (previously lines 82-86) Protocols 3.7.1.2(2), 3.7.1.2(2)(a-d) Added lines 86-90, 93, 95 Protocols 3.9(1), 3.9(4-5), 3.9(7-8), 3.9.1(1), 3.9.1(3) Edit to line 197 - Administrative Change Protocol 3.10.7.1.3(2)(g) Added lines 224 and 225 Protocols 3.10.7.2(2) and 3.10.7.2(3) Removed (previously line 249) Protocol 3.10.7.3(1)(e) Added line 282 - Administrative Change: added header for Section 3.15.3 Added lines 284, 287, 288: Protocol 3.15.3(7), 3.15.3(11), 3.15.3(11)(e) Revised lines 276, 279, 282, 283, 284, 388 - per NPRR989 Protocol 3.15(15), 3.15(16), 3.15.3, 3.15.3(4), 3.15.3(7), 6.5.7.7(6) Edit to lines 285-286 - renumbered per NPRR1026, Protocol 3.15.3(10) and 3.15.3(10)(d) Added lines 292-295 Protocols 5.4, 5.4(1), 5.4(1)(a), 5.4(1)(e) Revised lines 399 and 402 - per NOGRR204, OG 2.7.3.3(4) and OG 2.7.3.4(4) | ERCOT compliance staff
2024-11-21 | 14 | Revised Format & Security Protocol for lines 41-43 Administrative Change Protocols 3.24(1)(a-b), 3.24(2) Added lines 145-148 - per NPRR1186 Protocols 3.9.1(5)(h)(i-iii) Edit to lines 156-175 Format & Security Protocol for Protocols 3.10.6(3)(a)(i-ii), 3.10.6(3)(a)(iii)(A-B), 3.10.6(3)(a)(iv)(A-B), 3.10.6(3)(b)(i-ii), 3.10.6(3)(b)(iii)(A-B), 3.10.6(3)(b)(iv)(A-B), 3.10.6(4-6) Added lines 279-282 - per NPRR1231 Protocols 3.14.5(5)(b), 3.14.5(5)(b)(i), and 3.14.5(5)(b)(ii) Edit to lines 343-344 - per NPRR1186 Protocols 6.5.5.2(2)(q) and 6.5.5.2(2)(r) Added line 345 - per NPRR1186 Protocol 6.5.5.2(2)(s) Edit to lines 359-360 - per NPRR1186 Protocols 6.5.5.2(5)(l) and 6.5.5.2(5)(m) Edit to line 360 - per NPRR1131 Protocol 6.5.5.2(5)(m) Added line 361 - per NPRR1186 Protocol 6.5.5.2(5)(n) Edit to lines 368-370 - per NPRR1186 Protocols 6.5.5.2(12)(a), 6.5.5.2(12)(b), 6.5.5.2(12)(c) Revised line 387 - Administrative Change Protocol 6.5.7.1.13(1)(c)(i) | ERCOT compliance staff
2025-07-01 | 15 | Initial posting for IRO-010-5 and TOP-003-6.1 Added columns I-N, separated data and information into two separate tabs (one for Nodal Protocols the other for Operating Guides) per implementation of NERC Project No. 2021-06 - IRO-010-5/TOP-003-6.1 Removed lines 39-43 - Administrative Change Protocols 3.24(1), 3.24(2) Edit to lines 42-48 – per NPRR1244 Protocols 3.6.1(1)(a)(i-vi); 3.6.1(1)(b) Edit to lines 123-125, 127, 129, 131 – per NPRR1188 Protocols 3.9.1(5)(b)(iii)(D-F); 3.9.1(5)(b)(iii)(H); 3.9.1(5)(c)(i); 3.9.1(5)(d)(i) Edit to line 146 - per NPRR1254 Protocol 3.10.1(3) Added line 147 - per NPRR1254 Protocol 3.10.1(4) Edit to lines 350, 352, 353, 356 – per NPRR1188 Protocols 6.5.5.2(5)(g); 6.5.5.2(5)(i); 6.5.5.2(5)(j); 6.5.5.2(5)(m) | ERCOT compliance staff
2025-12-05 | 16 | Edit to line 49 - per NPRR1007 Protocol 3.6.1(1)(c) Edit to line 77, 78, 79 - per NPRR1007 Protocols 3.8.3(1), 3.8.3(2), 3.8.3(5) Edit to line 90 - per NPRR1007, NPRR1014, NPRR1204 Protocol 3.9.1(3) Removed (previously line 96) - per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(i)(B) Removed (previously line 98) - NPRR1000 Protocol 3.9.1(5)(b)(i)(D) Removed (previously line 100) per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(i)(F) Removed (previously line 101) per NPRR1000, NPRR1007 Protocol 3.9.1(5)(b)(i)(G) Removed (previously line 102) per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(i)(H) Removed (previously line 105) per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(i)(K) Removed (previously line 106) per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(i)(L) Edit to line 101 per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(i)(N) renumbered to (G) Edit to line 102 per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(i)(O) renumbered to (H) Edit to line 103 per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(i)(P) renumbered to (I) Removed (previously line 111) per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(i)(Q) Added line 104 per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(i)(K) Edit to line 105 per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(i)(R) renumbered to (J) Removed (previously line 116) per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(ii)(B) Edit to line 108 per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(ii)(C) renumbered to 3.9.1(5)(b)(ii)(B) Removed (previously lines 121-125) per NPRR1007, NPRR1014 Protocols 3.9.1(5)(b)(iii)(A-E) Removed (previously line) 126 per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(iii)(F) Removed (previously line) 128 per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(iii)(H) Added line 113 per NPRR1007, NPRR1014 Protocol 3.9.1(5)(b)(iii)(B) Edit to line 120 per NPRR1007, NPRR1014 Protocol 3.9.1(5)(g) Removed (previously lines 137-141) per NPRR1007, NPRR1014 Protocols 3.9.1(5)(g)(i)-(v) Edit to line 124 Protocol 3.9.1(5)(h)(iii) per administrative change Edit to line 130 per NPRR1246 Protocol 3.10.6(1) Edit to line 181 per NPRR1246 Protocol 3.10.7.1.4 Edit to line 204 per NPRR1246 Protocol 3.10.7.2(1) Added line 208 Protocol 3.10.7.2(10) per administrative change Edit to line 281 per NPRR1009, NPRR1014 Protocol 5.4(1)(e) Removed (previously lines 303-304) per NPRR1000 Protocols 6.4.2.5 and 6.4.2.5(3)(a) Edit to line 283 per NPRR1010 Protocol 6.4.6(1) Edit to line 296 per NPRR1246 Protocol 6.5.5.1(3) Added line 297 Protocol 6.5.5.1(4), per administrative change Added, removed, and renumbered lines 301-321 per NPRR1010, 1014, 1029 Protocols 6.5.5.2(2)(a) - 6.5.5.2(2)(t) Renumbered lines 323-328 per NPRR1270 Protocols 6.5.5.2(4)-6.5.5.2(5)(e) renumbered to 6.5.5.2(5)-6.5.5.2(6)(e) Edit to lines 329-337 and added lines 366-367 per NPRR1010 and NPRR1029 Protocols 6.5.5.2(5)(f)-6.5.5.2(5)(l) renumbered to 6.5.5.2(6)(f)-6.5.5.2(6)(n) Renumbered lines 338-340 per NPRR1010 and NPRR1029 Protocols 6.5.5.2(7), 6.5.5.2(7)(a), 6.5.5.2(7)(e) renumbered to 6.5.5.2(9), 6.5.5.2(9)(a), 6.5.5.2(9)(e) Edit to line 341 per NPRR1010, NPRR1014, NPRR1029 Protocol 6.5.5.2(9) renumbered to 6.5.5.2(11) Edit made to line 342 Protocol 6.5.5.2(10) renumbered to 6.5.5.2(12), per administrative change Renumbered lines 343-348 per NPRR1010 and NPRR1029 Protocols 6.5.5.2(12), 6.5.5.2(12)(a-e) renumbered to 6.5.5.2(14), 6.5.5.2(14)(a-e) Edit made to lines 351-352 Protocol 6.5.7.1.12(2)(a-b), removed (previously lines 383-384) Protocols 6.5.7.1.12(2)(b)(iii) and 6.5.7.1.12(2)(b)(iv) per NPRR1010 and NPRR1014 , were renumbered accordingly Removed (previously lines 401 and 402) per NPRR1000, NPRR1010, NPRR1246, NPRR1270 Protocols 6.5.7.6.2.3 and 6.5.7.6.2.3(8) Lines were renumbered accordingly where deemed appropriate. Operating Guide changes: Edit made to line 14 per NOGRR268, OG 4.5.3.2 (1)(i) | ERCOT compliance staff
2026-06-29 | 17 | Edit to line 14 (Op. Guide) per NOGRR268, Operating Guide 4.5.3.2(1)(i) Edit to lines 19, 20 per NPRR1287 Protocols 3.1.4.7(1), 3.1.4.7(2) | ERCOT compliance staff