## Slide 1: Long-Term Load Forecast Update Kate Lamb Supervisor Load Forecasting and Analysis June 23, 2026
Key Takeaways
This presentation provides an update on the preliminary 2026 LTLF and key methodology changes. The large-load component will be finalized after Batch Zero data is available.
Outline:
Economic Forecast
Roof-Top Solar Forecast
Electric Vehicle Forecast
Crypto Forecast
Net Outlook
Large Load Forecast Update

## Slide 2: Introduction
ERCOT is in the process of revising the 2026 Long-Term Load Forecast (LTLF) to reflect updated forecast inputs, revised treatment of load response, and the evolving large-load forecasting process.
ERCOT filed a preliminary 2026 LTLF in April and subsequently initiated a process to adjust the forecast pursuant to the process outlined in 16 TAC § 25.370(e)(2)(B).
This update summarizes key changes to the major forecast components, including base economic load, 4CP response, rooftop solar, electric vehicles, crypto load, and large loads.
Following Commission guidance on June 18, large-load values will be updated through the Batch Zero process, with final integration into the LTLF expected after Batch Zero data is available.
Today’s discussion is intended to provide stakeholders with an overview of methodology updates and expected timing for final forecast postings.

## Slide 3: Summer Base Load Forecast and 4CP Response Range
The forecast is built using linear regression models that combine weather, premise data, and calendar effects to capture long‑term load trends.
A Rank‑and‑Average method produces a normal‑weather hourly forecast by ranking hourly values from 15 weather scenarios and averaging them.
These ranked hourly forecasts are then mapped onto a 2022 calendar to create a realistic, time‑sequenced load shape.
Due to higher uncertainty driven by new large-load interconnections and existing large-load response, we developed a forecast range to illustrate the potential impact of 4CP load response. This range reflects historical 4CP behavior and its expected influence on future demand.
Chart: MW
| 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Response Included | 86245 | 87374 | 88974 | 89630 | 90715 | 91842
No Response | 89301 | 90470 | 92127 | 92807 | 93930 | 95098
Key Takeaway: ERCOT developed a base load forecast range to reflect uncertainty around 4CP response, with the no-response case approximately 3.1–3.3 GW higher than the response-included case across 2026–2031.

## Slide 4: Rooftop Solar Forecast Outlook
Key Takeaway: The updated rooftop solar forecast reflects a smaller expected rooftop solar contribution than the prior LTLF, driven by slower expected installation growth and lower expected realized output. Changes to available (federal and state) incentives have made projects less financially attractive, further dampening expected installation growth.
Chart: MW
| 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
2026 Solar Forecast | -1448.7624 | -1681.1606 | -1924.2678 | -2239.4231 | -2580.3791 | -2959.405 | -3397.3725 | -3879.4934 | -4415.9824 | -5012.674 | -5666.9358
Prior LTLF Solar | -1669 | -2220 | -2917 | -3782 | -4841 | -6121 | -7692 | -9546 | -11710 | -14199 | -17027
Year | 2026 Solar Forecast | Prior LTLF Solar
2026 | -1,448 | -1,669
2027 | -1,681 | -2,220
2028 | -1,924 | -2,917
2029 | -2,239 | -3,782
2030 | -2,580 | -4,841
2031 | -2,959 | -6,121
2032 | -3,397 | -7,692
2033 | -3,879 | -9,546
2034 | -4,415 | -11,710
2035 | -5,012 | -14,199
2036 | -5,667 | -17,027

## Slide 5: Electric Vehicle Forecast Summary
Technological advancements and supportive policy measures have contributed to a slight upward adjustment in the EV forecast.
However, persistent challenges such as limited charging infrastructure and high consumer costs continue to constrain growth.
Additionally, the expiration of the federal tax credit has further tempered adoption expectations.
Chart: MW
| 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
2026 Electric Vehicle Forecast | 669.3463 | 896.6077 | 1193.6938 | 1592.7014 | 2121.6105 | 2793.5515 | 3635.3503 | 4674.8942 | 5939.7628 | 7455.4272 | 9243.0395
Prior LTLF EV Forecast | 636 | 852 | 1130 | 1507 | 2007 | 2642 | 3436 | 4417 | 5610 | 7039 | 8723
Key Takeaway: The EV forecast is slightly higher than the prior LTLF, although growth remains moderated by charging infrastructure constraints, vehicle costs, and changes to federal incentives.

## Slide 6: Crypto Forecast Summary
This year, ERCOT is transitioning from the simple linear trend approach used in prior years to a that better captures the complexity of crypto-related load growth.
The updated model will:
Applies more Realistic Growth Expectations
Models price-responsive behavior based on observed historical operations
Uses energization timing and operational behavior as key inputs to improve precision and capture real-world variability.
Chart: MW
| 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
2026 Crypto Forecast | 6055.3078 | 7033.773 | 7802.8255 | 8390.5601 | 8838.3062 | 9182.8046 | 9451.9223 | 9665.6386 | 9838.0725 | 9979.2427 | 10096.3461
Prior LTLF Crypto Forecast | 4944 | 5807 | 6671 | 7535 | 8398 | 9262 | 10125 | 10989 | 11852 | 12716 | 13580
Key Takeaway: The updated crypto forecast uses a fitted growth model and incorporates price-responsive behavior to better reflect observed operational patterns.

## Slide 7: Crypto Response Varies with System Conditions
Crypto load response is modeled based on observed historical operations, with response varying by system conditions. Hot/high-load days receive greater modeled response, while mild/lower-load days receive less or no modeled response. Modeled crypto load reduction is capped at 18%, based on observed summer 2025 non-coincident peak behavior
Key Takeaway: Crypto response is modeled to be higher on hot/high-load days and lower on mild/lower-load days
Chart: MW
High Temperature Day
Mild Temperature Day

## Slide 8: Summer Net Outlook Before Large Load Forecast
The forecast incorporates 4CP demand response. The 2026 peak value was set to align with the Monthly Outlook for Resource Adequacy P50 forecast.
Chart: MW
| 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Base Forecast | 86244.9163 | 87373.8046 | 85903.026 | 86457.5587 | 87569.3256 | 85723.327
Base Econ + EV Forecast | 86905.3855 | 88252.7028 | 87067.0354 | 88006.0719 | 89631.9196 | 88516.8785
Base Econ + EV Forecast + PV Forecast | 86423.3046 | 87701.4256 | 86311.3229 | 87035.7418 | 88523.2885 | 88066.8872
Base Econ + EV Forecast + PV Forecast + Crypto | 87430.5728 | 88900.0413 | 91147.3894 | 92504.3907 | 94322.795 | 95025.8147

## Slide 9: Winter Net Outlook Before Large Load Forecast
Winter peak demand forecasts reflect an upward revision driven by increasingly extreme winter weather events in recent years, as observed across the ERCOT region during recent severe cold snaps
Chart: MW
| 2026-2027 Winter | 2027-2028 Winter | 2028-2029 Winter | 2029-2030 Winter | 2030-2031 Winter | 2031-2032 Winter
Base Forecast | 76911.8416 | 76825.0663 | 78279.297 | 79610.831 | 79185.5322 | 81194.5734
Base Econ + EV Forecast | 77129.3798 | 77115.4965 | 78431.1346 | 80127.7786 | 81566.0874 | 82080.4946
Base Econ + EV Forecast + PV Forecast | 77080.7678 | 77059.9282 | 78366.4019 | 80052.6339 | 81549.3929 | 81981.0021
Base Econ + EV Forecast + PV Forecast + Crypto | 83194.8084 | 84140.8645 | 86205.5308 | 88470.8072 | 90408.2627 | 91180.1941

## Slide 10: Batch Large Load Forecast Update
The Public Utility Commission of Texas approved ERCOT’s Batch Zero Process, enabling the Large Loads identified through the Batch Study Process to be formally incorporated into the Long‑Term Load Forecast (LTLF)
Batch Zero base load data replaces TDSP‑reported large‑load data in the 2026 RTP Compliance Plan, producing an adjusted LTLF that is added to the economic forecast. Although Batch Zero values won’t be confirmed until mid‑August 2026, ERCOT expects the Batch Zero will result in a more realistic forecast.
Finalized LTLF will be posted after the Batch Zero Large Load data has been fully integrated into the forecast

## Slide 11: Thank you!
Kate.Lamb@ercot.com