## Slide 1
DWG Report to ROS
Aditi Upadhyay – DWG Chair
July 9th 2026

## Slide 2
PGRR 122: Reliability criteria for Large Load Loss
Why this matters
Large simultaneous load loss can impact frequency stability and may require IROLs, or other operational constraints.
Existing mitigations:
PGRR115 address consequential load loss with a 1000 MW limit for P1/P7 contingencies.
NOGRR282 address non-consequential load loss through proposed ride-through requirements for LCL
Remaining gap: Existing and near-term LCLs that are exempt from PGRR 115 or NOGRR282 may still create load-loss risk
Transmission solutions will not be effective option to mitigate the risk of loss of load due to lack of voltage ride-through capability.
Stability threshold
3,200 MW
maximum allowable total load loss before frequency instability risk
Applies to
P1, P2, P4, P5, P7 single contingencies
P3-type prior outage + manual adjustment + subsequent contingency
Resolution pathway
When the 3,200 MW threshold is exceeded:
Planning measure
ERCOT and TSPs evaluate transmission solutions that resolve the deficiency with estimated capital cost below $200M.
Interconnection limits
May limit Large Load allocation if criteria cannot be met through transmission solutions.
Operational mitigation
Apply operational mechanisms such as IROLs and real-time curtailment as the backstop.
Next Step: Provide feedback on implementation language before ROS action.
DWG Webex meeting held on 6/25/2026

## Slide 3
ERCOT 2026/27 DWG Flat Start update:
Major process change:
Pass 0 will use June SSWG seed cases for DWG review but the October SSWG cases will be the basis for the final 2027 DWG flat start cases set.
ERCOT will not accept additional TSP transmission topology, load, or generation updates during DWG flat start development; those changes must be coordinated through SSWG before October cases are published.
The process will transition to PSSE v36 .5(Market Notice W- A050225-01)
DWG Approved:
PGRR 144 Dynamic Model Submission and Review Requirements for Large Loads
DWG Procedure Manual update for MOD-026-2