| NPRR Number | 1308 | NPRR Title | Board Priority - Related to NOGRR282, Large Computational Load Ride-Through Requirements |
| --- | --- | --- | --- |
| Date of Decision |  | July 9, 2026 |  |
| Action |  | Approved |  |
| Timeline |  | Urgent – On 12/8/25, the Board designated Nodal Protocol Revision Request (NPRR) 1308 a Board Priority Revision Request. |  |
| Estimated Impacts |  | Cost/Budgetary: None Project Duration: No project required |  |
| Effective Date |  | August 1, 2026 |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Nodal Protocol Sections Requiring Revision |  | 2.1, Definitions 2.2, Acronyms and Abbreviations |  |
| Related Documents Requiring Revision/Related Revision Requests |  | NOGRR282 |  |
| Revision Description |  | This NPRR defines Large Computational Load (LCL). |  |
| Reason for Revision |  | Strategic Plan Objective 1 – Be an industry leader for grid reliability and resilience Strategic Plan Objective 2 - Enhance the ERCOT region’s economic competitiveness with respect to trends in wholesale power rates and retail electricity prices to consumers Strategic Plan Objective 3 - Advance ERCOT, Inc. as an independent leading industry expert and an employer of choice by fostering innovation, investing in our people, and emphasizing the importance of our mission General system and/or process improvement(s) Regulatory requirements ERCOT Board/PUCT Directive (please select ONLY ONE – if more than one apply, please select the ONE that is most relevant) |  |
| Justification of Reason for Revision and Market Impacts |  | The LCL definition is needed to differentiate this type of load from other types of Large Loads. Due to the unique characteristics of LCLs, they require specific rules, such as frequency and voltage ride-through requirements. |  |
| PRS Decision |  | On 12/10/25, PRS voted unanimously to table NPRR1308 and refer the issue to ROS. All Market Segments participated in the vote. On 4/15/26, PRS voted to recommend approval of NPRR1308 as amended by the 4/13/26 ERCOT comments and to forward to TAC NPRR1308 and the 11/14/25 Impact Analysis. There was one opposing vote from the Consumer (Occidental) Market Segment. All Market Segments participated in the vote. |  |
| Summary of PRS Discussion |  | On 12/10/25, ERCOT Staff provided an overview of NPRR1308. Participants requested additional review by ROS alongside the related NOGRR282. On 4/15/26, participants noted the ROS endorsement of NPRR1308 and reviewed the 4/13/26 ERCOT comments. |  |
| TAC Decision |  | On 4/29/26, TAC voted to recommend approval of NPRR1308 as recommended by PRS in the 4/15/26 PRS Report. There were two opposing votes from the Consumer (2) (Air Liquide, CMC Steel) Market Segment and four abstentions from the Consumer (City of Dallas), Cooperative (GSEC), Independent Generator (Vistra), and Independent Retail Electric Provider (IREP) (Demand Control 2) Market Segments. All Market Segments participated in the vote. |  |
| Summary of TAC Discussion |  | On 4/29/26, ERCOT staff presented on the history of NPRR1308/NOGRR282 and participants discussed ride-through exemptions under NOGRR282 and the potential for shifting the exemption date from November 2025 to July 2026. |  |
| Explanation of Opposing TAC Votes |  | Consumer/Air Liquide – Explanation requested but not provided Consumer/CMC Steel – Explanation requested but not provided |  |
| TAC Review/Justification of Recommendation |  | Revision Request ties to Reason for Revision as explained in Justification Impact Analysis reviewed and impacts are justified as explained in Justification Opinions were reviewed and discussed Comments were reviewed and discussed (if applicable) Other: (explain) |  |
| ERCOT Board Decision |  | On 6/2/26, the ERCOT Board voted unanimously to recommend approval of NPRR1308 as recommended by TAC in the 4/29/26 TAC Report. |  |
| PUCT Decision |  | On 7/9/26, the PUCT approved NPRR1308 and accompanying ERCOT Market Impact Statement as presented in Project No. 54445, Review of Protocols Adopted by the Independent Organization. |  |

| Opinions |  |
| --- | --- |
| Credit Review | ERCOT Credit Staff and the Credit Finance Sub Group (CFSG) have reviewed NPRR1308 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |
| Independent Market Monitor Opinion | IMM has no opinion on NPRR1308. |
| ERCOT Opinion | ERCOT supports approval of NPRR1308. |
| ERCOT Market Impact Statement | ERCOT Staff has reviewed NPRR1308 and believes the market impact for NPRR1308, along with NOGRR282, provides necessary requirements to reduce the reliability risk posed by LCLs unexpectedly tripping or transferring to backup generation when frequency and voltage excursions within a specified range occur. Without these requirements, events involving LCL loss would increase in magnitude, potentially leading to system frequency and voltage instability. |

| Sponsor |  |
| --- | --- |
| Name | Patrick Gravois |
| E-mail Address | Patrick.Gravois@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4695 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Cory Phillips |
| E-Mail Address | cory.phillips@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Google 120425 | Presented discussion topics related to NPRR1308 and system operating limits |
| ERCOT 121025 | Responded to the 12/4/25 Google comments |
| ROS 010826 | Requested PRS continue to table NPRR1308 |
| Data Center Coalition 020926 | Raised concerns with the proposed definition within NPRR1308 |
| ROS 040826 | Endorsed NPRR1308 as submitted |
| ERCOT 041326 | Replaced uses of “Large Electronic Load (LEL)” with “Large Computational Load (LCL)” to avoid conflicts with the existing term, Low Emergency Limit (LEL) |

Market Rules Notes

None

Proposed Protocol Language Revision

## 2.1	DEFINITIONS

## Large Load

One or more Facilities at a single site with an aggregate peak Demand greater than or equal to 75 MW behind one or more common Points of Interconnection (POIs) or Service Delivery Points.

### Large Computational Load (LCL)

A Large Load in which 50% or greater of the Demand at the site consists of power electronic based load, specifically computational load, such as data centers and cryptocurrency mining facilities.

## 2.2	ACRONYMS AND ABBREVIATIONS

LCL	Large Computational Load