## Slide 1: ERCOT Frequency Events June 2026 ERCOT Operations Planning PDCWG Meeting July 22, 2026

## Slide 2: 6/1/2026 18:39:15 (Non-FME)
Notes: A combine cycle tripped in steps for a combine loss of approximately ~556 MW
Starting Frequency: 60.018 Hz
Minimum Frequency: 59.976 Hz
A-C Time : 4 seconds
Recovery Time(back to deadband): 0 minutes 16 seconds
Trip Reason: Unknown at this time.
Contextual Information: A total of 238 MW of regulation Up was deployed during the event.
Reason for no selection: Unit trip was not clean

## Slide 3: 6/5/2026 7:39:19 (Non-FME)
Notes: A unit tripped offline for ~453 MW
Starting Frequency: 60.018 Hz
Minimum Frequency: 59.968 Hz
A-C Time : 5 seconds
Recovery Time(back to deadband): 1 minutes 06 seconds
Trip Reason: Unknown at this time.
Contextual Information: A total of 68 MW of regulation Up was deployed during the event.
Reason for no selection: A-B frequency too small

## Slide 4: 6/5/2026 23:54:58 (Non-FME)
Notes: A unit tripped offline while experiencing a runback for ~670 MW
Starting Frequency: 60.008 Hz
Minimum Frequency: 59.953 Hz
A-C Time : 10 seconds
Recovery Time(back to deadband): 4 minutes 0 seconds
Trip Reason: Unknown at this time.
Contextual Information: A total of 331 MW of regulation Up was deployed during the event.
Reason for no selection: Unit experienced a runback

## Slide 5: 6/6/2026 8:23:20 (FME)
Notes: A unit tripped offline for ~708 MW
Starting Frequency: 60.017 Hz
Minimum Frequency: 59.950 Hz
A-C Time : 4 seconds
Recovery Time(back to deadband): 4 minutes 29 seconds
Trip Reason: Unknown at this time
Contextual Information: A total of 336 MW of regulation Up and 400 MW of manual offset was deployed during the event.

## Slide 6: 6/14/2026 9:29:42 (Non-FME)
Notes: A unit tripped offline for ~757 MW
Starting Frequency: 59.983 Hz
Minimum Frequency: 59.954 Hz
A-C Time : 2 seconds
Recovery Time(back to deadband): 3 minutes 22 seconds
Trip Reason: Unknown at this time
Contextual Information: A total of 381 MW of regulation Up was deployed during the event.
Reason for no selection: A-B frequency too small

## Slide 7: 6/17/2026 23:25:00 (Non-FME)
Notes: A unit tripped offline for ~1305 MW
Starting Frequency: 59.998 Hz
Minimum Frequency: 59.925 Hz
A-C Time : 3 seconds
Recovery Time(back to deadband): 5 minutes 16 seconds
Trip Reason: Unknown at this time
Contextual Information: A total of 375 MW of regulation Up and 400 MW of manual offset was deployed during the event.
Reason for no selection: A-B frequency too small

## Slide 8: 6/18/2026 15:25:45 (Non-FME)
Notes: A unit tripped offline for ~588 MW
Starting Frequency: 60.017 Hz
Minimum Frequency: 59.961 Hz
A-C Time : 4 seconds
Recovery Time(back to deadband): 3 minutes 24 seconds
Trip Reason: Unknown at this time
Contextual Information: A total of 264 MW of regulation Up and 300 MW of manual offset was deployed during the event.
Reason for no selection: A-B frequency too small

## Slide 9: 6/20/2026 22:58:50 (Non-FME)
Notes: A unit tripped offline for ~448 MW
Starting Frequency: 60.002 Hz
Minimum Frequency: 59.964 Hz
A-C Time : 3 seconds
Recovery Time(back to deadband): 3 minutes 29 seconds
Trip Reason: Unknown at this time
Contextual Information: A total of 253 MW of regulation Up was deployed during the event.
Reason for no selection: A-B frequency too small

## Slide 10: 6/23/2026 9:15:20 (Non-FME)
Notes: Multiple combine cycles tripped offline for a combine loss of approximately ~710 MW
Starting Frequency: 59.99 Hz
Minimum Frequency: 59.963 Hz
A-C Time : 2 seconds
Recovery Time(back to deadband): 8 minutes 32 seconds
Trip Reason: Lightning strike
Contextual Information: A total of 632 MW of regulation Up and 400 MW of manual offset was deployed during the event.
Reason for no selection: A-B frequency too small

## Slide 11: 6/23/2026 16:45:31 (Non-FME)
Notes: Multiple combine cycles tripped offline for a combine loss of approximately ~400 MW
Starting Frequency: 59.975 Hz
Minimum Frequency: 59.958 Hz
A-C Time : 3 seconds
Recovery Time(back to deadband): 7 minutes 30 seconds
Trip Reason: Electrical issues on site
Contextual Information: A total of 800 MW of regulation Up was deployed during the event.
Reason for no selection: A-B frequency too small. Event occurred below deadband.

## Slide 12: Questions/Comments?