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[bookmark: _Toc235457750]Report Highlights 
The unofficial ERCOT peak load for June 2026 was 82,772 MW and occurred on 06/18/2026 during hour ending 17:00, this is 5,376 MW higher than the June 2025 peak demand of 77,396 MW on 06/19/2025
There were 10 frequency events.
There were no events which required automatic/manual deployment of Load Resources that were controlled by an Under-Frequency Relays.
There were 0 OCNs
There were 9 Advisories – All for ERCOT has postponed the deadline for the posting of the DAM solution for Operating Days: 06/07/26, 06/10/26, 06/11/26, 06/18/26, 06/19/26, 06/21/26, 06/24/26, 06/25/26, and 07/01/26 due to long solution run time.
There was 0 Watches.
There were 0 Emergency Notices.
There were 73 RUC commitments.
A Wind Generation Record of 29,031 MW was set on 06/29/2026 at 02:00.
A Renewable Generation Record of 52,063 MW was set on 06/27/2026 at 12:47.
The following GTCs saw congestion in June: 
	GTC
	Days Congestion

	East Texas
	22

	Nelson Sharpe - Rio Hondo
	20

	North - Houston
	20

	West Texas
	18

	North Edinburg - Lobo
	18

	South Texas Export Pawnee - Spruce
	16

	Panhandle
	12

	South Texas Export Pawnee - Tango
	11

	McCamey
	8

	Zapata Starr
	4

	Treadwell
	2

	Valley Export
	2

	Kinney
	1

	South Texas Import Katoen - Lonhill
	1





[bookmark: _Toc235457751]Frequency Control
[bookmark: _Toc235457752]Frequency Events
The ERCOT Interconnection experienced 10 frequency events.
A summary of the frequency events is provided below. The reported frequency events meet one of the following criteria: Delta Frequency is 60 mHz or greater; the MW loss is 350 MW or greater; resource trip event triggered ECRS deployment. Frequency events that have been identified as Frequency Measurable Events (FME) for purposes of BAL-001-TRE-2 analysis are highlighted in blue. When analyzing frequency events, ERCOT evaluates PMU data according to industry standards. Events with an oscillating frequency of less than 1 Hz are inter-area, while higher frequencies indicate local events. Industry standards specify that damping ratio for inter-area oscillations should be 3.0% or greater. For the frequency event listed below, the ERCOT system met these standards and transitioned well after the disturbance. In the case of negative delta frequency, the MW Loss column could refer to load loss.

	Date and Time
	Delta Frequency
	Max/Min Frequency
	[bookmark: RANGE!D1]Duration of Event
	[bookmark: RANGE!E1]PMU Data 
	MW Loss
	Load
	IRR
	Inertia

	
	[bookmark: RANGE!B2](Hz)
	(Hz)
	
	Oscillation Mode (Hz)
	Damping Ratio
	
	(MW)
	% 
	[bookmark: RANGE!J2](MW-s)

	6/1/2026 18:39:15
	0.040
	59.976
	00:04:33
	0.47
	14%
	556
	    78,073 
	42%
	  310,775 

	6/5/2026 7:39:19
	0.049
	59.969
	00:01:36
	0.67
	11%
	453
	    53,778 
	21%
	  283,413 

	6/5/2026 23:54:58
	0.052
	59.954
	00:04:10
	0.52
	5%
	670
	    55,242 
	16%
	  284,707 

	6/6/2026 8:23:20
	0.057
	59.950
	00:04:50
	0.79
	12%
	708
	    51,991 
	18%
	  280,207 

	6/14/2026 9:29:42
	0.029
	59.953
	00:03:46
	0.67
	13%
	757
	    58,154 
	38%
	  294,010 

	6/17/2026 23:25:00
	0.063
	59.928
	00:05:27
	0.58
	6%
	1305
	    65,608 
	37%
	  301,016 

	6/18/2026 15:25:45
	0.054
	59.961
	01:05:27
	0.61
	12%
	588
	    82,184 
	51%
	  299,663 

	6/20/2026 22:58:50
	0.026
	59.964
	02:05:27
	0.56
	8%
	448
	    61,618 
	35%
	  294,281 

	6/23/2026 9:15:20
	0.046
	59.964
	03:05:27
	0.26
	11%
	710
	    64,225 
	53%
	  278,149 

	6/23/2026 16:45:31
	0.021
	59.957
	04:05:27
	0.55
	10%
	400
	    81,704 
	52%
	  286,117 



    [image: ]
[bookmark: _Toc90113254][bookmark: _Toc90367425](Note: All data on this graph encompasses frequency event analysis based on BAL-001-TRE-2.)

[bookmark: _Toc235457753]Automatic/Manual Load Resource Deployments
	Resource Location
	# of Resources
	Operating Day
	Total # of Hours Committed
	Total MWhs 
	Reason for Commitment
	MWs of ECRS Deployed 
	MWs of RRS Deployed 

	
	
	
	
	
	
	
	



There were no events which required automatic/manual deployment of Load Resources that were controlled by an Under-Frequency Relays.

[bookmark: _Toc235457754]Reliability Unit Commitment
ERCOT reports on Reliability Unit Commitments (RUC) monthly. Commitments are reported grouped by operating day and weather zone. The total number of hours committed is the sum of the hours for all the units in the specified region. Additional information on RUC commitments can be found on the MIS secure site at Grid  Generation  Reliability Unit Commitment.
There were 73 RUC commitments.
	Resource Location
	# of Resources
	Operating Day
	Total # of Hours Committed
	 Total MWhs 
	Reason for Commitment

	NORTH_CENTRAL 
	4
	June 1, 2026
	20
	         2,184.0 
	 System Capacity 

	 NORTH_CENTRAL 
	3
	June 2, 2026
	24
	         1,536.0 
	 DCDHTVW5 

	 NORTH_CENTRAL 
	1
	June 3, 2026
	4
	            956.0 
	 System Capacity 

	 COAST, NORTH_CENTRAL 
	4
	June 6, 2026
	23
	         2,459.5 
	 System Capacity 

	 EAST, NORTH, NORTH_CENTRAL 
	3
	June 9, 2026
	13
	         4,664.9 
	 SHC2EXC5 

	 NORTH, NORTH_CENTRAL, SOUTH_CENTRAL 
	3
	June 10, 2026
	14
	         4,225.2 
	 SHC2EXC5, SHCKEXC5 

	 EAST, NORTH_CENTRAL 
	3
	June 14, 2026
	13
	         4,328.0 
	 System Capacity 

	 EAST, NORTH_CENTRAL 
	4
	June 15, 2026
	19
	         6,385.0 
	 System Capacity 

	 EAST, NORTH, NORTH_CENTRAL 
	6
	June 16, 2026
	26
	         8,738.0 
	 SCRDJON5, System Capacity 

	 EAST, NORTH_CENTRAL, SOUTHERN 
	9
	June 18, 2026
	47
	       12,600.0 
	 SCRDJON5, SHC2EXC5, System Capacity 

	 COAST, EAST, NORTH_CENTRAL 
	12
	June 19, 2026
	127
	       34,846.0 
	 System Capacity 

	 NORTH_CENTRAL 
	1
	June 20, 2026
	7
	         3,976.0 
	 System Capacity 

	 EAST, NORTH, NORTH_CENTRAL 
	9
	June 22, 2026
	50
	       14,577.8 
	 E_PASP, System Capacity 

	 NORTH_CENTRAL 
	1
	June 23, 2026
	4
	         1,568.0 
	 SHC2EXC5 

	 NORTH, NORTH_CENTRAL 
	6
	June 24, 2026
	44
	         4,629.1 
	 SHC2EXC5 

	 EAST, NORTH, NORTH_CENTRAL 
	3
	June 29, 2026
	13
	         4,485.9 
	 SHC2EXC5, SHCKEXC5 

	 NORTH_CENTRAL 
	1
	June 30, 2026
	8
	            967.0 
	 SHC2EXC5 





[bookmark: _Toc235457755]IRR, Wind, and Solar Generation as a Percent of Load
[bookmark: _Hlk83634375]The graph below shows the maximum, minimum and average aggregate solar, wind and IRR output as a percentage of total ERCOT load when evaluated as 10-minute averaged intervals, over the past 13 months. Current wind and solar generation and penetration records are listed in the footnote below[footnoteRef:2]. Maximum IRR penetration for June 2026 was 76.88% on 6/28/2026 interval ending 09:40 and minimum IRR penetration for June 2026 was 3.97%on 6/16/2026 interval ending 06:20. [2:  Current Wind Generation Record: 29,011 MW on 05/18/2026 at 00:01 | Current Wind Penetration Record: 69.15% on 04/10/2022 at 01:43
  Current Solar Generation Record: 33,981 MW on 05/13/2026 at 12:43 | Current Solar Penetration Record: 72.74% on 05/02/2026 at 11:28] 


[image: ]

During the hour of peak load for the month, hourly integrated wind generation was 12,576 MW and solar generation was 27,353 MW. The graph below shows the wind and solar penetration percentage during the hour of the peak load in the last 13 months.

    [image: ]

Lastly, the graph below shows the minimum wind, solar, and IRR output during the peak load hour as a percentage of the daily peak load for every day in the month.

[image: ]


[bookmark: _Toc235457756][bookmark: _Hlk80277108][bookmark: _Hlk130892461]Largest Net-Load Ramps
The net-load ramp is defined as the change in net-load (load minus wind and PVGR generation) during the defined time horizon. Such a variation in net-load needs to be accommodated in grid operations to ensure that the reliability of the grid is satisfactorily maintained. The largest net-load ramps over 5-minute, 10-minute, 15-minute, 30-minute, and 60-minute intervals in June 2026 were 1,891 MW, 2,649 MW, 3,976 MW, 6,380 MW, and 11,157 MW respectively. A comparison with historical values is provided in the table below.
	Month and Year
	5 min
	10 min
	15 min
	30 min
	60 min

	Jun-15
	1,038 MW
	1,771 MW
	2,489 MW
	3,119 MW
	5,360 MW

	Jun-16
	1,183 MW
	1,716 MW
	2,148 MW
	3,131 MW
	5,975 MW

	Jun-17
	751 MW
	1,287 MW
	1,772 MW
	3,106 MW
	5,573 MW

	Jun-18
	1,029 MW
	1,413 MW
	2,035 MW
	3,590 MW
	6,320 MW

	Jun-19
	824 MW
	1,284 MW
	1,706 MW
	2,985 MW
	5,684 MW

	Jun-20
	902 MW
	1,615 MW
	2,340 MW
	3,726 MW
	7,015 MW

	Jun-21
	1,442 MW
	2,157 MW
	2,646 MW
	3,468 MW
	5,963 MW

	Jun-22
	1,064 MW
	1,588 MW
	2,166 MW
	4,035 MW
	7,866 MW

	Jun-23
	1,044 MW
	1,672 MW
	2,316 MW
	4,075 MW
	7,845 MW

	Jun-24
	1,978 MW
	2,883 MW
	3,466 MW
	4,547 MW
	7,498 MW

	Jun-25
	1,653 MW
	2,416 MW
	3,334 MW
	5,516 MW
	10,007 MW

	Jun-26
	1,891 MW
	2,649 MW
	3,976 MW
	6,380 MW
	11,157 MW

	
	6/11/2026
	6/11/2026
	6/11/2026
	6/24/2026
	6/24/2026

	
	(IE 19:14)
	(IE 19:17)
	(IE 19:24)
	(IE 19:28)
	(IE 19:39)

	All Months in 2015-2026
	3,797 MW
	3,901 MW
	5,018 MW
	9,696 MW
	18,089 MW

	
	5/28/2025
	5/3/2026
	2/24/2025
	2/24/2025
	4/6/2026

	
	(IE 10:27)
	(IE 18:40)
	(IE 17:39)
	(IE 17:51)
	(IE 19:17)





[bookmark: _Toc235457757]Congestion Analysis
[bookmark: _Toc235457758]Notable Constraints
[bookmark: _Hlk92804220]Nodal protocol section 3.20 specifies that ERCOT shall identify transmission constraints that are binding in Real-Time three or more Operating Days within a calendar month. As part of this process, ERCOT reports congestion that meets this criterion to ROS. In addition, ERCOT also highlights notable constraints that have an estimated congestion rent exceeding $1,000,000 for a calendar month. These constraints are detailed in the table below, including approved transmission upgrades from TPIT that may provide some congestion relief based on ERCOT’s engineering judgement. Rows highlighted in blue indicate the congestion was affected by one or more outages. For a list of all constraints activated in SCED, please see Appendix A at the end of this report.

	Data Item1
	Contingency Name
	Overloaded Element
	Contingency Name
	Overloaded Element
	# of Days Constraint Binding
	Congestion Rent
	Transmission Project

	
	
	
	
	
	
	
	
	

	n/a_n/a_WESTEX
	BASE CASE
	WESTEX
	Basecase
	WESTEX GTC
	16
	$24,599,695.49
	Permian Basin Reliability Plan (765-kV import paths) (The PUCT approved ,helps improve, but not fully exit, the GTC yet.)

	HCKSW_EXCSW_107__B
	SHC2EXC5
	107__B
	HICKS SWITCH to EXCHANGE SWITCH LIN _C
	Hicks Switch - Exchange Switch 345kV
	17
	$11,305,932.80
	 

	STP_WAP_STPWAP39_1
	DWPWFWP5
	STPWAP39_1
	TWR(345) WAP-WLF64 & WAP-WLY72
	South Texas Project - Wa Parish 345kV
	17
	$9,197,686.14
	 

	TREADWEL_YELWJCKT_TREADW_YELWJC1_1
	DBIGKEN5
	TREADW_YELWJC1_1
	Bighil-Kendal 345kV
	Yellow Jacket - Treadwell 138kV
	21
	                 6,773,732.89 
	 

	MDO_PHR_MDOPHR99_A
	DWAP_OB5
	MDOPHR99_A
	TWR (345) OB-WAP98 & OB-WAP99
	Meadow - Ph Robinson 345kV
	14
	                 6,423,280.32 
	CNP_28TPIT103344_PH_Robinson_to_WA_Parish_Hardening (MOD 103344 Phase 103435, 25RPG028)

	ZEN_THW_THWZEN98_A
	DRNS_TB5
	THWZEN98_A
	Rns-Rtw & Sng-Tb 345kV
	Th Wharton - Zenith 345kV
	15
	                 5,789,582.08 
	 

	HHGT_OMEGA_HHGTOM_1
	BASE CASE
	HHGTOM_1
	Basecase
	Omega - Horse Hollow Generation Tie 345kV
	14
	                 4,476,204.86 
	 

	CMNSW_CMNTP_651__B
	SCMNCPS5
	651__B
	COMANCHE SWITCH (Oncor) to COMANCHE PEAK SES LIN _A
	Comanche Tap - Comanche Switch (Oncor) 138kV
	16
	                 4,411,731.13 
	 

	LNGSW_PRLSW_6965__A
	DBAKCED5
	6965__A
	BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV
	Longshore Switch - Prairieland Switch 345kV
	12
	                 4,295,502.41 
	Oncor_FW_81268_Longshore – Consavvy 345 kV Double-Circuit Line Rebuild (MOD 81268, 23RPG034)

	SAMSW_VENSW_35055__A
	SVENFTS5
	35055__A
	FORT SMITH SWITCH to FORT SMITH SWITCH LIN _B
	Sam Switch - Venus Switch 345kV
	7
	$4,139,470.13
	Rebuild Sam Switch - Venus Switch 345 kV DCKT (78369)

	MGSES_CATSW_6945__A
	SRGRMGS5
	6945__A
	MORGAN CREEK SES to RANGER CAMP SWITCH LIN _A
	Morgan Creek Ses - Cattleman Switch 345kV
	12
	$4,112,471.33
	West Texas 345-kV Infrastructure Rebuild Project (23RPG034)

	MDO_PHR_MDOPHR99_A
	DPHRCTR5
	MDOPHR99_A
	Ctr-Phr&Cby 345kV
	Meadow - Ph Robinson 345kV
	19
	$3,956,968.83
	CNP_28TPIT103344_PH_Robinson_to_WA_Parish_Hardening (MOD 103344 Phase 103435, 25RPG028)

	n/a_n/a_NE_LOB
	BASE CASE
	NE_LOB
	Basecase
	NE_LOB GTC
	15
	$3,748,214.22
	San Antonio South Reliability I Project (22RPG048)
LRGV Transmission Improvement Project (21RPG017)
San Antonio South Reliability II Project (23RPG032)

	SCRCV_KNAPP_6437__F
	DMTSCOS5
	6437__F
	DMTSW TO SCOSW 345 DBLCKT
	Knapp - Scurry Chevron 138kV
	23
	$3,532,632.19
	Oncor_FW_102849_Union 138 kV Switch (MOD 102849)

	BCKSW_CGRSW_6215__A
	DSCOTKW5
	6215__A
	SCOSW TO TKWSW 345 DBLCKT
	Bluff Creek Switch - China Grove Switch 138kV
	14
	$3,343,071.80
	 

	TMPSW_FRYSW_1715__B
	DSALHUT5
	1715__B
	SALSW - HUTTO 345KV
	Temple Switch - Fryers Creek 138kV
	10
	$3,199,619.59
	ONCOR_SE_87677_Fryers_Creek_Temple_138 kVLine (MOD 87677)

	SALDS_SONTERRA_1710__A
	DSALHUT5
	1710__A
	SALSW - HUTTO 345KV
	Salado South - Sonterra 138kV
	8
	$2,854,510.16
	 

	WLVSW_GAILS_6217__A
	SVEAW_L5
	6217__A
	wett_long_draw to VEALMOOR - Sharyland Utilities LIN 1
	Willow Valley Switch - Gail Sub 138kV
	17
	$2,769,950.60
	 

	TWINBU_HARGROVE_HARGRO_TWINBU1_1
	DBAKCED5
	HARGRO_TWINBU1_1
	BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV
	Hargrove - Twin Buttes 138kV
	6
	$2,727,482.14
	 

	SEA_SEA_SEA_AAT1
	DFRYBC58
	SEA_AAT1
	DOUBLE KNBSW-SALSW 345 & FRYSW-BELCNTY 138
	Seaton 138kV
	3
	$2,533,065.50
	 

	ODEHV_ODEHV_ODEHV_MR3H
	DODEMOS5
	ODEHV_MR3H
	ODEHV-MOSSW 345&ODEHV-WLFSW 345_DBLCKT
	Odessa Ehv Switch 345kV
	1
	$2,434,265.25
	 

	LPLMK_LPLNE_LPLMK_LPLNE_1
	SBWDDBM5
	LPLMK_LPLNE_1
	BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1
	Mackenzie Substation - Northeast Substation 115kV
	18
	$2,404,826.67
	 

	n/a_n/a_NELRIO
	BASE CASE
	NELRIO
	Basecase
	NELRIO GTC
	19
	$2,116,049.89
	The Lower Rio Grande Valley (LRGV) System Enhancement Project (21RPG017) 

	BRTSW_JUNPR_12020__B
	DLONPK25
	12020__B
	DBL_PKRSW-GRSES_PKRSW-LONSW_345KV
	Barton Chapel Wind Farm - Juniper Sub 138kV
	11
	$1,962,717.99
	 

	GN_PZ_GN_PZ_08_A
	SMDOOAS5
	GN_PZ_08_A
	MEADOW to OASIS LIN A
	Grant - Plaza 138kV
	11
	$1,891,074.10
	 

	GRSES_GRMES_6375__A
	DLONPK25
	6375__A
	DBL_PKRSW-GRSES_PKRSW-LONSW_345KV
	Graham Ses - Graham East 138kV
	12
	$1,812,604.65
	 

	WLY_WAP_WAPWLY72_A
	DBLW2JC5
	WAPWLY72_A
	TWR (345) JCK-WAT62 & BLY-JCK57
	Wa Parish - Whaley 345kV
	15
	$1,804,892.20
	 

	BERGHE_BERGHE_BERGHE_AT1H
	DZORHAY5
	BERGHE_AT1H
	ZORN - HAYSEN 345KV
	Bergheim 345kV
	9
	$1,714,519.62
	 

	JN_BI_BI_JN_64_A
	DWAP_BI5
	BI_JN_64_A
	TWR (345) WAP-BI50 & SMITHERS-BI98
	Bellaire - Jeanetta 345kV
	10
	$1,705,103.22
	 

	NEWMAN_WALNUT1_NEWM_WAL_1
	SOAKSHI8
	NEWM_WAL_1
	OAKLAND SUBSTATION to SHILOH LIN 1
	Newman - Walnut 138kV
	2
	$1,571,582.71
	GPL_TPIT_110733_WylieSW_LCP_Upgrades_Walnut_Newman_Line (MOD: 110733)

	MADDUX_TREADWEL_MADDUX_TREADW1_1
	DBIGKEN5
	MADDUX_TREADW1_1
	Bighil-Kendal 345kV
	Maddux - Treadwell 138kV
	12
	$1,563,081.23
	 

	SAMSW_FVLSW_35045__A
	SHELBUL5
	35045__A
	HELIX to BULLOCK LIN 1A
	Sam Switch - Files Valley Switch 345kV
	6
	$1,561,357.23
	 

	LAKENASW_SAMATHIS_LAKENA_SAMATH1_1
	DBAKCED5
	LAKENA_SAMATH1_1
	BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV
	Lake Nasworthy - San Angelo Mathis Field 69kV
	15
	$1,554,976.98
	 

	MV_HBRG4_MV_WESL4_WESLCO_HIDLBRG_1
	MHARNED5
	WESLCO_HIDLBRG_1
	Manual dbl ckt for NEDIN-BONILLA 345kV & RIOH-PRIM138kV
	Heidelburg Sub - Weslaco Sub 138kV
	13
	$1,434,928.70
	STEC_71928_Heidelberg_AEPWeslaco_Upgrade (MOD 71928)

	CRDSW_OLNEY_6830__B
	DGRMGRS8
	6830__B
	FIREROCK TO BRNWD 138 AND FIREROCK TO BANGS 69 DBLCKT
	Cottonwood Road Switch - Olney Pod 69kV
	17
	$1,402,318.38
	 

	FMRVL_RYSSW_400__A
	SFMRRYS5
	400__A
	Farmersville Switch to Farmersville Switch LIN _A
	Royse Switch - Farmersville Switch 345kV
	11
	$1,373,314.95
	ONCOR_MNE_99066_Royse Switch – Farmersville Switch 345 kV Double-Circuit Line (MOD 99066, 25RPG004)

	CONCHO_VRBS_CONCHO_VRBS1_1
	SCRMSAR8
	CONCHO_VRBS1_1
	SAN ANGELO RED CREEK to BALLINGER LIN 1
	San Angelo Concho - Veribest 69kV
	5
	$1,334,261.76
	 

	BCPSW_AZLES_6275__D
	DCMBCPS8
	6275__D
	CPSES-CMBSW & CMDSW-HOD 138_DBLCKT
	Base Camp Switch - Azle Sub (Oncor) 138kV
	2
	$1,299,247.76
	 

	n/a_n/a_EASTEX
	BASE CASE
	EASTEX
	Basecase
	EASTEX GTC
	19
	$1,250,368.94
	 

	SALDS_SONTERRA_1710__A
	SANDFLO8
	1710__A
	ANDICE to FLORENCE LIN 1
	Salado South - Sonterra 138kV
	1
	$1,232,470.21
	 

	BIGHIL_OERSTED_225T558_1
	DBAKCED5
	225T558_1
	BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV
	Big Hill - Orsted 345kV
	5
	$1,231,901.43
	 

	FROWS_MCLSW_1025__B
	SMC2WEA8
	1025__B
	MCLANE SWITCH to WACO EAST LIN _C
	Mclane Switch - Frow Sub 138kV
	6
	$1,145,501.29
	 

	CMNSW_CMNTP_651__B
	DBUCRGP5
	651__B
	MANUAL DOUBLE RGPSW - KLNSW 345 KV & BUCSW - KLNSW 345 KV
	Comanche Tap - Comanche Switch (Oncor) 138kV
	11
	$1,124,615.16
	 

	PALOUSE_WOLFCAMP_PALOUS_WOLFCA1_1
	DBIGSCH5
	PALOUS_WOLFCA1_1
	Big Hill - Schneeman Draw & Big Hill - Schneeman Draw 2
	Palouse - Wolfcamp 138kV
	13
	$1,123,582.60
	 

	KENDAL_BERGHE_656T656_1
	DCAGCO58
	656T656_1
	Cagnon-Kendal 345 & Cico-Comfor 138
	Bergheim - Kendall 345kV
	6
	$1,026,161.65
	 

	SALDS_SONTERRA_1710__A
	DGABAN89
	1710__A
	Double contingency GABRIE-ANDUIN 69kV & GABRIE-GLASSC
	Salado South - Sonterra 138kV
	1
	$1,012,566.34
	 

	FROWS_MCLSW_1025__B
	SMCLWNE8
	1025__B
	MCLANE SWITCH to WACO NORTHEAST TAP LIN _A
	Mclane Switch - Frow Sub 138kV
	10
	$958,239.47
	 

	FBRSW_THSES_505__B
	DVENFTS5
	505__B
	VENSW-FTSSW & VENSW-SAMSW 345 DBLCKT
	Tradinghouse Ses - Four Brothers Switch 345kV
	5
	$956,164.49
	 

	YELWJCKT_FORTMA_FORTMA_YELWJC1_1
	DBIGKEN5
	FORTMA_YELWJC1_1
	Bighil-Kendal 345kV
	Yellow Jacket - Fort Mason 138kV
	12
	$871,998.89
	 

	PAWNEE_CALAVERS_PAWNEE_SPRUCE_1
	DELMSAN5
	PAWNEE_SPRUCE_1
	Elmcreek-Sanmigl 345kV
	Pawnee Switching Station - Calaveras 345kV
	7
	$862,145.19
	 

	HONDOCK_DEVINESW_HON_DEVI_1
	SHONF38
	HON_DEVI_1
	HONDO to HONDO CREEK SWITCHING STATION LIN 1
	Hondo Creek Switching Station - Devine Switch 69kV
	16
	$838,357.55
	 

	NLARSW_PILONCIL_NLARSW_PILONC1_1
	DFOAVLO5
	NLARSW_PILONC1_1
	FOWLERTON to LOBO & AVANZADA
	North Laredo Switch - Piloncillo 138kV
	16
	$765,976.14
	 

	CRDSW_OLNEY_6830__B
	SGRMGRS8
	6830__B
	GRAHAM EAST to GRAHAM EAST LIN _A
	Cottonwood Road Switch - Olney Pod 69kV
	7
	$760,461.65
	 

	n/a_n/a_E_PASP
	BASE CASE
	E_PASP
	Basecase
	E_PASP GTC
	13
	$670,228.21
	San Antonio South Reliability I Project , 22RPG048
LRGV Transmission Improvement Project (21RPG017)
San Antonio South Reliability II Project (23RPG032)

	n/a_n/a_PNHNDL
	BASE CASE
	PNHNDL
	Basecase
	PNHNDL GTC
	7
	$664,919.25
	 

	TYPRK_PLYAM_6200__F
	DCDHTVW5
	6200__F
	TVWSW TO CDHSW 345 AND CDHSW TO VENSW 345 DBLCKT
	Poly-America - Tyre Park Sub 138kV
	11
	$579,064.82
	 

	MRVLY_ESTLD_6635__G
	SCLCGTN8
	6635__G
	COLONY CREEK to GHOST TOWN SWITCH LIN _A
	Morton Valley (Oncor) - Eastland 69kV
	8
	$576,525.82
	 

	NUECES_B_WHITE_PT_NUECES_WHITE_2_1
	SMAYWHI8
	NUECES_WHITE_2_1
	GILA to MAYO LIN 1
	Nueces Bay - Whitepoint 138kV
	10
	$562,190.59
	 

	FROWS_MCLSW_1025__B
	SELMTH25
	1025__B
	ELM MOTT to ELM MOTT LIN _A
	Mclane Switch - Frow Sub 138kV
	16
	$561,694.22
	 

	FMRVL_RYSSW_381__A
	SFMRRY25
	381__A
	Farmersville Switch to ROYSE SWITCH LIN _A
	Farmersville Switch - Royse Switch 345kV
	8
	$535,265.06
	 

	LNGSW_PRLSW_6965__A
	MCATPRL5
	6965__A
	MAN_SGL_CATSW-PRLSW_345KV
	Longshore Switch - Prairieland Switch 345kV
	4
	$525,813.46
	Oncor_FW_81268_Longshore – Consavvy 345 kV Double-Circuit Line Rebuild (MOD 81268, 23RPG034)

	FRONTERA_S_MISSIN_BENTS_FRTER_1B_1
	SSHAFRO8
	BENTS_FRTER_1B_1
	FRONTERA to SHARYLAND LIN 1
	Frontera - South Mission 138kV
	16
	$456,570.55
	 

	NVKSW_ANARN_6840__B
	DMGSRIC8
	6840__B
	DBL_CKT_GRSES-RICSW_138 kV and GRSES-SGRAS_138 kV
	Anarene - Navy Kickapoo Switch 69kV
	15
	$443,991.07
	 

	KLNSW_HHSTH_630__B
	DSALKLN5
	630__B
	SALSW TO KLNSW 345 DBLCKT
	Harker Heights South - Killeen Switch 138kV
	3
	$379,367.43
	ONCOR_SE_87699_Belton - Killeen 138 kV_Line (MOD 87699, 24RPG001)

	FARMLAND_W_LD_345_FARMLAND_LONGD_1
	DCOTWR25
	FARMLAND_LONGD_1
	DBL_CKT_W_CS_345-WRASW_345KV_ln70155_A-WHIT_RV_W_CW1
	Farmland - Wett_Long_Draw 345kV
	6
	$377,136.62
	 

	ANGLETON_WCOLLOCL_G138_15_1
	SWCOWCO8
	G138_15_1
	WEST COLUMBIA MAIN TNP to ANGLETON TNP LIN 1
	West Columbia Local Tnp - Angleton Tnp 138kV
	4
	$349,722.23
	 

	WFSSW_NSTAR_6085__E
	DRILKRW5
	6085__E
	RILEY TO KRWSW 345 DBLCKT
	North Star - Wichita Falls South Switch 138kV
	3
	$330,622.12
	 

	BCESW_SNDSW_421__A
	SSNDBGR5
	421__A
	SANDOW SWITCH to BADGER SWITCH LIN _A
	Sandow Switch - Bell County East Switch 345kV
	5
	$320,852.44
	 

	ZEN_THW_THWZEN71_A
	DRNS_TB5
	THWZEN71_A
	Rns-Rtw & Sng-Tb 345kV
	Th Wharton - Zenith 345kV
	3
	$312,199.16
	 

	FOWLRTON_TILDEN_FWLRTN_TILDEN_1
	DFOWSMG5
	FWLRTN_TILDEN_1
	FOWLRTON TO SAN MIGUEL DOUBLE CIRCUIT CONTINGENCY
	Fowlerton - Tilden 138 Sub 138kV
	7
	$296,934.16
	 

	PALOUSE_CROSSOVE_CROSSO_PALOUS1_1
	SWOLPAL8
	CROSSO_PALOUS1_1
	PALOUSE to Wolfcamp LIN 1
	Crossover - Palouse 138kV
	11
	$277,374.62
	 

	HI_LONE_CEDACA_HI_LONE_TLINE_1
	BASE CASE
	HI_LONE_TLINE_1
	Basecase
	Cedar Canyon - High Lonesome 345kV
	3
	$273,172.73
	 

	n/a_n/a_MCCAMY
	BASE CASE
	MCCAMY
	Basecase
	MCCAMY GTC
	6
	$245,247.16
	 

	HECKER_RESNIK_HECKER_RESNIK1_1
	DMCDUPS8
	HECKER_RESNIK1_1
	MCCAMPBE - RESNIK & I_DUPSW 138kV
	Hecker - Resnik 138kV
	8
	$242,624.27
	Rebuild the Hecker to Resnik 138 kV line  76286

	HOWARD_LEON_CRK_D5_S1_1
	SP5CAG8
	D5_S1_1
	CAGNON to CAGNON LIN 1
	Leon Creek - Howard 138kV
	6
	$228,802.09
	 

	BRUNI_BRUNI_BRUNI_69_1
	DFOAVLO5
	BRUNI_69_1
	FOWLERTON to LOBO & AVANZADA
	Bruni Sub 138kV
	7
	$225,807.32
	 

	BGRSW_SNDSW_455__A
	SBCESN35
	455__A
	BELL COUNTY EAST SWITCH to BELL COUNTY EAST SWITCH LIN _A
	Badger Switch - Sandow Switch 345kV
	6
	$225,262.75
	 

	SACRC_DPCRK_6240__C
	DMTSCOS5
	6240__C
	DMTSW TO SCOSW 345 DBLCKT
	Sacroc - Deep Creek Sub 138kV
	5
	$218,288.86
	 

	FLTSW_PRSSW_1545__A
	SPRSPAR8
	1545__A
	PARIS SWITCH to PARIS LIN _A
	Paris Switch - Flying Tiger Switch 138kV
	11
	$199,040.49
	 

	SEA_SEA_SEA_AAT1
	DFRYTM58
	SEA_AAT1
	DOUBLE FRYSW-TMPSW 138 & KNBSW-SALSW 345
	Seaton 138kV
	6
	$183,848.68
	 

	LAKENASW_SAMATHIS_LAKENA_SAMATH1_1
	SBGLTWI8
	LAKENA_SAMATH1_1
	TWIN BUTTES to HARGROVE LIN 1
	Lake Nasworthy - San Angelo Mathis Field 69kV
	4
	$176,714.15
	 

	PALOUSE_WOLFCAMP_PALOUS_WOLFCA1_1
	DBIGKEN5
	PALOUS_WOLFCA1_1
	Bighil-Kendal 345kV
	Palouse - Wolfcamp 138kV
	4
	$157,547.07
	 

	LNGSW_PRLSW_6965__A
	DSLKNOR5
	6965__A
	Double NORTMC-SLKSW&SLKSW 345kV
	Longshore Switch - Prairieland Switch 345kV
	4
	$151,765.98
	Oncor_FW_81268_Longshore – Consavvy 345 kV Double-Circuit Line Rebuild (MOD 81268, 23RPG034)

	PIPECR_MEDILA_255T279_1
	DCAGCI58
	255T279_1
	Cagnon-Kendal 345 &Cico-Mengcr 138
	Medina Lake - Pipe Creek 138kV
	4
	$130,608.88
	 

	MEXTP_ITALY_2270__B
	SBLURDH8
	2270__B
	BLUM to RED HILL SWITCH LIN _G
	Milford Exxon Tap - Italy 69kV
	9
	$125,443.06
	 

	WCOLLOCL_ANGLETON_G138_15_1
	SWCOWCO8
	G138_15_1
	WEST COLUMBIA MAIN TNP to ANGLETON TNP LIN 1
	West Columbia Local Tnp - Angleton Tnp 138kV
	4
	$118,776.46
	 

	BOW_BOW_BOW_FMR1
	DRILKRW5
	BOW_FMR1
	RILEY TO KRWSW 345 DBLCKT
	Bowie 138kV
	5
	$114,491.53
	 

	NORTMC_CROSSOVE_CROSSO_NORTMC1_1
	DBIGSCH5
	CROSSO_NORTMC1_1
	Big Hill - Schneeman Draw & Big Hill - Schneeman Draw 2
	North Mccamey - Crossover 138kV
	4
	$114,092.20
	 

	BRUNI_BRUNI_BRUNI_69_1
	SLAQLOB8
	BRUNI_69_1
	LAQUINTA to LOBO LIN 1
	Bruni Sub 138kV
	11
	$113,181.29
	 

	LA_PALMA_HAINE_DR_HAINE__LA_PAL1_1
	SRAYRI38
	HAINE__LA_PAL1_1
	LAS PULGAS to RAYMONDVILLE 2 LIN 1
	Haine Drive - La Palma 138kV
	8
	$112,429.32
	 

	HAYSEN_ZORN_6T227_1
	SHAYZO25
	6T227_1
	HAYS ENERGY to ZORN LIN 1
	Zorn - Hays Energy 345kV
	3
	$104,704.19
	 

	PALOUSE_CROSSOVE_CROSSO_PALOUS1_1
	DBAKCED5
	CROSSO_PALOUS1_1
	BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV
	Crossover - Palouse 138kV
	8
	$90,059.35
	 

	DILLEYSW_DILLEYSW_DILLEYSW_XF1H
	DDILCOT8
	DILLEYSW_XF1H
	Dilleysw-Sanmgsw&Cotulas 138kV
	Dilley Switch Aep 138kV
	3
	$57,160.15
	 

	MADDUX_SAPOWER_MADDUX_SAPOWE1_1
	SMA2SAP8
	MADDUX_SAPOWE1_1
	MADDUX to SAN ANGELO POWER STATION LIN 1
	Maddux - San Angelo Power Station 138kV
	8
	$47,785.75
	 

	MAXWELL_HAMILTON_HAMILT_MAXWEL1_1
	DBIGKEN5
	HAMILT_MAXWEL1_1
	Bighil-Kendal 345kV
	Hamilton Road - Maxwell 138kV
	10
	$46,122.83
	 

	HAMILTON_MAVERICK_HAMILT_MAVERI1_1
	SBRAPIN8
	HAMILT_MAVERI1_1
	BRACKETTVILLE to BRACKETTVILLE LIN 1
	Hamilton Road - Maverick 138kV
	6
	$44,729.18
	 

	KNBSW_TMPSW_270__A
	DSALHUT5
	270__A
	SALSW - HUTTO 345KV
	Temple Switch - Knob Creek Switch 345kV
	3
	$42,723.74
	 

	TNNALVIN_ALVIN_138_ALV_NAL_1
	SMDOPHR5
	138_ALV_NAL_1
	MEADOW to PH ROBINSON LIN A
	North Alvin Tnp - Alvin Tnp 138kV
	11
	$39,746.53
	 

	ASHERTON_CATARINA_ASHERT_CATARI1_1
	DLOFOAV5
	ASHERT_CATARI1_1
	Double LOBO - FOWLERTON & AVANZADA
	Asherton - Catarina 138kV
	4
	$39,063.62
	 

	SNYDR_SNYDR_SNYDR_FMR1
	SSNYCGR8
	SNYDR_FMR1
	SNYDER to CHINA GROVE SWITCH LIN _A
	Snyder 138kV
	8
	$38,313.49
	 

	NUECES_B_WHITE_PT_NUECES_WHITE_2_1
	SWHILON5
	NUECES_WHITE_2_1
	LON HILL to WHITEPOINT LIN 1
	Nueces Bay - Whitepoint 138kV
	3
	$35,699.23
	 

	MEXTP_ITALY_2270__B
	SBLAWDB8
	2270__B
	BLANTON to WOODBURY SWITCH LIN _C
	Milford Exxon Tap - Italy 69kV
	3
	$24,387.53
	 

	CARVER_TINSLEY_CARVER_TINSLE1_1
	DBIGKEN5
	CARVER_TINSLE1_1
	Bighil-Kendal 345kV
	Carver - Tinsley Tap 138kV
	3
	$23,302.22
	 

	RAYBURN_L_463S_RAY_L_46_1
	SFURVAN8
	RAY_L_46_1
	FURHMAN to VANDERBILT SWITCHING STATION LIN 1
	Sam Rayburn Switchyd - Loop 463 Sub 138kV
	4
	$20,973.73
	 

	SOLSTICE_SOLSTICE_SOLSTICE_PST1
	DBAKSOL5
	SOLSTICE_PST1
	Bakersfield - Solstice line 1 and 2
	Solstice 138kV
	7
	$20,671.48
	 

	HAINE_DR_OLEANDER_HAINE__OLEAND1_1
	SRAYRI38
	HAINE__OLEAND1_1
	LAS PULGAS to RAYMONDVILLE 2 LIN 1
	Oleander - Haine Drive 138kV
	3
	$20,186.64
	 

	FURHMAN_RAYBURN_RAYBUR_FURHMAN_1
	SFURVAN8
	RAYBUR_FURHMAN_1
	FURHMAN to VANDERBILT SWITCHING STATION LIN 1
	Sam Rayburn Switchyd - Furhman 138kV
	12
	$19,189.46
	 

	CATARINA_ASHERTON_ASHERT_CATARI1_1
	DLOFOAV5
	ASHERT_CATARI1_1
	Double LOBO - FOWLERTON & AVANZADA
	Asherton - Catarina 138kV
	4
	$18,345.14
	 

	LOBO_LARDVNTH_LARDVN_LOBO2_1
	MLARDUS8
	LARDVN_LOBO2_1
	Manuel LAREDO VFT NORTH to Dust Devil LIN 1
	Lobo - Laredo Vft North 138kV
	4
	$14,420.52
	 

	BIG_FOOT_PLEASANT_BIG_FO_PLEASA1_1
	SHONMOO8
	BIG_FO_PLEASA1_1
	MOORE SWITCHING STATION to HONDO CREEK SWITCHING STATION LIN 1
	Big Foot - Pleasanton 138kV
	4
	$13,497.15
	 

	CARVER_TINSLEY_CARVER_TINSLE1_1
	SILLFTL8
	CARVER_TINSLE1_1
	FORT LANCASTER to FORT LANCASTER LIN 1
	Carver - Tinsley Tap 138kV
	4
	$13,189.78
	 

	MAXWELL_HAMILTON_HAMILT_MAXWEL1_1
	SCT2CAR8
	HAMILT_MAXWEL1_1
	CAUTHORN to Carver LIN 1
	Hamilton Road - Maxwell 138kV
	3
	$12,936.31
	 

	IH20_TNCOLIET_138_IH2_COT_1
	SSTAWIC8
	138_IH2_COT_1
	STAGHORN TNP to WICKETT TNP LIN 1
	Ih 20 Tnp - Collie Field Tap Tnp 138kV
	13
	$10,991.37
	 

	MAVERICK_HAMILTON_HAMILT_MAVERI1_1
	SBRAHAM8
	HAMILT_MAVERI1_1
	BRACKETTVILLE to HAMILTON ROAD LIN 1
	Hamilton Road - Maverick 138kV
	3
	$9,983.03
	 

	LEONCRK_FTST_138_FTS_LNC_1
	STARLEO8
	138_FTS_LNC_1
	LEON CREEK TNP to TARBUSH TNP LIN 1
	Leon Creek Tnp - Fort Stockton Plant 138kV
	3
	$8,974.31
	 

	SPUR_SPUR_SPUR_69_1
	SSPUASP8
	SPUR_69_1
	ASPERMONT AEP to ASPERMONT AEP LIN 1
	Spur 138kV
	3
	$8,556.52
	 

	FTST_LEONCRK_138_FTS_LNC_1
	BASE CASE
	138_FTS_LNC_1
	Basecase
	Leon Creek Tnp - Fort Stockton Plant 138kV
	7
	$6,789.19
	 

	HAMILTON_MAVERICK_HAMILT_MAVERI1_1
	SBRAHAM8
	HAMILT_MAVERI1_1
	BRACKETTVILLE to HAMILTON ROAD LIN 1
	Hamilton Road - Maverick 138kV
	3
	$5,874.14
	 

	UVALDE_READING_READIN_UVALDE1_1
	DRAZSA89
	READIN_UVALDE1_1
	Double Circuit RAZORBAC to DRYFRIO 138 kV & UVALDE to SABINAL 69 kV
	Uvalde Aep - Reading 138kV
	6
	$5,154.03
	 

	FURHMAN_MOURSUND_MOURSUND_FUR_1
	SFURVAN8
	MOURSUND_FUR_1
	FURHMAN to VANDERBILT SWITCHING STATION LIN 1
	Moursund - Furhman 138kV
	7
	$5,084.97
	 

	CATARINA_ASHERTON_ASHERT_CATARI1_1
	DFOAVLO5
	ASHERT_CATARI1_1
	FOWLERTON to LOBO & AVANZADA
	Asherton - Catarina 138kV
	7
	$4,060.51
	 

	FRONTERA_S_MISSIN_BENTS_FRTER_1B_1
	SBENS_M8
	BENTS_FRTER_1B_1
	SOUTH MCALLEN to BENTSEN LIN 1
	Frontera - South Mission 138kV
	12
	$2,693.16
	 

	WLVSW_GAILS_6217__A
	SBUZHMP8
	6217__A
	BUZZARD DRAW SWITCH to HARDY MORGAN POI LIN _B
	Willow Valley Switch - Gail Sub 138kV
	3
	$1,788.97
	 

	SAPOWER_MADDUX_MADDUX_SAPOWE1_1
	SMA2SAP8
	MADDUX_SAPOWE1_1
	MADDUX to SAN ANGELO POWER STATION LIN 1
	Maddux - San Angelo Power Station 138kV
	8
	$1,314.41
	 

	LON_HILL_CLARK_WD_CLARK__LON_HI1_1
	SCITWEI8
	CLARK__LON_HI1_1
	CHAMPLIN to CHAMPLIN LIN 1
	Clarkwood - Lon Hill 138kV
	3
	$682.11
	 



[bookmark: _Toc235457759][bookmark: _Hlk219801104]Generic Transmission Constraint Congestion
	GTC
	Days Congestion

	East Texas
	22

	Nelson Sharpe - Rio Hondo
	20

	North - Houston
	20

	West Texas
	18

	North Edinburg - Lobo
	18

	South Texas Export Pawnee - Spruce
	16

	Panhandle
	12

	South Texas Export Pawnee - Tango
	11

	McCamey
	8

	Zapata Starr
	4

	Treadwell
	2

	Valley Export
	2

	Kinney
	1

	South Texas Import Katoen - Lonhill
	1



There was no activity on the remaining GTCs during the month.
Note: This is how many times a constraint has been activated to avoid exceeding a GTC limit, it does not imply an exceedance of the GTC occurred or that the GTC was binding.
[bookmark: _Toc235457760][bookmark: _Hlk164677736]Manual Overrides
· None
[bookmark: _Toc235457761]Congestion Costs for Calendar Year 2026
The following table represents the top twenty active constraints for the calendar year based on the estimated congestion rent attributed to the congestion. ERCOT updates this list on a monthly basis.
	Contingency
	Overloaded Element
	# of 5-min SCED
	Estimated
	Transmission

	Basecase
	WESTEX GTC
	15,848
	93,016,095.15
	Permian Basin Reliability Plan (765-kV import paths) (The PUCT approved ,helps improve, but not fully exit, the GTC yet.)

	MANUAL HCKSW-RAMSW 345 kV_2
	Hicks Switch 138kV
	1,363
	51,703,803.38
	 

	BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV
	Longshore Switch - Prairieland Switch 345kV
	13,078
	50,083,939.49
	Oncor_FW_81268_Longshore – Consavvy 345 kV Double-Circuit Line Rebuild (MOD 81268, 23RPG034)

	MANUAL RNKSW TO DHMSW 345&KRWSW TO DHMSW 345 DBLCKT
	Argyle - Highlands Tnp 138kV
	6,658
	34,163,478.64
	 

	Basecase
	EASTEX GTC
	6,423
	33,498,873.57
	 

	SALSW TO KLNSW 345 DBLCKT
	Killeen Switch - Stagecoach 138kV
	2,796
	31,304,486.27
	ONCOR_SE_87703_Belton_Killeen_138 kV Line (via Nolanville) (MOD 87703, 24RPG001)

	BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1
	Mackenzie Substation - Northeast Substation 115kV
	7,410
	27,212,675.15
	 

	DOUBLE NVARO-LEG & NVARO-OUTSW 345 KV
	Big Brown Ses - Jewett 345kV
	504
	26,003,760.95
	ONCOR_SE_99622_PIN_OAK_SWITCH (MOD 99622, 25RPG004)

	BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV
	Hargrove - Twin Buttes 138kV
	4,720
	23,055,639.53
	 

	Basecase
	Omega - Horse Hollow Generation Tie 345kV
	9,092
	21,121,872.06
	 

	DMTSW TO SCOSW 345 DBLCKT
	Knapp - Scurry Chevron 138kV
	11,052
	20,979,511.01
	Oncor_FW_102849_Union 138 kV Switch (MOD 102849)

	Basecase
	E_PASP GTC
	8,565
	20,067,479.45
	San Antonio South Reliability I Project , 22RPG048
LRGV Transmission Improvement Project (21RPG017)
San Antonio South Reliability II Project (23RPG032)

	MORGAN CREEK SES to RANGER CAMP SWITCH LIN _A
	Morgan Creek Ses - Cattleman Switch 345kV
	3,070
	20,046,474.58
	West Texas 345-kV Infrastructure Rebuild Project  (23RPG034)

	Basecase
	NE_LOB GTC
	17,240
	18,755,618.75
	San Antonio South Reliability I Project (22RPG048)
LRGV Transmission Improvement Project (21RPG017)
San Antonio South Reliability II Project (23RPG032)

	SALSW TO KLNSW 345 DBLCKT
	Harker Heights South - Killeen Switch 138kV
	3,820
	17,819,511.40
	ONCOR_SE_87699_Belton - Killeen 138 kV_Line (MOD 87699, 24RPG001)

	TWR(345) WAP-WLF64 & WAP-WLY72
	South Texas Project - Wa Parish 345kV
	4,059
	16,395,743.23
	 

	STP-Elmcreek&WAP 345kV
	South Texas Project - Elmcreek 345kV
	355
	15,792,038.58
	 

	MANUAL SINGLE SANDOW SWITCH to BADGER SWITCH 345
	Sandow Switch - Bell County East Switch 345kV
	2,202
	15,471,465.60
	 

	FOWLERTON to LOBO & AVANZADA
	Lobo - Laredo Vft North 138kV
	5,426
	15,369,961.62
	 

	MAN_SGL_RGRSW-MGSES_345KV
	Morgan Creek Ses - Cattleman Switch 345kV
	2,380
	14,991,540.47
	West Texas 345-kV Infrastructure Rebuild Project  (23RPG034)


[bookmark: _Toc235457762][bookmark: _Hlk219797360]


System Events
[bookmark: _Toc235457763]ERCOT Peak Load
The unofficial ERCOT peak load for June 2026 was 82,772 MW and occurred on 06/18/2026 during hour ending 17:00, this is 5,376 MW greater than the June 2025 demand of 77,396 MW on 06-19/2025 during hour ending 17:00. Instantaneous peak for June 2026 was 82,869 MW. Actual instantaneous peak for the same month last year was 78,411 MW.
[bookmark: _Toc235457764]Load Shed Events
· None.
[bookmark: _Toc235457765]Stability Events
· None.
[bookmark: _Toc235457766]Notable PMU Events
ERCOT analyzes PMU data for any significant system disturbances that do not fall into the Frequency Events category reported in section 2.1. The results are summarized in this section once the analysis has been completed.
There were no PMU events outside of those reported in section 2.1.
[bookmark: _Toc235457767]DC Tie Curtailment
None.
[bookmark: _Toc235457768][bookmark: _Hlk164863863][bookmark: _Hlk141082606][bookmark: _Hlk135641502]TRE/DOE Reportable Events
· [bookmark: _Toc13724670]CPS Submitted a DOE-417 for 06/21/2026 for complete loss of monitoring or control capability at its staffed Bulk Electric System control center for 30 continuous minutes or more.
[bookmark: _Toc235457769]New/Updated Constraint Management Plans
· ADD: MP_2026_02 REV0,MP_2026_03 REV0,MP_2026_04 REV1,MP_2026_05 REV1,MP_2026_06 REV1,MP_2026_07 REV1,MP_2026_08 REV0,MP_2026_09 REV1,MP_2026_10 REV0,MP_2026_11 REV1,MP_2026_12 REV0,MP_2026_13 REV1,MP_2026_14 REV1,MP_2026_15 REV1,MP_2026_16 REV0,MP_2026_17 REV0,ON_SHELF_MP_2026_01 REV0,ON_SHELF_MP_2026_02 REV0,PCAP_2026_03 REV0
· MOD: MP_2012_07_REV 13,MP_2012_08 REV12,MP_2022_17 REV11,MP_2016_12 REV11,MP_2021_03 REV9,MP_2022_01 REV5,MP_2022_02 REV6,MP_2022_03 REV5,MP_2022_08 REV5,MP_2023_08 REV4,MP_2023_11 REV7,MP_2024_04 REV2,MP_2024_05 REV2,MP_2024_08 REV2,MP_2024_10 REV2,MP_2025_01 REV8,MP_2025_09 REV1,MP_2025_10 REV2,MP_2025_12 REV3,MP_2025_13 REV3,MP_2025_14 REV1,MP_2025_16 REV5,MP_2025_17 REV4,MP_2025_18 REV1,MP_2025_20 REV1,MP_2025_21 REV2,MP_2025_23 REV1,MP_2025_24 REV1,MP_2025_26 REV1,MP_2025_28 REV1,MP_2025_42 REV2,MP_2025_44 REV2,MP_2025_45 REV2,MP_2024_12 REV4,MP_2011_08 REV37,ON_SHELF_MP_2024_02 REV2,ON_SHELF_MP_2024_03 REV3,ON_SHELF_MP_2024_04 REV2,ON_SHELF_MP_2024_06 REV6,ON_SHELF_MP_2025_11 REV1,ON_SHELF_MP_2025_30 REV2,ON_SHELF_MP_2025_31 REV4,PCAP_2010_01 REV16,PCAP_2024_01 REV2,PCAP_2025_01 REV2
· REMOVED: MP_2022_09 REV6,MP_2022_14 REV5,MP_2022_15 REV5,MP_2023_12 REV6,MP_2025_08 REV0,MP_2025_25 REV1,MP_2025_27 REV1,MP_2025_32 REV2,ON_SHELF_MP_2020_03 REV17,ON_SHELF_MP_2025_29 REV0,PCAP_2010_02 REV20
[bookmark: _Toc235457770]New/Modified/Removed RAS
· None
[bookmark: _Toc235457771]New Procedures/Forms/Operating Bulletins
	[bookmark: _Hlk207973620]Date
	Subject
	Bulletin No.

	6/30/2026
	   Transmission and Security Desk Operating Procedure V2 Rev 7
	2032

	6/30/2026
	Real Time Desk V2 Rev 4
	2031

	6/30/2026
	DC Tie Desk V2 Rev 3
	2030





[bookmark: _Toc235457772][bookmark: _Hlk164863872]Emergency Conditions
[bookmark: _Toc235457773]OCNs
· None
[bookmark: _Toc235457774]Advisories
	Date and Time
	Message

	June 6, 2026 13:31
	DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/07/2026 due to long execution time

	June 9, 2026 13:24
	DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/10/2026 due to long solution run time.

	June 10, 2026 13:24
	DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/11/2026 due to long solution run time.

	June 17, 2026 13:26
	DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/18/2026 due to long execution time.

	June 18, 2026 13:30
	DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/19/2026 due to observed submission issue.

	June 20, 2026 13:20
	DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/21/2026 due to long execution time.

	June 23, 2026 13:14
	DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/24/2026 due to long execution time.

	June 24, 2026 13:27
	DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/25/2026 due to long execution time.

	June 30, 2026 13:23
	DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 07/01/2026 due to long execution time.



[bookmark: _Toc235457775]Watches
· None

[bookmark: _Toc235457776]Emergency Notices
· None


[bookmark: _Toc235457777]Application Performance
[bookmark: _Toc235457778]TSAT/VSAT Performance Issues
	Date and Time
	Message

	
	


[bookmark: _Toc235457779]Communication Issues
· None.
[bookmark: _Toc235457780][bookmark: _Hlk164863883]Market System Issues
· None.


[bookmark: _Toc235457781]Model Updates
The Downstream Production Change (DPC) process allows ERCOT to make changes in the one-line Network Operations Model without loading a completely new model.  The purpose of this process is to allow for reliable grid operations as system conditions change between designated Network Operations Model database loads.  The DPC process is limited in scope to just those items listed below, with equipment ratings updates being the most common.  ERCOT has seen a rise in the use of the DPC process to make on-line updates to the Network Operations Model in recent years, instead of through the standard Network Operations Model Change Request process.
· Static Line ratings (Interim Update)
· Dynamic Line ratings (non-Interim Update)
· Autotransformer ratings (non-Interim Update)
· Breaker and Switch Normal status (Interim Update)
· Contingency Definitions (Interim Update)
· RAP and RAS changes or additions (Interim Update)
· Net Dependable and Reactive Capability (NDCRC) values (Interim Update)
· Impedance Updates (non-Interim)
[image: ]
A total of 59 DPCs were implemented in June 2026. 276 DPCs have been implemented year to date. DPCs submitted by TDSPs are mainly updates to transmission element ratings. DPCs submitted by ERCOT are mainly updates to manual contingency definitions. 
	Transmission Operator
	Number of DPCs

	AEP TEXAS COMPANY (TDSP)
	3

	BRAZOS ELECTRIC POWER CO OP INC (TDSP)
	0

	BROWNSVILLE PUBLIC UTILITIES BOARD (TDSP)
	0

	BRYAN TEXAS UTILITIES (TDSP)
	0

	CENTERPOINT ENERGY HOUSTON ELECTRIC LLC (TDSP)
	5

	CITY OF AUSTIN DBA AUSTIN ENERGY (TDSP)
	0

	CITY OF COLLEGE STATION (TDSP)
	0

	CITY OF GARLAND (TDSP)
	0

	CPS ENERGY (TDSP)
	0

	CROSS TEXAS TRANSMISSION LLC (TSP))
	0

	DENTON MUNICIPAL ELECTRIC (TDSP)
	0

	ELECTRIC TRANSMISSION TEXAS LLC (TDSP)
	0

	ERCOT
	0

	LCRA TRANSMISSION SERVICES CORPORATION (TDSP)
	28

	LONE STAR TRANSMISSION LLC (TSP)
	1

	ONCOR ELECTRIC DELIVERY COMPANY LLC (TDSP)
	13

	PEDERNALES ELECTRIC CO OP INC (TDSP)
	0

	RAYBURN COUNTRY CO OP DBA RAYBURN ELECTRIC (TDSP)
	7

	SHARYLAND UTILITIES LP (TDSP)
	2

	SOUTH TEXAS ELECTRIC CO OP INC (TDSP)
	0

	TEXAS MUNICIPAL POWER AGENCY (TDSP)
	0

	TEXAS-NEW MEXICO POWER CO (TDSP)
	0

	WIND ENERGY TRANSMISSION TEXAS LLC (TSP)
	0




[bookmark: _Toc235457782]Appendix A: Real-Time Constraints
The following is a complete list of constraints activated in SCED. Full contingency descriptions can be found in the Standard Contingencies List located on the MIS secure site at Grid  Generation  Reliability Unit Commitment.
	Year
	Month
	Contingency Name
	Overloaded Element
	From Station
	To Station
	Count of Days

	2026
	June
	DMTSCOS5
	6437__F
	SCRCV
	KNAPP
	24

	2026
	June
	BASE CASE
	EASTEX
	n/a
	n/a
	22

	2026
	June
	DBIGKEN5
	TREADW_YELWJC1_1
	TREADWEL
	YELWJCKT
	22

	2026
	June
	SBWDDBM5
	LPLMK_LPLNE_1
	LPLMK
	LPLNE
	21

	2026
	June
	BASE CASE
	NELRIO
	n/a
	n/a
	20

	2026
	June
	SSTAWIC8
	138_IH2_COT_1
	IH20
	TNCOLIET
	20

	2026
	June
	BASE CASE
	N_TO_H
	n/a
	n/a
	20

	2026
	June
	SVEAW_L5
	6217__A
	WLVSW
	GAILS
	20

	2026
	June
	SSTAWIC8
	138_IH2_COT_1
	TNCOLIET
	IH20
	20

	2026
	June
	SRGRMGS5
	6945__A
	MGSES
	CATSW
	19

	2026
	June
	DPHRCTR5
	MDOPHR99_A
	MDO
	PHR
	19

	2026
	June
	SHC2EXC5
	107__B
	HCKSW
	EXCSW
	19

	2026
	June
	SSHAFRO8
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	19

	2026
	June
	DMGSRIC8
	6840__B
	NVKSW
	ANARN
	18

	2026
	June
	DGRMGRS8
	6830__B
	CRDSW
	OLNEY
	18

	2026
	June
	BASE CASE
	NE_LOB
	n/a
	n/a
	18

	2026
	June
	BASE CASE
	WESTEX
	n/a
	n/a
	18

	2026
	June
	SHONF38
	HON_DEVI_1
	HONDOCK
	DEVINESW
	18

	2026
	June
	SCMNCPS5
	651__B
	CMNSW
	CMNTP
	17

	2026
	June
	DWPWFWP5
	STPWAP39_1
	STP
	WAP
	17

	2026
	June
	DFOAVLO5
	NLARSW_PILONC1_1
	NLARSW
	PILONCIL
	17

	2026
	June
	SBENS_M8
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	17

	2026
	June
	DSCOTKW5
	6215__A
	BCKSW
	CGRSW
	17

	2026
	June
	SELMTH25
	1025__B
	FROWS
	MCLSW
	16

	2026
	June
	DCDHTVW5
	6200__F
	TYPRK
	PLYAM
	16

	2026
	June
	DBAKCED5
	6965__A
	LNGSW
	PRLSW
	16

	2026
	June
	SFURVAN8
	RAYBUR_FURHMAN_1
	FURHMAN
	RAYBURN
	16

	2026
	June
	DBLW2JC5
	WAPWLY72_A
	WLY
	WAP
	16

	2026
	June
	DRNS_TB5
	THWZEN98_A
	ZEN
	THW
	16

	2026
	June
	SLAQLOB8
	BRUNI_69_1
	BRUNI
	BRUNI
	16

	2026
	June
	BASE CASE
	E_PASP
	n/a
	n/a
	16

	2026
	June
	DBAKCED5
	LAKENA_SAMATH1_1
	LAKENASW
	SAMATHIS
	16

	2026
	June
	SMDOPHR5
	138_ALV_NAL_1
	TNNALVIN
	ALVIN
	16

	2026
	June
	BASE CASE
	HHGTOM_1
	HHGT
	OMEGA
	14

	2026
	June
	DBIGKEN5
	MADDUX_TREADW1_1
	MADDUX
	TREADWEL
	14

	2026
	June
	DWAP_OB5
	MDOPHR99_A
	MDO
	PHR
	14

	2026
	June
	SMDOOAS5
	GN_PZ_08_A
	GN
	PZ
	14

	2026
	June
	SMAYWHI8
	NUECES_WHITE_2_1
	NUECES_B
	WHITE_PT
	14

	2026
	June
	DBIGSCH5
	PALOUS_WOLFCA1_1
	PALOUSE
	WOLFCAMP
	14

	2026
	June
	DBIGKEN5
	FORTMA_YELWJC1_1
	YELWJCKT
	FORTMA
	13

	2026
	June
	DLONPK25
	6375__A
	GRSES
	GRMES
	13

	2026
	June
	MHARNED5
	WESLCO_HIDLBRG_1
	MV_HBRG4
	MV_WESL4
	13

	2026
	June
	SBLURDH8
	2270__B
	MEXTP
	ITALY
	12

	2026
	June
	SWOLPAL8
	CROSSO_PALOUS1_1
	PALOUSE
	CROSSOVE
	12

	2026
	June
	BASE CASE
	PNHNDL
	n/a
	n/a
	12

	2026
	June
	DBUCRGP5
	651__B
	CMNSW
	CMNTP
	12

	2026
	June
	DZORHAY5
	BERGHE_AT1H
	BERGHE
	BERGHE
	12

	2026
	June
	DWAP_BI5
	BI_JN_64_A
	JN
	BI
	12

	2026
	June
	DLONPK25
	12020__B
	BRTSW
	JUNPR
	12

	2026
	June
	SFMRRYS5
	400__A
	FMRVL
	RYSSW
	12

	2026
	June
	SPRSPAR8
	1545__A
	FLTSW
	PRSSW
	11

	2026
	June
	DSALHUT5
	1715__B
	TMPSW
	FRYSW
	11

	2026
	June
	DBIGKEN5
	HAMILT_MAXWEL1_1
	MAXWELL
	HAMILTON
	11

	2026
	June
	BASE CASE
	E_PATA
	n/a
	n/a
	11

	2026
	June
	DFOAVLO5
	BRUNI_69_1
	BRUNI
	BRUNI
	11

	2026
	June
	SMCLWNE8
	1025__B
	FROWS
	MCLSW
	10

	2026
	June
	DFRYTM58
	SEA_AAT1
	SEA
	SEA
	10

	2026
	June
	DFOAVLO5
	ASHERT_CATARI1_1
	CATARINA
	ASHERTON
	10

	2026
	June
	SMA2SAP8
	MADDUX_SAPOWE1_1
	MADDUX
	SAPOWER
	9

	2026
	June
	DBAKCED5
	CROSSO_PALOUS1_1
	PALOUSE
	CROSSOVE
	9

	2026
	June
	SMA2SAP8
	MADDUX_SAPOWE1_1
	SAPOWER
	MADDUX
	9

	2026
	June
	SSNYCGR8
	SNYDR_FMR1
	SNYDR
	SNYDR
	9

	2026
	June
	BASE CASE
	138_FTS_LNC_1
	FTST
	LEONCRK
	9

	2026
	June
	SFMRRY25
	381__A
	FMRVL
	RYSSW
	9

	2026
	June
	DSALHUT5
	1710__A
	SALDS
	SONTERRA
	9

	2026
	June
	DMCDUPS8
	HECKER_RESNIK1_1
	HECKER
	RESNIK
	9

	2026
	June
	SCLCGTN8
	6635__G
	MRVLY
	ESTLD
	8

	2026
	June
	DBAKCED5
	HARGRO_TWINBU1_1
	TWINBU
	HARGROVE
	8

	2026
	June
	SRAYRI38
	HAINE__LA_PAL1_1
	LA_PALMA
	HAINE_DR
	8

	2026
	June
	DRAZSA89
	READIN_UVALDE1_1
	UVALDE
	READING
	8

	2026
	June
	SVENFTS5
	35055__A
	SAMSW
	VENSW
	8

	2026
	June
	SGRMGRS8
	6830__B
	CRDSW
	OLNEY
	8

	2026
	June
	BASE CASE
	MCCAMY
	n/a
	n/a
	8

	2026
	June
	SFURVAN8
	MOURSUND_FUR_1
	FURHMAN
	MOURSUND
	8

	2026
	June
	DMTSCOS5
	6240__C
	SACRC
	DPCRK
	8

	2026
	June
	SBCESN35
	455__A
	BGRSW
	SNDSW
	7

	2026
	June
	DCAGCO58
	656T656_1
	KENDAL
	BERGHE
	7

	2026
	June
	SILLFTL8
	CARVER_TINSLE1_1
	CARVER
	TINSLEY
	7

	2026
	June
	DFOWSMG5
	FWLRTN_TILDEN_1
	FOWLRTON
	TILDEN
	7

	2026
	June
	SSNDBGR5
	421__A
	BCESW
	SNDSW
	7

	2026
	June
	SWHILON5
	NUECES_WHITE_2_1
	NUECES_B
	WHITE_PT
	7

	2026
	June
	SBRAPIN8
	HAMILT_MAVERI1_1
	HAMILTON
	MAVERICK
	7

	2026
	June
	DELMSAN5
	PAWNEE_SPRUCE_1
	PAWNEE
	CALAVERS
	7

	2026
	June
	DCOTWR25
	FARMLAND_LONGD_1
	FARMLAND
	W_LD_345
	7

	2026
	June
	DBAKSOL5
	SOLSTICE_PST1
	SOLSTICE
	SOLSTICE
	7

	2026
	June
	DCAGCI58
	255T279_1
	PIPECR
	MEDILA
	7

	2026
	June
	SWCOWCO8
	G138_15_1
	WCOLLOCL
	ANGLETON
	6

	2026
	June
	SHONMOO8
	BIG_FO_PLEASA1_1
	BIG_FOOT
	PLEASANT
	6

	2026
	June
	SP5CAG8
	D5_S1_1
	HOWARD
	LEON_CRK
	6

	2026
	June
	SWCOWCO8
	G138_15_1
	ANGLETON
	WCOLLOCL
	6

	2026
	June
	SHELBUL5
	35045__A
	SAMSW
	FVLSW
	6

	2026
	June
	SMC2WEA8
	1025__B
	FROWS
	MCLSW
	6

	2026
	June
	DVENFTS5
	505__B
	FBRSW
	THSES
	5

	2026
	June
	SSUNRGR8
	6240__C
	SACRC
	DPCRK
	5

	2026
	June
	DWPWFWP5
	155T217_1
	BELLSO
	PT
	5

	2026
	June
	SCRMSAR8
	CONCHO_VRBS1_1
	CONCHO
	VRBS
	5

	2026
	June
	SBUZHMP8
	6217__A
	WLVSW
	GAILS
	5

	2026
	June
	SFURVAN8
	RAY_L_46_1
	RAYBURN
	L_463S
	5

	2026
	June
	SSPUASP8
	SPUR_69_1
	SPUR
	SPUR
	5

	2026
	June
	SBLURDH8
	1275__A
	WDBSW
	HLSBR
	5

	2026
	June
	DBAKCED5
	225T558_1
	BIGHIL
	OERSTED
	5

	2026
	June
	DLOFOAV5
	ASHERT_CATARI1_1
	CATARINA
	ASHERTON
	5

	2026
	June
	DRILKRW5
	BOW_FMR1
	BOW
	BOW
	5

	2026
	June
	SBGLTWI8
	LAKENA_SAMATH1_1
	LAKENASW
	SAMATHIS
	5

	2026
	June
	DLOFOAV5
	ASHERT_CATARI1_1
	ASHERTON
	CATARINA
	5

	2026
	June
	SSAMTCR5
	505__B
	FBRSW
	THSES
	4

	2026
	June
	DFRYBC58
	SEA_AAT1
	SEA
	SEA
	4

	2026
	June
	SCOLBAL8
	BALLIN_HUMBLT1_1
	BALLINGE
	HUMBLTAP
	4

	2026
	June
	SRAYRI38
	HAINE__OLEAND1_1
	HAINE_DR
	OLEANDER
	4

	2026
	June
	SSOAHOL8
	138_FTS_LNC_1
	FTST
	LEONCRK
	4

	2026
	June
	SBRAPIN8
	ESCOND_GANSO1_1
	GANSO
	ESCONDID
	4

	2026
	June
	SOAKSHI8
	NEWM_WAL_1
	NEWMAN
	WALNUT1
	4

	2026
	June
	DBIGSCH5
	SANTAR_WOLFCA1_1
	WOLFCAMP
	SANTARIT
	4

	2026
	June
	BASE CASE
	ZAPSTR
	n/a
	n/a
	4

	2026
	June
	SBRAPIN8
	ESCOND_GANSO1_1
	ESCONDID
	GANSO
	4

	2026
	June
	MLARDUS8
	LARDVN_LOBO2_1
	LOBO
	LARDVNTH
	4

	2026
	June
	SHAYZO25
	6T227_1
	HAYSEN
	ZORN
	4

	2026
	June
	DSALHUT5
	270__A
	KNBSW
	TMPSW
	4

	2026
	June
	DRILKRW5
	6085__E
	WFSSW
	NSTAR
	4

	2026
	June
	DBIGSCH5
	CROSSO_NORTMC1_1
	NORTMC
	CROSSOVE
	4

	2026
	June
	DRNS_TB5
	THWZEN71_A
	ZEN
	THW
	4

	2026
	June
	STARLEO8
	138_FTS_LNC_1
	LEONCRK
	FTST
	4

	2026
	June
	MCATPRL5
	6965__A
	LNGSW
	PRLSW
	4

	2026
	June
	SBLURDH8
	1210__B
	HUBRD
	HAN1
	4

	2026
	June
	SCITWEI8
	CLARK__LON_HI1_1
	LON_HILL
	CLARK_WD
	4

	2026
	June
	DBIGKEN5
	PALOUS_WOLFCA1_1
	PALOUSE
	WOLFCAMP
	4

	2026
	June
	BASE CASE
	RANDAD_ZAPATA1_1
	RANDADO
	ZAPATA
	4

	2026
	June
	DSLKNOR5
	6965__A
	LNGSW
	PRLSW
	4

	2026
	June
	SBLAWDB8
	2270__B
	MEXTP
	ITALY
	3

	2026
	June
	DLOFOAV5
	NLARSW_PILONC1_1
	PILONCIL
	NLARSW
	3

	2026
	June
	SSCJFS8
	BCVPSA03_A
	PSA
	BCV
	3

	2026
	June
	SSTPESP8
	BLESSI_PAVLOV1_1
	BLESSING
	PAVLOV
	3

	2026
	June
	SBRAHAM8
	HAMILT_MAVERI1_1
	HAMILTON
	MAVERICK
	3

	2026
	June
	SBRAHAM8
	HAMILT_MAVERI1_1
	MAVERICK
	HAMILTON
	3

	2026
	June
	DELMSAN5
	MAGRUD_VICTOR2_1
	VICTORIA
	MAGRUDER
	3

	2026
	June
	SVEAW_L5
	6217__D
	KEYSB
	LMESA
	3

	2026
	June
	DDILCOT8
	DILLEYSW_XF1H
	DILLEYSW
	DILLEYSW
	3

	2026
	June
	MATHEB_8
	FB_RS_60_A
	RS
	FB
	3

	2026
	June
	DALASOA8
	138_FTS_LNC_1
	FTST
	LEONCRK
	3

	2026
	June
	DVENFTS5
	235__A
	SGRSW
	JEWET
	3

	2026
	June
	DCSHSSP5
	690__C
	SSPSW
	LBRPD
	3

	2026
	June
	DFOAVLO5
	FREER_LOBO1_1
	LOBO
	FREER
	3

	2026
	June
	DVICEDN8
	FURHMAN_VANDB_1
	FURHMAN
	VANBLTSS
	3

	2026
	June
	SSTPESP8
	LAN_CT_PAVLOV1_1
	PAVLOV
	LAN_CTY
	3

	2026
	June
	SHAMMAX8
	MAXWEL_WHITIN1_1
	MAXWELL
	WHITING
	3

	2026
	June
	DLOFOAV5
	NLARSW_PILONC1_1
	NLARSW
	PILONCIL
	3

	2026
	June
	SPRAWAL8
	155T217_1
	BELLSO
	PT
	3

	2026
	June
	DLOFOAV5
	BRUNI_69_1
	BRUNI
	BRUNI
	3

	2026
	June
	DBIGKEN5
	CARVER_TINSLE1_1
	CARVER
	TINSLEY
	3

	2026
	June
	SCT2CAR8
	HAMILT_MAXWEL1_1
	MAXWELL
	HAMILTON
	3

	2026
	June
	MTRYBRO8
	6217__A
	WLVSW
	GAILS
	3

	2026
	June
	DSALKLN5
	630__B
	KLNSW
	HHSTH
	3

	2026
	June
	DMBDRKC5
	651__B
	CMNSW
	CMNTP
	3

	2026
	June
	STARLEO8
	SOLSTICE_PST1
	SOLSTICE
	SOLSTICE
	3

	2026
	June
	DRAZSA89
	2585_1
	DOWNIES
	MOORE
	3

	2026
	June
	XBAL89
	CONCHO_VRBS1_1
	CONCHO
	VRBS
	3

	2026
	June
	BASE CASE
	HI_LONE_TLINE_1
	HI_LONE
	CEDACA
	3

	2026
	June
	DRILKRW5
	6085__B
	NSTAR
	LKARH
	3

	2026
	June
	DCMBCPS8
	6275__D
	BCPSW
	AZLES
	2

	2026
	June
	SLISBAT8
	GARZA_XF1H
	GARZA
	GARZA
	2

	2026
	June
	SNEDSTE5
	PANTER_WESMER1_1
	WESMER
	PANTERA
	2

	2026
	June
	DSLKSOL5
	138_FLT_FXT_1
	TNFXTAIL
	FLAT_TOP
	2

	2026
	June
	MHARNED5
	HAINE__LA_PAL1_1
	LA_PALMA
	HAINE_DR
	2

	2026
	June
	SCRDJON5
	HOOD_DECRDVA_1
	DCDAM
	HOD
	2

	2026
	June
	SBRABND8
	NEWM_WAL_1
	NEWMAN
	WALNUT1
	2

	2026
	June
	SCROPAL8
	PALOUS_WOLFCA1_1
	PALOUSE
	WOLFCAMP
	2

	2026
	June
	SWORBRD8
	138_WIC_STG_1
	WICKETT
	STAGHORN
	2

	2026
	June
	SCLCGTN8
	6360__A
	BRKTP
	BRKRG
	2

	2026
	June
	SREAUVA8
	DOWNIES_AX1H
	DOWNIES
	DOWNIES
	2

	2026
	June
	DSALHUT5
	GABRIE_AT1
	GABRIE
	GABRIE
	2

	2026
	June
	SHA2MAX8
	MAXWEL_WHITIN1_1
	MAXWELL
	WHITING
	2

	2026
	June
	SBOSELM5
	1210__B
	HUBRD
	HAN1
	2

	2026
	June
	SHELBUL5
	35055__A
	SAMSW
	VENSW
	2

	2026
	June
	MDBHRSA5
	6085__E
	WFSSW
	NSTAR
	2

	2026
	June
	MNLFIWO8
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	2

	2026
	June
	SMOOPEA8
	PALDRO_DILLEY_1
	PALODURO
	DILLEYSW
	2

	2026
	June
	BASE CASE
	REATA_ROMNE_1A_A
	REATA
	ROMNEY
	2

	2026
	June
	SMOOPEA8
	UVALDE_W_BATE1_1
	W_BATESV
	UVALDE
	2

	2026
	June
	BASE CASE
	VALEXP
	n/a
	n/a
	2

	2026
	June
	DKG_NB_5
	BCVPSA03_A
	PSA
	BCV
	2

	2026
	June
	SMDOOAS5
	BCVPSA03_A
	PSA
	BCV
	2

	2026
	June
	SMOOPEA8
	DILLY_PEARSA1_1
	DILLY
	PEARSAL1
	2

	2026
	June
	SLARDUS8
	LARDVN_LOBO2_1
	LOBO
	LARDVNTH
	2

	2026
	June
	BASE CASE
	TRDWEL
	n/a
	n/a
	2

	2026
	June
	SHCKEXC5
	106__C
	HCKSW
	EXCSW
	2

	2026
	June
	SPALFRO8
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	2

	2026
	June
	MELNHST5
	BLESSING_1382
	BLESSING
	BLESSING
	2

	2026
	June
	DKG_NB_5
	MDOPHR99_A
	MDO
	PHR
	2

	2026
	June
	SBRAHAM8
	ESCOND_GANSO1_1
	ESCONDID
	GANSO
	2

	2026
	June
	DFOWSMG5
	GEO_SIG_1
	GEOWEST
	SIGMOR
	2

	2026
	June
	SBRAESC8
	HAMILT_MAVERI1_1
	HAMILTON
	MAVERICK
	2

	2026
	June
	SL_4RAY8
	RAYBURN_69_2
	RAYBURN
	RAYBURN
	2

	2026
	June
	SSNYCGR8
	6695__B
	SNYDR
	AMOTP
	2

	2026
	June
	DWO5_EU8
	DT_PK_91_A
	PK
	DT
	2

	2026
	June
	BASE CASE
	FURHMAN_VANDB_1
	FURHMAN
	VANBLTSS
	2

	2026
	June
	DSGTSCH5
	LAKENA_SAMATH1_1
	LAKENASW
	SAMATHIS
	2

	2026
	June
	SBOSWHT8
	LKW_WHT_1
	LKWHITNY
	WHTNY
	2

	2026
	June
	BASE CASE
	RAYBUR_FURHMAN_1
	FURHMAN
	RAYBURN
	2

	2026
	June
	SCOLBAL8
	SANA_FMR1
	SANA
	SANA
	1

	2026
	June
	MSNDWCR5
	SNDSW_MR1L
	SNDSW
	SNDSW
	1

	2026
	June
	DSNG_TB5
	THWZEN98_A
	ZEN
	THW
	1

	2026
	June
	DSALHUT5
	421__A
	BCESW
	SNDSW
	1

	2026
	June
	SGRSJUN8
	6275__D
	BCPSW
	AZLES
	1

	2026
	June
	SCSDNK8
	BCVPSA03_A
	PSA
	BCV
	1

	2026
	June
	SWCPYT8
	FB_RS_60_A
	RS
	FB
	1

	2026
	June
	DHUTGEA8
	GABRIE_AT1
	GABRIE
	GABRIE
	1

	2026
	June
	SBWDDBM5
	LPLNW_LPLMD_1
	LPLNW
	LPLMD
	1

	2026
	June
	MSNDWCR5
	SNDSW_MR1H
	SNDSW
	SNDSW
	1

	2026
	June
	SNWEWES8
	WES_MV_W_1
	WESLACO
	MV_WESL4
	1

	2026
	June
	DTNFBCA8
	138_FTS_LNC_1
	FTST
	LEONCRK
	1

	2026
	June
	BASE CASE
	155T217_1
	BELLSO
	PT
	1

	2026
	June
	SHLSWH28
	2270__B
	MEXTP
	ITALY
	1

	2026
	June
	DTOKJK_5
	260_A_1
	JEWET
	SNG
	1

	2026
	June
	MLNGPR25
	5025__A
	RGRSW
	PRMSW
	1

	2026
	June
	SDANBLE8
	BLESSING_69A1
	BLESSING
	BLESSING
	1

	2026
	June
	SANGSTA5
	BLESSI_LOLITA1_1
	LOLITA
	BLESSING
	1

	2026
	June
	SLKAWFS8
	BOW_FMR1
	BOW
	BOW
	1

	2026
	June
	DTOKJK_5
	HRN_GOOD_1
	HRN
	GOODLAND
	1

	2026
	June
	BASE CASE
	I_KALO
	n/a
	n/a
	1

	2026
	June
	SOBWAP5
	OB_WAP98_A
	WAP
	OB
	1

	2026
	June
	MDHSRSA5
	12020__B
	BRTSW
	JUNPR
	1

	2026
	June
	DBAKSOL5
	225T558_1
	BIGHIL
	OERSTED
	1

	2026
	June
	SVEAW_L5
	6217__B
	GAILS
	KEYSB
	1

	2026
	June
	DCPSST58
	651__B
	CMNSW
	CMNTP
	1

	2026
	June
	SHLSWDB8
	810__B
	BLUMS
	RVSTP
	1

	2026
	June
	DCHBJO25
	CBY_AT3H
	CBY
	CBY
	1

	2026
	June
	BASE CASE
	HENWAP01_A
	WAP
	HEN
	1

	2026
	June
	SOXYIN28
	I_DUPP_I_DUPS1_1
	I_DUPP1
	I_DUPSW
	1

	2026
	June
	DRNS_TB5
	MDOPHR99_A
	MDO
	PHR
	1

	2026
	June
	DODEMOS5
	ODEHV_MR3H
	ODEHV
	ODEHV
	1

	2026
	June
	SFURVAN8
	RAY_MOURSUND_1
	MOURSUND
	RAYBURN
	1

	2026
	June
	MBONNED5
	WESLCO_HIDLBRG_1
	MV_HBRG4
	MV_WESL4
	1

	2026
	June
	SBRESAL8
	105T105_1
	SALEM
	HIGH36
	1

	2026
	June
	SBLAWDB8
	1210__B
	HUBRD
	HAN1
	1

	2026
	June
	SSTAPYO8
	138_HRT_BPT_1
	BRDSPRYT
	HARPOONT
	1

	2026
	June
	SWORBRD8
	138_PYT_STG_1
	STAGHORN
	PYOTE
	1

	2026
	June
	DBLBYWF5
	155T217_1
	BELLSO
	PT
	1

	2026
	June
	SANDFLO8
	1715__B
	TMPSW
	FRYSW
	1

	2026
	June
	DWLV89N8
	3410__A
	ELVSW
	REGST
	1

	2026
	June
	STAYS_M8
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	1

	2026
	June
	SFURMOU8
	FURHMAN_VANDB_1
	FURHMAN
	VANBLTSS
	1

	2026
	June
	BASE CASE
	HENWAP01_A
	HEN
	WAP
	1

	2026
	June
	BASE CASE
	KINNEY
	n/a
	n/a
	1

	2026
	June
	DRNS_TB5
	NB_THW97_A
	THW
	NB
	1

	2026
	June
	SNICBLU8
	OAKC_SERDEV1_1
	OAKC
	OAKC
	1

	2026
	June
	DBUCRGP5
	TREADW_YELWJC1_1
	TREADWEL
	YELWJCKT
	1

	2026
	June
	SNWEWES8
	WESLCO_HIDLBRG_1
	MV_HBRG4
	MV_WESL4
	1

	2026
	June
	XTRS258
	1210__B
	HUBRD
	HAN1
	1

	2026
	June
	DPHRCTR5
	138_ALV_NAL_1
	TNNALVIN
	ALVIN
	1

	2026
	June
	SALVTNN8
	138_FWP_MNL_1
	FRWYPARK
	MAINLAND
	1

	2026
	June
	SSTAWIC8
	138_HRT_BPT_1
	BRDSPRYT
	HARPOONT
	1

	2026
	June
	DGABAN89
	1710__A
	SALDS
	SONTERRA
	1

	2026
	June
	SECRDMT8
	6215__A
	BCKSW
	CGRSW
	1

	2026
	June
	DBWNRGP5
	651__B
	CMNSW
	CMNTP
	1

	2026
	June
	DKLNRGP5
	651__C
	CMNTP
	SHILO
	1

	2026
	June
	DMGSRIC8
	6840__A
	ANARN
	CRDSW
	1

	2026
	June
	SLCDYN8
	FB_RS_60_A
	RS
	FB
	1

	2026
	June
	STNNMDO8
	G138_8A_1
	PHR
	HDNLAKES
	1

	2026
	June
	UJUNBES1
	HEXT_MASONS1_1
	HEXT
	MASONSW
	1

	2026
	June
	SMDOPHR5
	MDO_AT1
	MDO
	MDO
	1

	2026
	June
	SMCEABS8
	MERK_MKLT1_1
	MKLT
	MERK
	1

	2026
	June
	SGIRTNW8
	M_69_N1_1
	TNFS
	TNPINION
	1

	2026
	June
	SBELFRY8
	SEA_AAT1
	SEA
	SEA
	1

	2026
	June
	DRAZSA89
	UVALDE_W_BATE1_1
	UVALDE
	W_BATESV
	1

	2026
	June
	SWCOW2C8
	_WC_WCO_1
	WC
	WCOLMAIN
	1

	2026
	June
	DSLKSOL5
	138_FTS_LNC_1
	FTST
	LEONCRK
	1

	2026
	June
	SFBRTHS5
	500__B
	SAMSW
	TCRSW
	1

	2026
	June
	DCAGCO58
	584T584_1
	KENDAL
	WELFAR
	1

	2026
	June
	SPRMRCK5
	6053__C
	CATSW
	PRLSW
	1

	2026
	June
	DSCOTKW5
	6685__A
	CGRSW
	CLCTY
	1

	2026
	June
	SHLSWDB8
	810__G
	RDHSW
	BLUMS
	1

	2026
	June
	SLARDUS8
	ASHERT_CATARI1_1
	ASHERTON
	CATARINA
	1

	2026
	June
	BASE CASE
	BAKRFLD_CEDCAN_1
	CEDACA
	BAKESW
	1

	2026
	June
	DCHBJO25
	CBY_AT1H
	CBY
	CBY
	1

	2026
	June
	XUVA189
	CHAPAR_TURTLC1_1
	TURTLCRK
	CHAPARRO
	1

	2026
	June
	DRAZSA89
	DOWNIES_AX1H
	DOWNIES
	DOWNIES
	1

	2026
	June
	DBUCRGP5
	FORTMA_YELWJC1_1
	YELWJCKT
	FORTMA
	1

	2026
	June
	SANDFLO8
	1710__A
	SALDS
	SONTERRA
	1

	2026
	June
	DSNDBGR5
	36040__A
	KNBSW
	SALSW
	1

	2026
	June
	DHILMAR5
	361T361_1
	SCHERT
	PARKWA
	1

	2026
	June
	DVLSPAC5
	389__A
	WDDSW
	MNSES
	1

	2026
	June
	DFVLFTS5
	505__B
	FBRSW
	THSES
	1

	2026
	June
	DCAGCO58
	583T583_1
	BANDER
	MASOCR
	1

	2026
	June
	DSLKNOR5
	6056__B
	PRLSW
	CONSW
	1

	2026
	June
	XCMB58
	651__B
	CMNSW
	CMNTP
	1

	2026
	June
	DWLFMET5
	6525__A
	ODEHV
	RTRSW
	1

	2026
	June
	SGRMGRS8
	6830__C
	OLNEY
	GRAHM
	1

	2026
	June
	DBLUBUF8
	ABNTHW_SERDEV1_1
	ABNTHWST
	ABNTHWST
	1

	2026
	June
	MXMUB58
	ABNTHW_SERDEV1_1
	ABNTHWST
	ABNTHWST
	1

	2026
	June
	SBWSTOW9
	BOW_FMR1
	BOW
	BOW
	1

	2026
	June
	DBIGKEN5
	CROSSO_NORTMC1_1
	NORTMC
	CROSSOVE
	1

	2026
	June
	SHA2MAX8
	CTHR_TINSLE1_1
	CTHR
	TINSLEY
	1

	2026
	June
	DBIGSCH5
	FORTMA_YELWJC1_1
	YELWJCKT
	FORTMA
	1

	2026
	June
	DVICDUP8
	GREENL_WEAVER1_1
	WEAVERRD
	GREENLK
	1

	2026
	June
	SFORRAY8
	RAY_L_46_1
	RAYBURN
	L_463S
	1

	2026
	June
	SNEDSTE5
	WESLCO_HIDLBRG_1
	MV_HBRG4
	MV_WESL4
	1

	2026
	June
	MMCLWLA8
	1025__B
	FROWS
	MCLSW
	1

	2026
	June
	DTCRTHS5
	35045__A
	SAMSW
	FVLSW
	1

	2026
	June
	MBULNAV5
	35045__A
	SAMSW
	FVLSW
	1

	2026
	June
	DBUCRGP5
	505__B
	FBRSW
	THSES
	1

	2026
	June
	MRNKDHM5
	587__A
	ARGYL
	LWSVH
	1

	2026
	June
	DFRYBC58
	BELCNTY_XFMR
	BELCNTY
	BELCNTY
	1

	2026
	June
	MPASTNE5
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	1

	2026
	June
	DFRIILL8
	CARVER_TINSLE1_1
	CARVER
	TINSLEY
	1

	2026
	June
	SCOMHA38
	CARVER_TINSLE1_1
	CARVER
	TINSLEY
	1

	2026
	June
	SWAATH8
	FB_RS_60_A
	RS
	FB
	1

	2026
	June
	SJRESA28
	GABRIE_AT1
	GABRIE
	GABRIE
	1

	2026
	June
	SBRAPIN8
	GANSO_MAVERI1_1
	MAVERICK
	GANSO
	1

	2026
	June
	XVIC89
	MAGRUD_VICTOR2_1
	VICTORIA
	MAGRUDER
	1

	2026
	June
	SCOMHA38
	MAXWEL_WHITIN1_1
	MAXWELL
	WHITING
	1

	2026
	June
	SGRIRAP5
	MELONC_SEADRF1_1
	SEADRFTC
	MELONCRE
	1



© 2026 ERCOT
All rights reserved.		22
image2.png
Frequency Events & Average Duration

< o © N [ee]
< < ™ ™ N
L L L L L

SJUBAT JO JequinN
N

< (=] ©
N N - [ee] <
L L L L L

o

~{

9z-unr
- 9z-kei
- 9g-1dy
- 9z-1e
- 9¢-god
- 9z-uer

\. G¢-9°d
N\

- GZ-AON
GZ10
r Gg-des
- Gg-bny
eralily

- Gz-unp
- Ge-Rew
- Gg-idy
- GZ-1ei
- Gz-ge4
» Gg-uer
» 7¢-09(
- ¥Z-AON
- Y2100
yg-das
- yg-bny
Al

600 -

(spuo2as) uoneinqg jJuaAngz

ye-unr

o

Axis Title
—+—0.1 Hz Events Duration Standard Deviation (Seconds)

—a—Number of Events

~a- Average Duration (Seconds)





image3.svg
                                                                                                                    0  4  8  12  16  20  24  28  32  36  40  44  0  200  400  600  Jun-24  Jul-24  Aug-24  Sep-24  Oct-24  Nov-24  Dec-24  Jan-25  Feb-25  Mar-25  Apr-25  May-25  Jun-25  Jul-25  Aug-25  Sep-25  Oct-25  Nov-25  Dec-25  Jan-26  Feb-26  Mar-26  Apr-26  May-26  Jun-26  Axis Title      Average Duration (Seconds)      0.1 Hz Events Duration Standard Deviation (Seconds)      Number of Events   Frequency  Events & Average Duration  Event Duration  (Seconds)  Number of Events 


image4.png
IRR Output / Total ERCOT Load

100%

90%

80%

70%

60%

50%

40%

30%

20%

10%

0%

Solar Max

Jun-25

Monthly Max/Min/Avg Wind, Solar, IRR Output as a Percentage of Total ERCOT Load

BEEE Solar Avg Excl Night ~ mmmml Solar Avg Incl Night ~ E=Z3Wind Max  EEEEEWind Avg  mmmm Wind Min

«+®e« |RR Max

= m= «|RR Avg

Jul-25

Aug-25

Sep-25 Oct-25 Nov-25 Dec-25 Jan-26 Feb-26

Mar-26

Apr-26

May-26

=—=—|RR Min

Jun-26





image5.png
60%
55%
50%
45%

L 40%

3 35%

s 30%

$ 25%

£ 20%
15%
10%

5%
0%

Wind, Solar, IRR penetration during hour of Peak Load

Jun-25

Aug-25

mm \Wind mmmSolar mmmIRR —Peak Load

i

Oct-25

Dec-25

Feb-26

Apr-26

Jun-26

96,000
88,000
80,000
72,000
64,000
56,000
48,000
40,000
32,000
24,000
16,000
8,000

o

Peak Load (MW)




image6.svg
                              0  8,000  16,000  24,000  32,000  40,000  48,000  56,000  64,000  72,000  80,000  88,000  96,000  0%  5%  10%  15%  20%  25%  30%  35%  40%  45%  50%  55%  60%  Jun-25  Aug-25  Oct-25  Dec-25  Feb-26  Apr-26  Jun-26  Peak Load (MW)  % of Peak Load  Wind, Solar, IRR penetration during hour of Peak Load       Wind    Solar    IRR    Peak Load 


image7.png
% of Peak Load

Minimum Wind, Solar, IRR Output during the peak load hour as percentage of daily peak Load in June, 2026

B Wind M Solar H IRR " Monthly Peak Load Day

75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
0%

- NN T 0 © N~ 0 O O
= X = X =X = = = = =
© © ©W ©W ©W O ©O© © O =

6/11
6/12
6/13
6/14
6/15
6/16
6/17
6/18
6/19
6/20
6/21
6/22
6/23
6/24
6/25
6/26
6/27
6/28
6/29
6/30




image8.svg
                                                     0%  5%  10%  15%  20%  25%  30%  35%  40%  45%  50%  55%  60%  65%  70%  75%  6/1  6/2  6/3  6/4  6/5  6/6  6/7  6/8  6/9  6/10  6/11  6/12  6/13  6/14  6/15  6/16  6/17  6/18  6/19  6/20  6/21  6/22  6/23  6/24  6/25  6/26  6/27  6/28  6/29  6/30  % of Peak Load  Minimum Wind, Solar, IRR Output during the peak load hour as percentage of daily peak Load in June, 2026      Wind    Solar    IRR    Monthly Peak Load Day 


image9.png
90

80

70

60

5

o

4

o

3

o

2l

o

1

o

o

Number of DPCs Submitted By Month

Jun-25 Jul-25 Aug-25 Sep-25 Oct-25  Nov-25

= WIND ENERGY TRANSMISSION TEXAS LLC (TSP)
B TEXAS MUNICIPAL POWER AGENCY (TDSP)
uSHARYLAND UTILITIES LP (TDSP)
HPEDERNALES ELECTRIC CO OP INC (TDSP)
uLONE STAR TRANSMISSION LLC (TSP)

EERCOT

EDENTON MUNICIPAL ELECTRIC (TDSP)

B CENTERPOINT ENERGY HOUSTON ELECTRIC LLC (TDSP)
ECITY OF GARLAND (TDSP)

uCITY OF AUSTIN DBAAUSTIN ENERGY (TDSP)
uBROWNSVILLE PUBLIC UTILITIES BOARD (TDSP)
uAEP TEXAS COMPANY (TDSP)

Dec-25 Jan-26 Feb-26 Mar-26  Apr-26 May-26  Jun-26

B TEXAS-NEW MEXICO POWER CO (TDSP)

B SOUTH TEXAS ELECTRIC CO OP INC (TDSP)

= RAYBURN COUNTRY CO OP DBA RAYBURN ELECTRIC (TDSP)
©ONCOR ELECTRIC DELIVERY COMPANY LLC (TDSP)

= LCRA TRANSMISSION SERVICES CORPORATION (TDSP)
B ELECTRIC TRANSMISSION TEXAS LLC (TDSP)

HCROSS TEXAS TRANSMISSION LLC (TSP)

uCPS ENERGY (TDSP)

ECITY OF COLLEGE STATION (TDSP)

mBRYAN TEXAS UTILITIES (TDSP)

HBRAZOS ELECTRIC POWER CO OP INC (TDSP)




image10.svg
                                              0  10  20  30  40  50  60  70  80  90  Jun-25  Jul-25  Aug-25  Sep-25  Oct-25  Nov-25  Dec-25  Jan-26  Feb-26  Mar-26  Apr-26  May-26  Jun-26  Number of DPCs Submitted By Month    WIND ENERGY TRANSMISSION TEXAS LLC (TSP)    TEXAS-NEW MEXICO POWER CO (TDSP)    TEXAS MUNICIPAL POWER AGENCY (TDSP)    SOUTH TEXAS ELECTRIC CO OP INC (TDSP)    SHARYLAND UTILITIES LP (TDSP)    RAYBURN COUNTRY CO OP DBA RAYBURN ELECTRIC (TDSP)    PEDERNALES ELECTRIC CO OP INC (TDSP)    ONCOR ELECTRIC DELIVERY COMPANY LLC (TDSP)    LONE STAR TRANSMISSION LLC (TSP)    LCRA TRANSMISSION SERVICES CORPORATION (TDSP)    ERCOT    ELECTRIC TRANSMISSION TEXAS LLC (TDSP)    DENTON MUNICIPAL ELECTRIC (TDSP)    CROSS TEXAS TRANSMISSION LLC (TSP)    CENTERPOINT ENERGY HOUSTON ELECTRIC LLC (TDSP)    CPS ENERGY (TDSP)    CITY OF GARLAND (TDSP)    CITY OF COLLEGE STATION (TDSP)    CITY OF AUSTIN DBA AUSTIN ENERGY (TDSP)    BRYAN TEXAS UTILITIES (TDSP)    BROWNSVILLE PUBLIC UTILITIES BOARD (TDSP)    BRAZOS ELECTRIC POWER CO OP INC (TDSP)    AEP TEXAS COMPANY (TDSP) 


image1.png
ercot>




