June 2026 ERCOT Monthly Operations Report

Reliability and Operations Subcommittee Meeting

August 6, 2026

Table of Contents

1.	Report Highlights	2

2.	Frequency Control	3

2.1.	Frequency Events	3

2.2.	Automatic/Manual Load Resource Deployments	5

3.	Reliability Unit Commitment	6

4.	IRR, Wind, and Solar Generation as a Percent of Load	9

5.	Largest Net-Load Ramps	10

6.	Congestion Analysis	12

6.1.	Notable Constraints	12

6.2.	Generic Transmission Constraint Congestion	32

6.3.	Manual Overrides	32

6.4.	Congestion Costs for Calendar Year 2026	33

7.	System Events	34

7.1.	ERCOT Peak Load	34

7.2.	Load Shed Events	34

7.3.	Stability Events	34

7.4.	Notable PMU Events	35

7.5.	DC Tie Curtailment	35

7.6.	TRE/DOE Reportable Events	35

7.7.	New/Updated Constraint Management Plans	35

7.8.	New/Modified/Removed RAS	35

7.9.	New Procedures/Forms/Operating Bulletins	35

8.	Emergency Conditions	36

8.1.	OCNs	36

8.2.	Advisories	36

8.3.	Watches	36

8.4.	Emergency Notices	36

9.	Application Performance	36

9.1.	TSAT/VSAT Performance Issues	36

9.2.	Communication Issues	37

9.3.	Market System Issues	37

10.	Model Updates	37

Appendix A: Real-Time Constraints	40

# Report Highlights

The unofficial ERCOT peak load for June 2026 was 82,772 MW and occurred on 06/18/2026 during hour ending 17:00, this is 5,376 MW higher than the June 2025 peak demand of 77,396 MW on 06/19/2025

There were 10 frequency events.

There were no events which required automatic/manual deployment of Load Resources that were controlled by an Under-Frequency Relays.

There were 0 OCNs

There were 9 Advisories – All for ERCOT has postponed the deadline for the posting of the DAM solution for Operating Days: 06/07/26, 06/10/26, 06/11/26, 06/18/26, 06/19/26, 06/21/26, 06/24/26, 06/25/26, and 07/01/26 due to long solution run time.

There was 0 Watches.

There were 0 Emergency Notices.

There were 73 RUC commitments.

A Wind Generation Record of 29,031 MW was set on 06/29/2026 at 02:00.

A Renewable Generation Record of 52,063 MW was set on 06/27/2026 at 12:47.

The following GTCs saw congestion in June:

| GTC | Days Congestion |
| --- | --- |
| East Texas | 22 |
| Nelson Sharpe - Rio Hondo | 20 |
| North - Houston | 20 |
| West Texas | 18 |
| North Edinburg - Lobo | 18 |
| South Texas Export Pawnee - Spruce | 16 |
| Panhandle | 12 |
| South Texas Export Pawnee - Tango | 11 |
| McCamey | 8 |
| Zapata Starr | 4 |
| Treadwell | 2 |
| Valley Export | 2 |
| Kinney | 1 |
| South Texas Import Katoen - Lonhill | 1 |

# Frequency Control

## Frequency Events

The ERCOT Interconnection experienced 10 frequency events.

A summary of the frequency events is provided below. The reported frequency events meet one of the following criteria: Delta Frequency is 60 mHz or greater; the MW loss is 350 MW or greater; resource trip event triggered ECRS deployment. Frequency events that have been identified as Frequency Measurable Events (FME) for purposes of BAL-001-TRE-2 analysis are highlighted in blue. When analyzing frequency events, ERCOT evaluates PMU data according to industry standards. Events with an oscillating frequency of less than 1 Hz are inter-area, while higher frequencies indicate local events. Industry standards specify that damping ratio for inter-area oscillations should be 3.0% or greater. For the frequency event listed below, the ERCOT system met these standards and transitioned well after the disturbance. In the case of negative delta frequency, the MW Loss column could refer to load loss.

| Date and Time | Delta Frequency | Max/Min Frequency | Duration of Event | PMU Data |  | MW Loss | Load | IRR | Inertia |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | (Hz) | (Hz) |  | Oscillation Mode (Hz) | Damping Ratio |  | (MW) | % | (MW-s) |
| 6/1/2026 18:39:15 | 0.040 | 59.976 | 00:04:33 | 0.47 | 14% | 556 | 78,073 | 42% | 310,775 |
| 6/5/2026 7:39:19 | 0.049 | 59.969 | 00:01:36 | 0.67 | 11% | 453 | 53,778 | 21% | 283,413 |
| 6/5/2026 23:54:58 | 0.052 | 59.954 | 00:04:10 | 0.52 | 5% | 670 | 55,242 | 16% | 284,707 |
| 6/6/2026 8:23:20 | 0.057 | 59.950 | 00:04:50 | 0.79 | 12% | 708 | 51,991 | 18% | 280,207 |
| 6/14/2026 9:29:42 | 0.029 | 59.953 | 00:03:46 | 0.67 | 13% | 757 | 58,154 | 38% | 294,010 |
| 6/17/2026 23:25:00 | 0.063 | 59.928 | 00:05:27 | 0.58 | 6% | 1305 | 65,608 | 37% | 301,016 |
| 6/18/2026 15:25:45 | 0.054 | 59.961 | 01:05:27 | 0.61 | 12% | 588 | 82,184 | 51% | 299,663 |
| 6/20/2026 22:58:50 | 0.026 | 59.964 | 02:05:27 | 0.56 | 8% | 448 | 61,618 | 35% | 294,281 |
| 6/23/2026 9:15:20 | 0.046 | 59.964 | 03:05:27 | 0.26 | 11% | 710 | 64,225 | 53% | 278,149 |
| 6/23/2026 16:45:31 | 0.021 | 59.957 | 04:05:27 | 0.55 | 10% | 400 | 81,704 | 52% | 286,117 |

(Note: All data on this graph encompasses frequency event analysis based on BAL-001-TRE-2.)

## Automatic/Manual Load Resource Deployments

| Resource Location | # of Resources | Operating Day | Total # of Hours Committed | Total MWhs | Reason for Commitment | MWs of ECRS Deployed | MWs of RRS Deployed |
| --- | --- | --- | --- | --- | --- | --- | --- |

There were no events which required automatic/manual deployment of Load Resources that were controlled by an Under-Frequency Relays.

# Reliability Unit Commitment

ERCOT reports on Reliability Unit Commitments (RUC) monthly. Commitments are reported grouped by operating day and weather zone. The total number of hours committed is the sum of the hours for all the units in the specified region. Additional information on RUC commitments can be found on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

There were 73 RUC commitments.

| Resource Location | # of Resources | Operating Day | Total # of Hours Committed | Total MWhs | Reason for Commitment |
| --- | --- | --- | --- | --- | --- |
| NORTH_CENTRAL | 4 | June 1, 2026 | 20 | 2,184.0 | System Capacity |
| NORTH_CENTRAL | 3 | June 2, 2026 | 24 | 1,536.0 | DCDHTVW5 |
| NORTH_CENTRAL | 1 | June 3, 2026 | 4 | 956.0 | System Capacity |
| COAST, NORTH_CENTRAL | 4 | June 6, 2026 | 23 | 2,459.5 | System Capacity |
| EAST, NORTH, NORTH_CENTRAL | 3 | June 9, 2026 | 13 | 4,664.9 | SHC2EXC5 |
| NORTH, NORTH_CENTRAL, SOUTH_CENTRAL | 3 | June 10, 2026 | 14 | 4,225.2 | SHC2EXC5, SHCKEXC5 |
| EAST, NORTH_CENTRAL | 3 | June 14, 2026 | 13 | 4,328.0 | System Capacity |
| EAST, NORTH_CENTRAL | 4 | June 15, 2026 | 19 | 6,385.0 | System Capacity |
| EAST, NORTH, NORTH_CENTRAL | 6 | June 16, 2026 | 26 | 8,738.0 | SCRDJON5, System Capacity |
| EAST, NORTH_CENTRAL, SOUTHERN | 9 | June 18, 2026 | 47 | 12,600.0 | SCRDJON5, SHC2EXC5, System Capacity |
| COAST, EAST, NORTH_CENTRAL | 12 | June 19, 2026 | 127 | 34,846.0 | System Capacity |
| NORTH_CENTRAL | 1 | June 20, 2026 | 7 | 3,976.0 | System Capacity |
| EAST, NORTH, NORTH_CENTRAL | 9 | June 22, 2026 | 50 | 14,577.8 | E_PASP, System Capacity |
| NORTH_CENTRAL | 1 | June 23, 2026 | 4 | 1,568.0 | SHC2EXC5 |
| NORTH, NORTH_CENTRAL | 6 | June 24, 2026 | 44 | 4,629.1 | SHC2EXC5 |
| EAST, NORTH, NORTH_CENTRAL | 3 | June 29, 2026 | 13 | 4,485.9 | SHC2EXC5, SHCKEXC5 |
| NORTH_CENTRAL | 1 | June 30, 2026 | 8 | 967.0 | SHC2EXC5 |

# IRR, Wind, and Solar Generation as a Percent of Load

The graph below shows the maximum, minimum and average aggregate solar, wind and IRR output as a percentage of total ERCOT load when evaluated as 10-minute averaged intervals, over the past 13 months. Current wind and solar generation and penetration records are listed in the footnote below. Maximum IRR penetration for June 2026 was 76.88% on 6/28/2026 interval ending 09:40 and minimum IRR penetration for June 2026 was 3.97%on 6/16/2026 interval ending 06:20.

During the hour of peak load for the month, hourly integrated wind generation was 12,576 MW and solar generation was 27,353 MW. The graph below shows the wind and solar penetration percentage during the hour of the peak load in the last 13 months.

Lastly, the graph below shows the minimum wind, solar, and IRR output during the peak load hour as a percentage of the daily peak load for every day in the month.

# Largest Net-Load Ramps

The net-load ramp is defined as the change in net-load (load minus wind and PVGR generation) during the defined time horizon. Such a variation in net-load needs to be accommodated in grid operations to ensure that the reliability of the grid is satisfactorily maintained. The largest net-load ramps over 5-minute, 10-minute, 15-minute, 30-minute, and 60-minute intervals in June 2026 were 1,891 MW, 2,649 MW, 3,976 MW, 6,380 MW, and 11,157 MW respectively. A comparison with historical values is provided in the table below.

| Month and Year | 5 min | 10 min | 15 min | 30 min | 60 min |
| --- | --- | --- | --- | --- | --- |
| Jun-15 | 1,038 MW | 1,771 MW | 2,489 MW | 3,119 MW | 5,360 MW |
| Jun-16 | 1,183 MW | 1,716 MW | 2,148 MW | 3,131 MW | 5,975 MW |
| Jun-17 | 751 MW | 1,287 MW | 1,772 MW | 3,106 MW | 5,573 MW |
| Jun-18 | 1,029 MW | 1,413 MW | 2,035 MW | 3,590 MW | 6,320 MW |
| Jun-19 | 824 MW | 1,284 MW | 1,706 MW | 2,985 MW | 5,684 MW |
| Jun-20 | 902 MW | 1,615 MW | 2,340 MW | 3,726 MW | 7,015 MW |
| Jun-21 | 1,442 MW | 2,157 MW | 2,646 MW | 3,468 MW | 5,963 MW |
| Jun-22 | 1,064 MW | 1,588 MW | 2,166 MW | 4,035 MW | 7,866 MW |
| Jun-23 | 1,044 MW | 1,672 MW | 2,316 MW | 4,075 MW | 7,845 MW |
| Jun-24 | 1,978 MW | 2,883 MW | 3,466 MW | 4,547 MW | 7,498 MW |
| Jun-25 | 1,653 MW | 2,416 MW | 3,334 MW | 5,516 MW | 10,007 MW |
| Jun-26 | 1,891 MW | 2,649 MW | 3,976 MW | 6,380 MW | 11,157 MW |
|  | 6/11/2026 | 6/11/2026 | 6/11/2026 | 6/24/2026 | 6/24/2026 |
|  | (IE 19:14) | (IE 19:17) | (IE 19:24) | (IE 19:28) | (IE 19:39) |
| All Months in 2015-2026 | 3,797 MW | 3,901 MW | 5,018 MW | 9,696 MW | 18,089 MW |
|  | 5/28/2025 | 5/3/2026 | 2/24/2025 | 2/24/2025 | 4/6/2026 |
|  | (IE 10:27) | (IE 18:40) | (IE 17:39) | (IE 17:51) | (IE 19:17) |

# Congestion Analysis

## Notable Constraints

Nodal protocol section 3.20 specifies that ERCOT shall identify transmission constraints that are binding in Real-Time three or more Operating Days within a calendar month. As part of this process, ERCOT reports congestion that meets this criterion to ROS. In addition, ERCOT also highlights notable constraints that have an estimated congestion rent exceeding $1,000,000 for a calendar month. These constraints are detailed in the table below, including approved transmission upgrades from TPIT that may provide some congestion relief based on ERCOT’s engineering judgement. Rows highlighted in blue indicate the congestion was affected by one or more outages. For a list of all constraints activated in SCED, please see Appendix A at the end of this report.

| Data Item1 | Contingency Name | Overloaded Element | Contingency Name | Overloaded Element | # of Days Constraint Binding | Congestion Rent | Transmission Project |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| n/a_n/a_WESTEX | BASE CASE | WESTEX | Basecase | WESTEX GTC | 16 | $24,599,695.49 |  | Permian Basin Reliability Plan (765-kV import paths) (The PUCT approved ,helps improve, but not fully exit, the GTC yet.) |
| HCKSW_EXCSW_107__B | SHC2EXC5 | 107__B | HICKS SWITCH to EXCHANGE SWITCH LIN _C | Hicks Switch - Exchange Switch 345kV | 17 | $11,305,932.80 |  |  |
| STP_WAP_STPWAP39_1 | DWPWFWP5 | STPWAP39_1 | TWR(345) WAP-WLF64 & WAP-WLY72 | South Texas Project - Wa Parish 345kV | 17 | $9,197,686.14 |  |  |
| TREADWEL_YELWJCKT_TREADW_YELWJC1_1 | DBIGKEN5 | TREADW_YELWJC1_1 | Bighil-Kendal 345kV | Yellow Jacket - Treadwell 138kV | 21 | 6,773,732.89 |  |  |
| MDO_PHR_MDOPHR99_A | DWAP_OB5 | MDOPHR99_A | TWR (345) OB-WAP98 & OB-WAP99 | Meadow - Ph Robinson 345kV | 14 | 6,423,280.32 |  | CNP_28TPIT103344_PH_Robinson_to_WA_Parish_Hardening (MOD 103344 Phase 103435, 25RPG028) |
| ZEN_THW_THWZEN98_A | DRNS_TB5 | THWZEN98_A | Rns-Rtw & Sng-Tb 345kV | Th Wharton - Zenith 345kV | 15 | 5,789,582.08 |  |  |
| HHGT_OMEGA_HHGTOM_1 | BASE CASE | HHGTOM_1 | Basecase | Omega - Horse Hollow Generation Tie 345kV | 14 | 4,476,204.86 |  |  |
| CMNSW_CMNTP_651__B | SCMNCPS5 | 651__B | COMANCHE SWITCH (Oncor) to COMANCHE PEAK SES LIN _A | Comanche Tap - Comanche Switch (Oncor) 138kV | 16 | 4,411,731.13 |  |  |
| LNGSW_PRLSW_6965__A | DBAKCED5 | 6965__A | BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Longshore Switch - Prairieland Switch 345kV | 12 | 4,295,502.41 |  | Oncor_FW_81268_Longshore – Consavvy 345 kV Double-Circuit Line Rebuild (MOD 81268, 23RPG034) |
| SAMSW_VENSW_35055__A | SVENFTS5 | 35055__A | FORT SMITH SWITCH to FORT SMITH SWITCH LIN _B | Sam Switch - Venus Switch 345kV | 7 | $4,139,470.13 |  | Rebuild Sam Switch - Venus Switch 345 kV DCKT (78369) |
| MGSES_CATSW_6945__A | SRGRMGS5 | 6945__A | MORGAN CREEK SES to RANGER CAMP SWITCH LIN _A | Morgan Creek Ses - Cattleman Switch 345kV | 12 | $4,112,471.33 |  | West Texas 345-kV Infrastructure Rebuild Project (23RPG034) |
| MDO_PHR_MDOPHR99_A | DPHRCTR5 | MDOPHR99_A | Ctr-Phr&Cby 345kV | Meadow - Ph Robinson 345kV | 19 | $3,956,968.83 |  | CNP_28TPIT103344_PH_Robinson_to_WA_Parish_Hardening (MOD 103344 Phase 103435, 25RPG028) |
| n/a_n/a_NE_LOB | BASE CASE | NE_LOB | Basecase | NE_LOB GTC | 15 | $3,748,214.22 |  | San Antonio South Reliability I Project (22RPG048) LRGV Transmission Improvement Project (21RPG017) San Antonio South Reliability II Project (23RPG032) |
| SCRCV_KNAPP_6437__F | DMTSCOS5 | 6437__F | DMTSW TO SCOSW 345 DBLCKT | Knapp - Scurry Chevron 138kV | 23 | $3,532,632.19 |  | Oncor_FW_102849_Union 138 kV Switch (MOD 102849) |
| BCKSW_CGRSW_6215__A | DSCOTKW5 | 6215__A | SCOSW TO TKWSW 345 DBLCKT | Bluff Creek Switch - China Grove Switch 138kV | 14 | $3,343,071.80 |  |  |
| TMPSW_FRYSW_1715__B | DSALHUT5 | 1715__B | SALSW - HUTTO 345KV | Temple Switch - Fryers Creek 138kV | 10 | $3,199,619.59 |  | ONCOR_SE_87677_Fryers_Creek_Temple_138 kVLine (MOD 87677) |
| SALDS_SONTERRA_1710__A | DSALHUT5 | 1710__A | SALSW - HUTTO 345KV | Salado South - Sonterra 138kV | 8 | $2,854,510.16 |  |  |
| WLVSW_GAILS_6217__A | SVEAW_L5 | 6217__A | wett_long_draw to VEALMOOR - Sharyland Utilities LIN 1 | Willow Valley Switch - Gail Sub 138kV | 17 | $2,769,950.60 |  |  |
| TWINBU_HARGROVE_HARGRO_TWINBU1_1 | DBAKCED5 | HARGRO_TWINBU1_1 | BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Hargrove - Twin Buttes 138kV | 6 | $2,727,482.14 |  |  |
| SEA_SEA_SEA_AAT1 | DFRYBC58 | SEA_AAT1 | DOUBLE KNBSW-SALSW 345 & FRYSW-BELCNTY 138 | Seaton 138kV | 3 | $2,533,065.50 |  |  |
| ODEHV_ODEHV_ODEHV_MR3H | DODEMOS5 | ODEHV_MR3H | ODEHV-MOSSW 345&ODEHV-WLFSW 345_DBLCKT | Odessa Ehv Switch 345kV | 1 | $2,434,265.25 |  |  |
| LPLMK_LPLNE_LPLMK_LPLNE_1 | SBWDDBM5 | LPLMK_LPLNE_1 | BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1 | Mackenzie Substation - Northeast Substation 115kV | 18 | $2,404,826.67 |  |  |
| n/a_n/a_NELRIO | BASE CASE | NELRIO | Basecase | NELRIO GTC | 19 | $2,116,049.89 |  | The Lower Rio Grande Valley (LRGV) System Enhancement Project (21RPG017) |
| BRTSW_JUNPR_12020__B | DLONPK25 | 12020__B | DBL_PKRSW-GRSES_PKRSW-LONSW_345KV | Barton Chapel Wind Farm - Juniper Sub 138kV | 11 | $1,962,717.99 |  |  |
| GN_PZ_GN_PZ_08_A | SMDOOAS5 | GN_PZ_08_A | MEADOW to OASIS LIN A | Grant - Plaza 138kV | 11 | $1,891,074.10 |  |  |
| GRSES_GRMES_6375__A | DLONPK25 | 6375__A | DBL_PKRSW-GRSES_PKRSW-LONSW_345KV | Graham Ses - Graham East 138kV | 12 | $1,812,604.65 |  |  |
| WLY_WAP_WAPWLY72_A | DBLW2JC5 | WAPWLY72_A | TWR (345) JCK-WAT62 & BLY-JCK57 | Wa Parish - Whaley 345kV | 15 | $1,804,892.20 |  |  |
| BERGHE_BERGHE_BERGHE_AT1H | DZORHAY5 | BERGHE_AT1H | ZORN - HAYSEN 345KV | Bergheim 345kV | 9 | $1,714,519.62 |  |  |
| JN_BI_BI_JN_64_A | DWAP_BI5 | BI_JN_64_A | TWR (345) WAP-BI50 & SMITHERS-BI98 | Bellaire - Jeanetta 345kV | 10 | $1,705,103.22 |  |  |
| NEWMAN_WALNUT1_NEWM_WAL_1 | SOAKSHI8 | NEWM_WAL_1 | OAKLAND SUBSTATION to SHILOH LIN 1 | Newman - Walnut 138kV | 2 | $1,571,582.71 |  | GPL_TPIT_110733_WylieSW_LCP_Upgrades_Walnut_Newman_Line (MOD: 110733) |
| MADDUX_TREADWEL_MADDUX_TREADW1_1 | DBIGKEN5 | MADDUX_TREADW1_1 | Bighil-Kendal 345kV | Maddux - Treadwell 138kV | 12 | $1,563,081.23 |  |  |
| SAMSW_FVLSW_35045__A | SHELBUL5 | 35045__A | HELIX to BULLOCK LIN 1A | Sam Switch - Files Valley Switch 345kV | 6 | $1,561,357.23 |  |  |
| LAKENASW_SAMATHIS_LAKENA_SAMATH1_1 | DBAKCED5 | LAKENA_SAMATH1_1 | BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Lake Nasworthy - San Angelo Mathis Field 69kV | 15 | $1,554,976.98 |  |  |
| MV_HBRG4_MV_WESL4_WESLCO_HIDLBRG_1 | MHARNED5 | WESLCO_HIDLBRG_1 | Manual dbl ckt for NEDIN-BONILLA 345kV & RIOH-PRIM138kV | Heidelburg Sub - Weslaco Sub 138kV | 13 | $1,434,928.70 |  | STEC_71928_Heidelberg_AEPWeslaco_Upgrade (MOD 71928) |
| CRDSW_OLNEY_6830__B | DGRMGRS8 | 6830__B | FIREROCK TO BRNWD 138 AND FIREROCK TO BANGS 69 DBLCKT | Cottonwood Road Switch - Olney Pod 69kV | 17 | $1,402,318.38 |  |  |
| FMRVL_RYSSW_400__A | SFMRRYS5 | 400__A | Farmersville Switch to Farmersville Switch LIN _A | Royse Switch - Farmersville Switch 345kV | 11 | $1,373,314.95 |  | ONCOR_MNE_99066_Royse Switch – Farmersville Switch 345 kV Double-Circuit Line (MOD 99066, 25RPG004) |
| CONCHO_VRBS_CONCHO_VRBS1_1 | SCRMSAR8 | CONCHO_VRBS1_1 | SAN ANGELO RED CREEK to BALLINGER LIN 1 | San Angelo Concho - Veribest 69kV | 5 | $1,334,261.76 |  |  |
| BCPSW_AZLES_6275__D | DCMBCPS8 | 6275__D | CPSES-CMBSW & CMDSW-HOD 138_DBLCKT | Base Camp Switch - Azle Sub (Oncor) 138kV | 2 | $1,299,247.76 |  |  |
| n/a_n/a_EASTEX | BASE CASE | EASTEX | Basecase | EASTEX GTC | 19 | $1,250,368.94 |  |  |
| SALDS_SONTERRA_1710__A | SANDFLO8 | 1710__A | ANDICE to FLORENCE LIN 1 | Salado South - Sonterra 138kV | 1 | $1,232,470.21 |  |  |
| BIGHIL_OERSTED_225T558_1 | DBAKCED5 | 225T558_1 | BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Big Hill - Orsted 345kV | 5 | $1,231,901.43 |  |  |
| FROWS_MCLSW_1025__B | SMC2WEA8 | 1025__B | MCLANE SWITCH to WACO EAST LIN _C | Mclane Switch - Frow Sub 138kV | 6 | $1,145,501.29 |  |  |
| CMNSW_CMNTP_651__B | DBUCRGP5 | 651__B | MANUAL DOUBLE RGPSW - KLNSW 345 KV & BUCSW - KLNSW 345 KV | Comanche Tap - Comanche Switch (Oncor) 138kV | 11 | $1,124,615.16 |  |  |
| PALOUSE_WOLFCAMP_PALOUS_WOLFCA1_1 | DBIGSCH5 | PALOUS_WOLFCA1_1 | Big Hill - Schneeman Draw & Big Hill - Schneeman Draw 2 | Palouse - Wolfcamp 138kV | 13 | $1,123,582.60 |  |  |
| KENDAL_BERGHE_656T656_1 | DCAGCO58 | 656T656_1 | Cagnon-Kendal 345 & Cico-Comfor 138 | Bergheim - Kendall 345kV | 6 | $1,026,161.65 |  |  |
| SALDS_SONTERRA_1710__A | DGABAN89 | 1710__A | Double contingency GABRIE-ANDUIN 69kV & GABRIE-GLASSC | Salado South - Sonterra 138kV | 1 | $1,012,566.34 |  |  |
| FROWS_MCLSW_1025__B | SMCLWNE8 | 1025__B | MCLANE SWITCH to WACO NORTHEAST TAP LIN _A | Mclane Switch - Frow Sub 138kV | 10 | $958,239.47 |  |  |
| FBRSW_THSES_505__B | DVENFTS5 | 505__B | VENSW-FTSSW & VENSW-SAMSW 345 DBLCKT | Tradinghouse Ses - Four Brothers Switch 345kV | 5 | $956,164.49 |  |  |
| YELWJCKT_FORTMA_FORTMA_YELWJC1_1 | DBIGKEN5 | FORTMA_YELWJC1_1 | Bighil-Kendal 345kV | Yellow Jacket - Fort Mason 138kV | 12 | $871,998.89 |  |  |
| PAWNEE_CALAVERS_PAWNEE_SPRUCE_1 | DELMSAN5 | PAWNEE_SPRUCE_1 | Elmcreek-Sanmigl 345kV | Pawnee Switching Station - Calaveras 345kV | 7 | $862,145.19 |  |  |
| HONDOCK_DEVINESW_HON_DEVI_1 | SHONF38 | HON_DEVI_1 | HONDO to HONDO CREEK SWITCHING STATION LIN 1 | Hondo Creek Switching Station - Devine Switch 69kV | 16 | $838,357.55 |  |  |
| NLARSW_PILONCIL_NLARSW_PILONC1_1 | DFOAVLO5 | NLARSW_PILONC1_1 | FOWLERTON to LOBO & AVANZADA | North Laredo Switch - Piloncillo 138kV | 16 | $765,976.14 |  |  |
| CRDSW_OLNEY_6830__B | SGRMGRS8 | 6830__B | GRAHAM EAST to GRAHAM EAST LIN _A | Cottonwood Road Switch - Olney Pod 69kV | 7 | $760,461.65 |  |  |
| n/a_n/a_E_PASP | BASE CASE | E_PASP | Basecase | E_PASP GTC | 13 | $670,228.21 |  | San Antonio South Reliability I Project , 22RPG048 LRGV Transmission Improvement Project (21RPG017) San Antonio South Reliability II Project (23RPG032) |
| n/a_n/a_PNHNDL | BASE CASE | PNHNDL | Basecase | PNHNDL GTC | 7 | $664,919.25 |  |  |
| TYPRK_PLYAM_6200__F | DCDHTVW5 | 6200__F | TVWSW TO CDHSW 345 AND CDHSW TO VENSW 345 DBLCKT | Poly-America - Tyre Park Sub 138kV | 11 | $579,064.82 |  |  |
| MRVLY_ESTLD_6635__G | SCLCGTN8 | 6635__G | COLONY CREEK to GHOST TOWN SWITCH LIN _A | Morton Valley (Oncor) - Eastland 69kV | 8 | $576,525.82 |  |  |
| NUECES_B_WHITE_PT_NUECES_WHITE_2_1 | SMAYWHI8 | NUECES_WHITE_2_1 | GILA to MAYO LIN 1 | Nueces Bay - Whitepoint 138kV | 10 | $562,190.59 |  |  |
| FROWS_MCLSW_1025__B | SELMTH25 | 1025__B | ELM MOTT to ELM MOTT LIN _A | Mclane Switch - Frow Sub 138kV | 16 | $561,694.22 |  |  |
| FMRVL_RYSSW_381__A | SFMRRY25 | 381__A | Farmersville Switch to ROYSE SWITCH LIN _A | Farmersville Switch - Royse Switch 345kV | 8 | $535,265.06 |  |  |
| LNGSW_PRLSW_6965__A | MCATPRL5 | 6965__A | MAN_SGL_CATSW-PRLSW_345KV | Longshore Switch - Prairieland Switch 345kV | 4 | $525,813.46 |  | Oncor_FW_81268_Longshore – Consavvy 345 kV Double-Circuit Line Rebuild (MOD 81268, 23RPG034) |
| FRONTERA_S_MISSIN_BENTS_FRTER_1B_1 | SSHAFRO8 | BENTS_FRTER_1B_1 | FRONTERA to SHARYLAND LIN 1 | Frontera - South Mission 138kV | 16 | $456,570.55 |  |  |
| NVKSW_ANARN_6840__B | DMGSRIC8 | 6840__B | DBL_CKT_GRSES-RICSW_138 kV and GRSES-SGRAS_138 kV | Anarene - Navy Kickapoo Switch 69kV | 15 | $443,991.07 |  |  |
| KLNSW_HHSTH_630__B | DSALKLN5 | 630__B | SALSW TO KLNSW 345 DBLCKT | Harker Heights South - Killeen Switch 138kV | 3 | $379,367.43 |  | ONCOR_SE_87699_Belton - Killeen 138 kV_Line (MOD 87699, 24RPG001) |
| FARMLAND_W_LD_345_FARMLAND_LONGD_1 | DCOTWR25 | FARMLAND_LONGD_1 | DBL_CKT_W_CS_345-WRASW_345KV_ln70155_A-WHIT_RV_W_CW1 | Farmland - Wett_Long_Draw 345kV | 6 | $377,136.62 |  |  |
| ANGLETON_WCOLLOCL_G138_15_1 | SWCOWCO8 | G138_15_1 | WEST COLUMBIA MAIN TNP to ANGLETON TNP LIN 1 | West Columbia Local Tnp - Angleton Tnp 138kV | 4 | $349,722.23 |  |  |
| WFSSW_NSTAR_6085__E | DRILKRW5 | 6085__E | RILEY TO KRWSW 345 DBLCKT | North Star - Wichita Falls South Switch 138kV | 3 | $330,622.12 |  |  |
| BCESW_SNDSW_421__A | SSNDBGR5 | 421__A | SANDOW SWITCH to BADGER SWITCH LIN _A | Sandow Switch - Bell County East Switch 345kV | 5 | $320,852.44 |  |  |
| ZEN_THW_THWZEN71_A | DRNS_TB5 | THWZEN71_A | Rns-Rtw & Sng-Tb 345kV | Th Wharton - Zenith 345kV | 3 | $312,199.16 |  |  |
| FOWLRTON_TILDEN_FWLRTN_TILDEN_1 | DFOWSMG5 | FWLRTN_TILDEN_1 | FOWLRTON TO SAN MIGUEL DOUBLE CIRCUIT CONTINGENCY | Fowlerton - Tilden 138 Sub 138kV | 7 | $296,934.16 |  |  |
| PALOUSE_CROSSOVE_CROSSO_PALOUS1_1 | SWOLPAL8 | CROSSO_PALOUS1_1 | PALOUSE to Wolfcamp LIN 1 | Crossover - Palouse 138kV | 11 | $277,374.62 |  |  |
| HI_LONE_CEDACA_HI_LONE_TLINE_1 | BASE CASE | HI_LONE_TLINE_1 | Basecase | Cedar Canyon - High Lonesome 345kV | 3 | $273,172.73 |  |  |
| n/a_n/a_MCCAMY | BASE CASE | MCCAMY | Basecase | MCCAMY GTC | 6 | $245,247.16 |  |  |
| HECKER_RESNIK_HECKER_RESNIK1_1 | DMCDUPS8 | HECKER_RESNIK1_1 | MCCAMPBE - RESNIK & I_DUPSW 138kV | Hecker - Resnik 138kV | 8 | $242,624.27 |  | Rebuild the Hecker to Resnik 138 kV line 76286 |
| HOWARD_LEON_CRK_D5_S1_1 | SP5CAG8 | D5_S1_1 | CAGNON to CAGNON LIN 1 | Leon Creek - Howard 138kV | 6 | $228,802.09 |  |  |
| BRUNI_BRUNI_BRUNI_69_1 | DFOAVLO5 | BRUNI_69_1 | FOWLERTON to LOBO & AVANZADA | Bruni Sub 138kV | 7 | $225,807.32 |  |  |
| BGRSW_SNDSW_455__A | SBCESN35 | 455__A | BELL COUNTY EAST SWITCH to BELL COUNTY EAST SWITCH LIN _A | Badger Switch - Sandow Switch 345kV | 6 | $225,262.75 |  |  |
| SACRC_DPCRK_6240__C | DMTSCOS5 | 6240__C | DMTSW TO SCOSW 345 DBLCKT | Sacroc - Deep Creek Sub 138kV | 5 | $218,288.86 |  |  |
| FLTSW_PRSSW_1545__A | SPRSPAR8 | 1545__A | PARIS SWITCH to PARIS LIN _A | Paris Switch - Flying Tiger Switch 138kV | 11 | $199,040.49 |  |  |
| SEA_SEA_SEA_AAT1 | DFRYTM58 | SEA_AAT1 | DOUBLE FRYSW-TMPSW 138 & KNBSW-SALSW 345 | Seaton 138kV | 6 | $183,848.68 |  |  |
| LAKENASW_SAMATHIS_LAKENA_SAMATH1_1 | SBGLTWI8 | LAKENA_SAMATH1_1 | TWIN BUTTES to HARGROVE LIN 1 | Lake Nasworthy - San Angelo Mathis Field 69kV | 4 | $176,714.15 |  |  |
| PALOUSE_WOLFCAMP_PALOUS_WOLFCA1_1 | DBIGKEN5 | PALOUS_WOLFCA1_1 | Bighil-Kendal 345kV | Palouse - Wolfcamp 138kV | 4 | $157,547.07 |  |  |
| LNGSW_PRLSW_6965__A | DSLKNOR5 | 6965__A | Double NORTMC-SLKSW&SLKSW 345kV | Longshore Switch - Prairieland Switch 345kV | 4 | $151,765.98 |  | Oncor_FW_81268_Longshore – Consavvy 345 kV Double-Circuit Line Rebuild (MOD 81268, 23RPG034) |
| PIPECR_MEDILA_255T279_1 | DCAGCI58 | 255T279_1 | Cagnon-Kendal 345 &Cico-Mengcr 138 | Medina Lake - Pipe Creek 138kV | 4 | $130,608.88 |  |  |
| MEXTP_ITALY_2270__B | SBLURDH8 | 2270__B | BLUM to RED HILL SWITCH LIN _G | Milford Exxon Tap - Italy 69kV | 9 | $125,443.06 |  |  |
| WCOLLOCL_ANGLETON_G138_15_1 | SWCOWCO8 | G138_15_1 | WEST COLUMBIA MAIN TNP to ANGLETON TNP LIN 1 | West Columbia Local Tnp - Angleton Tnp 138kV | 4 | $118,776.46 |  |  |
| BOW_BOW_BOW_FMR1 | DRILKRW5 | BOW_FMR1 | RILEY TO KRWSW 345 DBLCKT | Bowie 138kV | 5 | $114,491.53 |  |  |
| NORTMC_CROSSOVE_CROSSO_NORTMC1_1 | DBIGSCH5 | CROSSO_NORTMC1_1 | Big Hill - Schneeman Draw & Big Hill - Schneeman Draw 2 | North Mccamey - Crossover 138kV | 4 | $114,092.20 |  |  |
| BRUNI_BRUNI_BRUNI_69_1 | SLAQLOB8 | BRUNI_69_1 | LAQUINTA to LOBO LIN 1 | Bruni Sub 138kV | 11 | $113,181.29 |  |  |
| LA_PALMA_HAINE_DR_HAINE__LA_PAL1_1 | SRAYRI38 | HAINE__LA_PAL1_1 | LAS PULGAS to RAYMONDVILLE 2 LIN 1 | Haine Drive - La Palma 138kV | 8 | $112,429.32 |  |  |
| HAYSEN_ZORN_6T227_1 | SHAYZO25 | 6T227_1 | HAYS ENERGY to ZORN LIN 1 | Zorn - Hays Energy 345kV | 3 | $104,704.19 |  |  |
| PALOUSE_CROSSOVE_CROSSO_PALOUS1_1 | DBAKCED5 | CROSSO_PALOUS1_1 | BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Crossover - Palouse 138kV | 8 | $90,059.35 |  |  |
| DILLEYSW_DILLEYSW_DILLEYSW_XF1H | DDILCOT8 | DILLEYSW_XF1H | Dilleysw-Sanmgsw&Cotulas 138kV | Dilley Switch Aep 138kV | 3 | $57,160.15 |  |  |
| MADDUX_SAPOWER_MADDUX_SAPOWE1_1 | SMA2SAP8 | MADDUX_SAPOWE1_1 | MADDUX to SAN ANGELO POWER STATION LIN 1 | Maddux - San Angelo Power Station 138kV | 8 | $47,785.75 |  |  |
| MAXWELL_HAMILTON_HAMILT_MAXWEL1_1 | DBIGKEN5 | HAMILT_MAXWEL1_1 | Bighil-Kendal 345kV | Hamilton Road - Maxwell 138kV | 10 | $46,122.83 |  |  |
| HAMILTON_MAVERICK_HAMILT_MAVERI1_1 | SBRAPIN8 | HAMILT_MAVERI1_1 | BRACKETTVILLE to BRACKETTVILLE LIN 1 | Hamilton Road - Maverick 138kV | 6 | $44,729.18 |  |  |
| KNBSW_TMPSW_270__A | DSALHUT5 | 270__A | SALSW - HUTTO 345KV | Temple Switch - Knob Creek Switch 345kV | 3 | $42,723.74 |  |  |
| TNNALVIN_ALVIN_138_ALV_NAL_1 | SMDOPHR5 | 138_ALV_NAL_1 | MEADOW to PH ROBINSON LIN A | North Alvin Tnp - Alvin Tnp 138kV | 11 | $39,746.53 |  |  |
| ASHERTON_CATARINA_ASHERT_CATARI1_1 | DLOFOAV5 | ASHERT_CATARI1_1 | Double LOBO - FOWLERTON & AVANZADA | Asherton - Catarina 138kV | 4 | $39,063.62 |  |  |
| SNYDR_SNYDR_SNYDR_FMR1 | SSNYCGR8 | SNYDR_FMR1 | SNYDER to CHINA GROVE SWITCH LIN _A | Snyder 138kV | 8 | $38,313.49 |  |  |
| NUECES_B_WHITE_PT_NUECES_WHITE_2_1 | SWHILON5 | NUECES_WHITE_2_1 | LON HILL to WHITEPOINT LIN 1 | Nueces Bay - Whitepoint 138kV | 3 | $35,699.23 |  |  |
| MEXTP_ITALY_2270__B | SBLAWDB8 | 2270__B | BLANTON to WOODBURY SWITCH LIN _C | Milford Exxon Tap - Italy 69kV | 3 | $24,387.53 |  |  |
| CARVER_TINSLEY_CARVER_TINSLE1_1 | DBIGKEN5 | CARVER_TINSLE1_1 | Bighil-Kendal 345kV | Carver - Tinsley Tap 138kV | 3 | $23,302.22 |  |  |
| RAYBURN_L_463S_RAY_L_46_1 | SFURVAN8 | RAY_L_46_1 | FURHMAN to VANDERBILT SWITCHING STATION LIN 1 | Sam Rayburn Switchyd - Loop 463 Sub 138kV | 4 | $20,973.73 |  |  |
| SOLSTICE_SOLSTICE_SOLSTICE_PST1 | DBAKSOL5 | SOLSTICE_PST1 | Bakersfield - Solstice line 1 and 2 | Solstice 138kV | 7 | $20,671.48 |  |  |
| HAINE_DR_OLEANDER_HAINE__OLEAND1_1 | SRAYRI38 | HAINE__OLEAND1_1 | LAS PULGAS to RAYMONDVILLE 2 LIN 1 | Oleander - Haine Drive 138kV | 3 | $20,186.64 |  |  |
| FURHMAN_RAYBURN_RAYBUR_FURHMAN_1 | SFURVAN8 | RAYBUR_FURHMAN_1 | FURHMAN to VANDERBILT SWITCHING STATION LIN 1 | Sam Rayburn Switchyd - Furhman 138kV | 12 | $19,189.46 |  |  |
| CATARINA_ASHERTON_ASHERT_CATARI1_1 | DLOFOAV5 | ASHERT_CATARI1_1 | Double LOBO - FOWLERTON & AVANZADA | Asherton - Catarina 138kV | 4 | $18,345.14 |  |  |
| LOBO_LARDVNTH_LARDVN_LOBO2_1 | MLARDUS8 | LARDVN_LOBO2_1 | Manuel LAREDO VFT NORTH to Dust Devil LIN 1 | Lobo - Laredo Vft North 138kV | 4 | $14,420.52 |  |  |
| BIG_FOOT_PLEASANT_BIG_FO_PLEASA1_1 | SHONMOO8 | BIG_FO_PLEASA1_1 | MOORE SWITCHING STATION to HONDO CREEK SWITCHING STATION LIN 1 | Big Foot - Pleasanton 138kV | 4 | $13,497.15 |  |  |
| CARVER_TINSLEY_CARVER_TINSLE1_1 | SILLFTL8 | CARVER_TINSLE1_1 | FORT LANCASTER to FORT LANCASTER LIN 1 | Carver - Tinsley Tap 138kV | 4 | $13,189.78 |  |  |
| MAXWELL_HAMILTON_HAMILT_MAXWEL1_1 | SCT2CAR8 | HAMILT_MAXWEL1_1 | CAUTHORN to Carver LIN 1 | Hamilton Road - Maxwell 138kV | 3 | $12,936.31 |  |  |
| IH20_TNCOLIET_138_IH2_COT_1 | SSTAWIC8 | 138_IH2_COT_1 | STAGHORN TNP to WICKETT TNP LIN 1 | Ih 20 Tnp - Collie Field Tap Tnp 138kV | 13 | $10,991.37 |  |  |
| MAVERICK_HAMILTON_HAMILT_MAVERI1_1 | SBRAHAM8 | HAMILT_MAVERI1_1 | BRACKETTVILLE to HAMILTON ROAD LIN 1 | Hamilton Road - Maverick 138kV | 3 | $9,983.03 |  |  |
| LEONCRK_FTST_138_FTS_LNC_1 | STARLEO8 | 138_FTS_LNC_1 | LEON CREEK TNP to TARBUSH TNP LIN 1 | Leon Creek Tnp - Fort Stockton Plant 138kV | 3 | $8,974.31 |  |  |
| SPUR_SPUR_SPUR_69_1 | SSPUASP8 | SPUR_69_1 | ASPERMONT AEP to ASPERMONT AEP LIN 1 | Spur 138kV | 3 | $8,556.52 |  |  |
| FTST_LEONCRK_138_FTS_LNC_1 | BASE CASE | 138_FTS_LNC_1 | Basecase | Leon Creek Tnp - Fort Stockton Plant 138kV | 7 | $6,789.19 |  |  |
| HAMILTON_MAVERICK_HAMILT_MAVERI1_1 | SBRAHAM8 | HAMILT_MAVERI1_1 | BRACKETTVILLE to HAMILTON ROAD LIN 1 | Hamilton Road - Maverick 138kV | 3 | $5,874.14 |  |  |
| UVALDE_READING_READIN_UVALDE1_1 | DRAZSA89 | READIN_UVALDE1_1 | Double Circuit RAZORBAC to DRYFRIO 138 kV & UVALDE to SABINAL 69 kV | Uvalde Aep - Reading 138kV | 6 | $5,154.03 |  |  |
| FURHMAN_MOURSUND_MOURSUND_FUR_1 | SFURVAN8 | MOURSUND_FUR_1 | FURHMAN to VANDERBILT SWITCHING STATION LIN 1 | Moursund - Furhman 138kV | 7 | $5,084.97 |  |  |
| CATARINA_ASHERTON_ASHERT_CATARI1_1 | DFOAVLO5 | ASHERT_CATARI1_1 | FOWLERTON to LOBO & AVANZADA | Asherton - Catarina 138kV | 7 | $4,060.51 |  |  |
| FRONTERA_S_MISSIN_BENTS_FRTER_1B_1 | SBENS_M8 | BENTS_FRTER_1B_1 | SOUTH MCALLEN to BENTSEN LIN 1 | Frontera - South Mission 138kV | 12 | $2,693.16 |  |  |
| WLVSW_GAILS_6217__A | SBUZHMP8 | 6217__A | BUZZARD DRAW SWITCH to HARDY MORGAN POI LIN _B | Willow Valley Switch - Gail Sub 138kV | 3 | $1,788.97 |  |  |
| SAPOWER_MADDUX_MADDUX_SAPOWE1_1 | SMA2SAP8 | MADDUX_SAPOWE1_1 | MADDUX to SAN ANGELO POWER STATION LIN 1 | Maddux - San Angelo Power Station 138kV | 8 | $1,314.41 |  |  |
| LON_HILL_CLARK_WD_CLARK__LON_HI1_1 | SCITWEI8 | CLARK__LON_HI1_1 | CHAMPLIN to CHAMPLIN LIN 1 | Clarkwood - Lon Hill 138kV | 3 | $682.11 |  |  |

## Generic Transmission Constraint Congestion

| GTC | Days Congestion |
| --- | --- |
| East Texas | 22 |
| Nelson Sharpe - Rio Hondo | 20 |
| North - Houston | 20 |
| West Texas | 18 |
| North Edinburg - Lobo | 18 |
| South Texas Export Pawnee - Spruce | 16 |
| Panhandle | 12 |
| South Texas Export Pawnee - Tango | 11 |
| McCamey | 8 |
| Zapata Starr | 4 |
| Treadwell | 2 |
| Valley Export | 2 |
| Kinney | 1 |
| South Texas Import Katoen - Lonhill | 1 |

- There was no activity on the remaining GTCs during the month.

Note: This is how many times a constraint has been activated to avoid exceeding a GTC limit, it does not imply an exceedance of the GTC occurred or that the GTC was binding.

## Manual Overrides

- None

## Congestion Costs for Calendar Year 2026

The following table represents the top twenty active constraints for the calendar year based on the estimated congestion rent attributed to the congestion. ERCOT updates this list on a monthly basis.

| Contingency | Overloaded Element | # of 5-min SCED | Estimated | Transmission |
| --- | --- | --- | --- | --- |
| Basecase | WESTEX GTC | 15,848 | 93,016,095.15 | Permian Basin Reliability Plan (765-kV import paths) (The PUCT approved ,helps improve, but not fully exit, the GTC yet.) |
| MANUAL HCKSW-RAMSW 345 kV_2 | Hicks Switch 138kV | 1,363 | 51,703,803.38 |  |
| BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Longshore Switch - Prairieland Switch 345kV | 13,078 | 50,083,939.49 | Oncor_FW_81268_Longshore – Consavvy 345 kV Double-Circuit Line Rebuild (MOD 81268, 23RPG034) |
| MANUAL RNKSW TO DHMSW 345&KRWSW TO DHMSW 345 DBLCKT | Argyle - Highlands Tnp 138kV | 6,658 | 34,163,478.64 |  |
| Basecase | EASTEX GTC | 6,423 | 33,498,873.57 |  |
| SALSW TO KLNSW 345 DBLCKT | Killeen Switch - Stagecoach 138kV | 2,796 | 31,304,486.27 | ONCOR_SE_87703_Belton_Killeen_138 kV Line (via Nolanville) (MOD 87703, 24RPG001) |
| BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1 | Mackenzie Substation - Northeast Substation 115kV | 7,410 | 27,212,675.15 |  |
| DOUBLE NVARO-LEG & NVARO-OUTSW 345 KV | Big Brown Ses - Jewett 345kV | 504 | 26,003,760.95 | ONCOR_SE_99622_PIN_OAK_SWITCH (MOD 99622, 25RPG004) |
| BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Hargrove - Twin Buttes 138kV | 4,720 | 23,055,639.53 |  |
| Basecase | Omega - Horse Hollow Generation Tie 345kV | 9,092 | 21,121,872.06 |  |
| DMTSW TO SCOSW 345 DBLCKT | Knapp - Scurry Chevron 138kV | 11,052 | 20,979,511.01 | Oncor_FW_102849_Union 138 kV Switch (MOD 102849) |
| Basecase | E_PASP GTC | 8,565 | 20,067,479.45 | San Antonio South Reliability I Project , 22RPG048 LRGV Transmission Improvement Project (21RPG017) San Antonio South Reliability II Project (23RPG032) |
| MORGAN CREEK SES to RANGER CAMP SWITCH LIN _A | Morgan Creek Ses - Cattleman Switch 345kV | 3,070 | 20,046,474.58 | West Texas 345-kV Infrastructure Rebuild Project (23RPG034) |
| Basecase | NE_LOB GTC | 17,240 | 18,755,618.75 | San Antonio South Reliability I Project (22RPG048) LRGV Transmission Improvement Project (21RPG017) San Antonio South Reliability II Project (23RPG032) |
| SALSW TO KLNSW 345 DBLCKT | Harker Heights South - Killeen Switch 138kV | 3,820 | 17,819,511.40 | ONCOR_SE_87699_Belton - Killeen 138 kV_Line (MOD 87699, 24RPG001) |
| TWR(345) WAP-WLF64 & WAP-WLY72 | South Texas Project - Wa Parish 345kV | 4,059 | 16,395,743.23 |  |
| STP-Elmcreek&WAP 345kV | South Texas Project - Elmcreek 345kV | 355 | 15,792,038.58 |  |
| MANUAL SINGLE SANDOW SWITCH to BADGER SWITCH 345 | Sandow Switch - Bell County East Switch 345kV | 2,202 | 15,471,465.60 |  |
| FOWLERTON to LOBO & AVANZADA | Lobo - Laredo Vft North 138kV | 5,426 | 15,369,961.62 |  |
| MAN_SGL_RGRSW-MGSES_345KV | Morgan Creek Ses - Cattleman Switch 345kV | 2,380 | 14,991,540.47 | West Texas 345-kV Infrastructure Rebuild Project (23RPG034) |

# System Events

## ERCOT Peak Load

The unofficial ERCOT peak load for June 2026 was 82,772 MW and occurred on 06/18/2026 during hour ending 17:00, this is 5,376 MW greater than the June 2025 demand of 77,396 MW on 06-19/2025 during hour ending 17:00. Instantaneous peak for June 2026 was 82,869 MW. Actual instantaneous peak for the same month last year was 78,411 MW.

## Load Shed Events

- None.

## Stability Events

- None.

## Notable PMU Events

ERCOT analyzes PMU data for any significant system disturbances that do not fall into the Frequency Events category reported in section 2.1. The results are summarized in this section once the analysis has been completed.

There were no PMU events outside of those reported in section 2.1.

## DC Tie Curtailment

None.

## TRE/DOE Reportable Events

- CPS Submitted a DOE-417 for 06/21/2026 for complete loss of monitoring or control capability at its staffed Bulk Electric System control center for 30 continuous minutes or more.

## New/Updated Constraint Management Plans

- ADD: MP_2026_02 REV0,MP_2026_03 REV0,MP_2026_04 REV1,MP_2026_05 REV1,MP_2026_06 REV1,MP_2026_07 REV1,MP_2026_08 REV0,MP_2026_09 REV1,MP_2026_10 REV0,MP_2026_11 REV1,MP_2026_12 REV0,MP_2026_13 REV1,MP_2026_14 REV1,MP_2026_15 REV1,MP_2026_16 REV0,MP_2026_17 REV0,ON_SHELF_MP_2026_01 REV0,ON_SHELF_MP_2026_02 REV0,PCAP_2026_03 REV0

- MOD: MP_2012_07_REV 13,MP_2012_08 REV12,MP_2022_17 REV11,MP_2016_12 REV11,MP_2021_03 REV9,MP_2022_01 REV5,MP_2022_02 REV6,MP_2022_03 REV5,MP_2022_08 REV5,MP_2023_08 REV4,MP_2023_11 REV7,MP_2024_04 REV2,MP_2024_05 REV2,MP_2024_08 REV2,MP_2024_10 REV2,MP_2025_01 REV8,MP_2025_09 REV1,MP_2025_10 REV2,MP_2025_12 REV3,MP_2025_13 REV3,MP_2025_14 REV1,MP_2025_16 REV5,MP_2025_17 REV4,MP_2025_18 REV1,MP_2025_20 REV1,MP_2025_21 REV2,MP_2025_23 REV1,MP_2025_24 REV1,MP_2025_26 REV1,MP_2025_28 REV1,MP_2025_42 REV2,MP_2025_44 REV2,MP_2025_45 REV2,MP_2024_12 REV4,MP_2011_08 REV37,ON_SHELF_MP_2024_02 REV2,ON_SHELF_MP_2024_03 REV3,ON_SHELF_MP_2024_04 REV2,ON_SHELF_MP_2024_06 REV6,ON_SHELF_MP_2025_11 REV1,ON_SHELF_MP_2025_30 REV2,ON_SHELF_MP_2025_31 REV4,PCAP_2010_01 REV16,PCAP_2024_01 REV2,PCAP_2025_01 REV2

- REMOVED: MP_2022_09 REV6,MP_2022_14 REV5,MP_2022_15 REV5,MP_2023_12 REV6,MP_2025_08 REV0,MP_2025_25 REV1,MP_2025_27 REV1,MP_2025_32 REV2,ON_SHELF_MP_2020_03 REV17,ON_SHELF_MP_2025_29 REV0,PCAP_2010_02 REV20

## New/Modified/Removed RAS

- None

## New Procedures/Forms/Operating Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 6/30/2026 | Transmission and Security Desk Operating Procedure V2 Rev 7 | 2032 |
| 6/30/2026 | Real Time Desk V2 Rev 4 | 2031 |
| 6/30/2026 | DC Tie Desk V2 Rev 3 | 2030 |

# Emergency Conditions

## OCNs

- None

## Advisories

| Date and Time | Message |
| --- | --- |
| June 6, 2026 13:31 | DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/07/2026 due to long execution time |
| June 9, 2026 13:24 | DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/10/2026 due to long solution run time. |
| June 10, 2026 13:24 | DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/11/2026 due to long solution run time. |
| June 17, 2026 13:26 | DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/18/2026 due to long execution time. |
| June 18, 2026 13:30 | DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/19/2026 due to observed submission issue. |
| June 20, 2026 13:20 | DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/21/2026 due to long execution time. |
| June 23, 2026 13:14 | DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/24/2026 due to long execution time. |
| June 24, 2026 13:27 | DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 06/25/2026 due to long execution time. |
| June 30, 2026 13:23 | DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 07/01/2026 due to long execution time. |

## Watches

- None

## Emergency Notices

- None

# Application Performance

## TSAT/VSAT Performance Issues

| Date and Time | Message |
| --- | --- |

## Communication Issues

- None.

## Market System Issues

- None.

# Model Updates

The Downstream Production Change (DPC) process allows ERCOT to make changes in the one-line Network Operations Model without loading a completely new model.  The purpose of this process is to allow for reliable grid operations as system conditions change between designated Network Operations Model database loads.  The DPC process is limited in scope to just those items listed below, with equipment ratings updates being the most common.  ERCOT has seen a rise in the use of the DPC process to make on-line updates to the Network Operations Model in recent years, instead of through the standard Network Operations Model Change Request process.

- Static Line ratings (Interim Update)

- Dynamic Line ratings (non-Interim Update)

- Autotransformer ratings (non-Interim Update)

- Breaker and Switch Normal status (Interim Update)

- Contingency Definitions (Interim Update)

- RAP and RAS changes or additions (Interim Update)

- Net Dependable and Reactive Capability (NDCRC) values (Interim Update)

- Impedance Updates (non-Interim)

A total of 59 DPCs were implemented in June 2026. 276 DPCs have been implemented year to date. DPCs submitted by TDSPs are mainly updates to transmission element ratings. DPCs submitted by ERCOT are mainly updates to manual contingency definitions.

| Transmission Operator | Number of DPCs |
| --- | --- |
| AEP TEXAS COMPANY (TDSP) | 3 |
| BRAZOS ELECTRIC POWER CO OP INC (TDSP) | 0 |
| BROWNSVILLE PUBLIC UTILITIES BOARD (TDSP) | 0 |
| BRYAN TEXAS UTILITIES (TDSP) | 0 |
| CENTERPOINT ENERGY HOUSTON ELECTRIC LLC (TDSP) | 5 |
| CITY OF AUSTIN DBA AUSTIN ENERGY (TDSP) | 0 |
| CITY OF COLLEGE STATION (TDSP) | 0 |
| CITY OF GARLAND (TDSP) | 0 |
| CPS ENERGY (TDSP) | 0 |
| CROSS TEXAS TRANSMISSION LLC (TSP)) | 0 |
| DENTON MUNICIPAL ELECTRIC (TDSP) | 0 |
| ELECTRIC TRANSMISSION TEXAS LLC (TDSP) | 0 |
| ERCOT | 0 |
| LCRA TRANSMISSION SERVICES CORPORATION (TDSP) | 28 |
| LONE STAR TRANSMISSION LLC (TSP) | 1 |
| ONCOR ELECTRIC DELIVERY COMPANY LLC (TDSP) | 13 |
| PEDERNALES ELECTRIC CO OP INC (TDSP) | 0 |
| RAYBURN COUNTRY CO OP DBA RAYBURN ELECTRIC (TDSP) | 7 |
| SHARYLAND UTILITIES LP (TDSP) | 2 |
| SOUTH TEXAS ELECTRIC CO OP INC (TDSP) | 0 |
| TEXAS MUNICIPAL POWER AGENCY (TDSP) | 0 |
| TEXAS-NEW MEXICO POWER CO (TDSP) | 0 |
| WIND ENERGY TRANSMISSION TEXAS LLC (TSP) | 0 |

# Appendix A: Real-Time Constraints

The following is a complete list of constraints activated in SCED. Full contingency descriptions can be found in the Standard Contingencies List located on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

| Year | Month | Contingency Name | Overloaded Element | From Station | To Station | Count of Days |
| --- | --- | --- | --- | --- | --- | --- |
| 2026 | June | DMTSCOS5 | 6437__F | SCRCV | KNAPP | 24 |
| 2026 | June | BASE CASE | EASTEX | n/a | n/a | 22 |
| 2026 | June | DBIGKEN5 | TREADW_YELWJC1_1 | TREADWEL | YELWJCKT | 22 |
| 2026 | June | SBWDDBM5 | LPLMK_LPLNE_1 | LPLMK | LPLNE | 21 |
| 2026 | June | BASE CASE | NELRIO | n/a | n/a | 20 |
| 2026 | June | SSTAWIC8 | 138_IH2_COT_1 | IH20 | TNCOLIET | 20 |
| 2026 | June | BASE CASE | N_TO_H | n/a | n/a | 20 |
| 2026 | June | SVEAW_L5 | 6217__A | WLVSW | GAILS | 20 |
| 2026 | June | SSTAWIC8 | 138_IH2_COT_1 | TNCOLIET | IH20 | 20 |
| 2026 | June | SRGRMGS5 | 6945__A | MGSES | CATSW | 19 |
| 2026 | June | DPHRCTR5 | MDOPHR99_A | MDO | PHR | 19 |
| 2026 | June | SHC2EXC5 | 107__B | HCKSW | EXCSW | 19 |
| 2026 | June | SSHAFRO8 | BENTS_FRTER_1B_1 | FRONTERA | S_MISSIN | 19 |
| 2026 | June | DMGSRIC8 | 6840__B | NVKSW | ANARN | 18 |
| 2026 | June | DGRMGRS8 | 6830__B | CRDSW | OLNEY | 18 |
| 2026 | June | BASE CASE | NE_LOB | n/a | n/a | 18 |
| 2026 | June | BASE CASE | WESTEX | n/a | n/a | 18 |
| 2026 | June | SHONF38 | HON_DEVI_1 | HONDOCK | DEVINESW | 18 |
| 2026 | June | SCMNCPS5 | 651__B | CMNSW | CMNTP | 17 |
| 2026 | June | DWPWFWP5 | STPWAP39_1 | STP | WAP | 17 |
| 2026 | June | DFOAVLO5 | NLARSW_PILONC1_1 | NLARSW | PILONCIL | 17 |
| 2026 | June | SBENS_M8 | BENTS_FRTER_1B_1 | FRONTERA | S_MISSIN | 17 |
| 2026 | June | DSCOTKW5 | 6215__A | BCKSW | CGRSW | 17 |
| 2026 | June | SELMTH25 | 1025__B | FROWS | MCLSW | 16 |
| 2026 | June | DCDHTVW5 | 6200__F | TYPRK | PLYAM | 16 |
| 2026 | June | DBAKCED5 | 6965__A | LNGSW | PRLSW | 16 |
| 2026 | June | SFURVAN8 | RAYBUR_FURHMAN_1 | FURHMAN | RAYBURN | 16 |
| 2026 | June | DBLW2JC5 | WAPWLY72_A | WLY | WAP | 16 |
| 2026 | June | DRNS_TB5 | THWZEN98_A | ZEN | THW | 16 |
| 2026 | June | SLAQLOB8 | BRUNI_69_1 | BRUNI | BRUNI | 16 |
| 2026 | June | BASE CASE | E_PASP | n/a | n/a | 16 |
| 2026 | June | DBAKCED5 | LAKENA_SAMATH1_1 | LAKENASW | SAMATHIS | 16 |
| 2026 | June | SMDOPHR5 | 138_ALV_NAL_1 | TNNALVIN | ALVIN | 16 |
| 2026 | June | BASE CASE | HHGTOM_1 | HHGT | OMEGA | 14 |
| 2026 | June | DBIGKEN5 | MADDUX_TREADW1_1 | MADDUX | TREADWEL | 14 |
| 2026 | June | DWAP_OB5 | MDOPHR99_A | MDO | PHR | 14 |
| 2026 | June | SMDOOAS5 | GN_PZ_08_A | GN | PZ | 14 |
| 2026 | June | SMAYWHI8 | NUECES_WHITE_2_1 | NUECES_B | WHITE_PT | 14 |
| 2026 | June | DBIGSCH5 | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 14 |
| 2026 | June | DBIGKEN5 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 13 |
| 2026 | June | DLONPK25 | 6375__A | GRSES | GRMES | 13 |
| 2026 | June | MHARNED5 | WESLCO_HIDLBRG_1 | MV_HBRG4 | MV_WESL4 | 13 |
| 2026 | June | SBLURDH8 | 2270__B | MEXTP | ITALY | 12 |
| 2026 | June | SWOLPAL8 | CROSSO_PALOUS1_1 | PALOUSE | CROSSOVE | 12 |
| 2026 | June | BASE CASE | PNHNDL | n/a | n/a | 12 |
| 2026 | June | DBUCRGP5 | 651__B | CMNSW | CMNTP | 12 |
| 2026 | June | DZORHAY5 | BERGHE_AT1H | BERGHE | BERGHE | 12 |
| 2026 | June | DWAP_BI5 | BI_JN_64_A | JN | BI | 12 |
| 2026 | June | DLONPK25 | 12020__B | BRTSW | JUNPR | 12 |
| 2026 | June | SFMRRYS5 | 400__A | FMRVL | RYSSW | 12 |
| 2026 | June | SPRSPAR8 | 1545__A | FLTSW | PRSSW | 11 |
| 2026 | June | DSALHUT5 | 1715__B | TMPSW | FRYSW | 11 |
| 2026 | June | DBIGKEN5 | HAMILT_MAXWEL1_1 | MAXWELL | HAMILTON | 11 |
| 2026 | June | BASE CASE | E_PATA | n/a | n/a | 11 |
| 2026 | June | DFOAVLO5 | BRUNI_69_1 | BRUNI | BRUNI | 11 |
| 2026 | June | SMCLWNE8 | 1025__B | FROWS | MCLSW | 10 |
| 2026 | June | DFRYTM58 | SEA_AAT1 | SEA | SEA | 10 |
| 2026 | June | DFOAVLO5 | ASHERT_CATARI1_1 | CATARINA | ASHERTON | 10 |
| 2026 | June | SMA2SAP8 | MADDUX_SAPOWE1_1 | MADDUX | SAPOWER | 9 |
| 2026 | June | DBAKCED5 | CROSSO_PALOUS1_1 | PALOUSE | CROSSOVE | 9 |
| 2026 | June | SMA2SAP8 | MADDUX_SAPOWE1_1 | SAPOWER | MADDUX | 9 |
| 2026 | June | SSNYCGR8 | SNYDR_FMR1 | SNYDR | SNYDR | 9 |
| 2026 | June | BASE CASE | 138_FTS_LNC_1 | FTST | LEONCRK | 9 |
| 2026 | June | SFMRRY25 | 381__A | FMRVL | RYSSW | 9 |
| 2026 | June | DSALHUT5 | 1710__A | SALDS | SONTERRA | 9 |
| 2026 | June | DMCDUPS8 | HECKER_RESNIK1_1 | HECKER | RESNIK | 9 |
| 2026 | June | SCLCGTN8 | 6635__G | MRVLY | ESTLD | 8 |
| 2026 | June | DBAKCED5 | HARGRO_TWINBU1_1 | TWINBU | HARGROVE | 8 |
| 2026 | June | SRAYRI38 | HAINE__LA_PAL1_1 | LA_PALMA | HAINE_DR | 8 |
| 2026 | June | DRAZSA89 | READIN_UVALDE1_1 | UVALDE | READING | 8 |
| 2026 | June | SVENFTS5 | 35055__A | SAMSW | VENSW | 8 |
| 2026 | June | SGRMGRS8 | 6830__B | CRDSW | OLNEY | 8 |
| 2026 | June | BASE CASE | MCCAMY | n/a | n/a | 8 |
| 2026 | June | SFURVAN8 | MOURSUND_FUR_1 | FURHMAN | MOURSUND | 8 |
| 2026 | June | DMTSCOS5 | 6240__C | SACRC | DPCRK | 8 |
| 2026 | June | SBCESN35 | 455__A | BGRSW | SNDSW | 7 |
| 2026 | June | DCAGCO58 | 656T656_1 | KENDAL | BERGHE | 7 |
| 2026 | June | SILLFTL8 | CARVER_TINSLE1_1 | CARVER | TINSLEY | 7 |
| 2026 | June | DFOWSMG5 | FWLRTN_TILDEN_1 | FOWLRTON | TILDEN | 7 |
| 2026 | June | SSNDBGR5 | 421__A | BCESW | SNDSW | 7 |
| 2026 | June | SWHILON5 | NUECES_WHITE_2_1 | NUECES_B | WHITE_PT | 7 |
| 2026 | June | SBRAPIN8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 7 |
| 2026 | June | DELMSAN5 | PAWNEE_SPRUCE_1 | PAWNEE | CALAVERS | 7 |
| 2026 | June | DCOTWR25 | FARMLAND_LONGD_1 | FARMLAND | W_LD_345 | 7 |
| 2026 | June | DBAKSOL5 | SOLSTICE_PST1 | SOLSTICE | SOLSTICE | 7 |
| 2026 | June | DCAGCI58 | 255T279_1 | PIPECR | MEDILA | 7 |
| 2026 | June | SWCOWCO8 | G138_15_1 | WCOLLOCL | ANGLETON | 6 |
| 2026 | June | SHONMOO8 | BIG_FO_PLEASA1_1 | BIG_FOOT | PLEASANT | 6 |
| 2026 | June | SP5CAG8 | D5_S1_1 | HOWARD | LEON_CRK | 6 |
| 2026 | June | SWCOWCO8 | G138_15_1 | ANGLETON | WCOLLOCL | 6 |
| 2026 | June | SHELBUL5 | 35045__A | SAMSW | FVLSW | 6 |
| 2026 | June | SMC2WEA8 | 1025__B | FROWS | MCLSW | 6 |
| 2026 | June | DVENFTS5 | 505__B | FBRSW | THSES | 5 |
| 2026 | June | SSUNRGR8 | 6240__C | SACRC | DPCRK | 5 |
| 2026 | June | DWPWFWP5 | 155T217_1 | BELLSO | PT | 5 |
| 2026 | June | SCRMSAR8 | CONCHO_VRBS1_1 | CONCHO | VRBS | 5 |
| 2026 | June | SBUZHMP8 | 6217__A | WLVSW | GAILS | 5 |
| 2026 | June | SFURVAN8 | RAY_L_46_1 | RAYBURN | L_463S | 5 |
| 2026 | June | SSPUASP8 | SPUR_69_1 | SPUR | SPUR | 5 |
| 2026 | June | SBLURDH8 | 1275__A | WDBSW | HLSBR | 5 |
| 2026 | June | DBAKCED5 | 225T558_1 | BIGHIL | OERSTED | 5 |
| 2026 | June | DLOFOAV5 | ASHERT_CATARI1_1 | CATARINA | ASHERTON | 5 |
| 2026 | June | DRILKRW5 | BOW_FMR1 | BOW | BOW | 5 |
| 2026 | June | SBGLTWI8 | LAKENA_SAMATH1_1 | LAKENASW | SAMATHIS | 5 |
| 2026 | June | DLOFOAV5 | ASHERT_CATARI1_1 | ASHERTON | CATARINA | 5 |
| 2026 | June | SSAMTCR5 | 505__B | FBRSW | THSES | 4 |
| 2026 | June | DFRYBC58 | SEA_AAT1 | SEA | SEA | 4 |
| 2026 | June | SCOLBAL8 | BALLIN_HUMBLT1_1 | BALLINGE | HUMBLTAP | 4 |
| 2026 | June | SRAYRI38 | HAINE__OLEAND1_1 | HAINE_DR | OLEANDER | 4 |
| 2026 | June | SSOAHOL8 | 138_FTS_LNC_1 | FTST | LEONCRK | 4 |
| 2026 | June | SBRAPIN8 | ESCOND_GANSO1_1 | GANSO | ESCONDID | 4 |
| 2026 | June | SOAKSHI8 | NEWM_WAL_1 | NEWMAN | WALNUT1 | 4 |
| 2026 | June | DBIGSCH5 | SANTAR_WOLFCA1_1 | WOLFCAMP | SANTARIT | 4 |
| 2026 | June | BASE CASE | ZAPSTR | n/a | n/a | 4 |
| 2026 | June | SBRAPIN8 | ESCOND_GANSO1_1 | ESCONDID | GANSO | 4 |
| 2026 | June | MLARDUS8 | LARDVN_LOBO2_1 | LOBO | LARDVNTH | 4 |
| 2026 | June | SHAYZO25 | 6T227_1 | HAYSEN | ZORN | 4 |
| 2026 | June | DSALHUT5 | 270__A | KNBSW | TMPSW | 4 |
| 2026 | June | DRILKRW5 | 6085__E | WFSSW | NSTAR | 4 |
| 2026 | June | DBIGSCH5 | CROSSO_NORTMC1_1 | NORTMC | CROSSOVE | 4 |
| 2026 | June | DRNS_TB5 | THWZEN71_A | ZEN | THW | 4 |
| 2026 | June | STARLEO8 | 138_FTS_LNC_1 | LEONCRK | FTST | 4 |
| 2026 | June | MCATPRL5 | 6965__A | LNGSW | PRLSW | 4 |
| 2026 | June | SBLURDH8 | 1210__B | HUBRD | HAN1 | 4 |
| 2026 | June | SCITWEI8 | CLARK__LON_HI1_1 | LON_HILL | CLARK_WD | 4 |
| 2026 | June | DBIGKEN5 | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 4 |
| 2026 | June | BASE CASE | RANDAD_ZAPATA1_1 | RANDADO | ZAPATA | 4 |
| 2026 | June | DSLKNOR5 | 6965__A | LNGSW | PRLSW | 4 |
| 2026 | June | SBLAWDB8 | 2270__B | MEXTP | ITALY | 3 |
| 2026 | June | DLOFOAV5 | NLARSW_PILONC1_1 | PILONCIL | NLARSW | 3 |
| 2026 | June | SSCJFS8 | BCVPSA03_A | PSA | BCV | 3 |
| 2026 | June | SSTPESP8 | BLESSI_PAVLOV1_1 | BLESSING | PAVLOV | 3 |
| 2026 | June | SBRAHAM8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 3 |
| 2026 | June | SBRAHAM8 | HAMILT_MAVERI1_1 | MAVERICK | HAMILTON | 3 |
| 2026 | June | DELMSAN5 | MAGRUD_VICTOR2_1 | VICTORIA | MAGRUDER | 3 |
| 2026 | June | SVEAW_L5 | 6217__D | KEYSB | LMESA | 3 |
| 2026 | June | DDILCOT8 | DILLEYSW_XF1H | DILLEYSW | DILLEYSW | 3 |
| 2026 | June | MATHEB_8 | FB_RS_60_A | RS | FB | 3 |
| 2026 | June | DALASOA8 | 138_FTS_LNC_1 | FTST | LEONCRK | 3 |
| 2026 | June | DVENFTS5 | 235__A | SGRSW | JEWET | 3 |
| 2026 | June | DCSHSSP5 | 690__C | SSPSW | LBRPD | 3 |
| 2026 | June | DFOAVLO5 | FREER_LOBO1_1 | LOBO | FREER | 3 |
| 2026 | June | DVICEDN8 | FURHMAN_VANDB_1 | FURHMAN | VANBLTSS | 3 |
| 2026 | June | SSTPESP8 | LAN_CT_PAVLOV1_1 | PAVLOV | LAN_CTY | 3 |
| 2026 | June | SHAMMAX8 | MAXWEL_WHITIN1_1 | MAXWELL | WHITING | 3 |
| 2026 | June | DLOFOAV5 | NLARSW_PILONC1_1 | NLARSW | PILONCIL | 3 |
| 2026 | June | SPRAWAL8 | 155T217_1 | BELLSO | PT | 3 |
| 2026 | June | DLOFOAV5 | BRUNI_69_1 | BRUNI | BRUNI | 3 |
| 2026 | June | DBIGKEN5 | CARVER_TINSLE1_1 | CARVER | TINSLEY | 3 |
| 2026 | June | SCT2CAR8 | HAMILT_MAXWEL1_1 | MAXWELL | HAMILTON | 3 |
| 2026 | June | MTRYBRO8 | 6217__A | WLVSW | GAILS | 3 |
| 2026 | June | DSALKLN5 | 630__B | KLNSW | HHSTH | 3 |
| 2026 | June | DMBDRKC5 | 651__B | CMNSW | CMNTP | 3 |
| 2026 | June | STARLEO8 | SOLSTICE_PST1 | SOLSTICE | SOLSTICE | 3 |
| 2026 | June | DRAZSA89 | 2585_1 | DOWNIES | MOORE | 3 |
| 2026 | June | XBAL89 | CONCHO_VRBS1_1 | CONCHO | VRBS | 3 |
| 2026 | June | BASE CASE | HI_LONE_TLINE_1 | HI_LONE | CEDACA | 3 |
| 2026 | June | DRILKRW5 | 6085__B | NSTAR | LKARH | 3 |
| 2026 | June | DCMBCPS8 | 6275__D | BCPSW | AZLES | 2 |
| 2026 | June | SLISBAT8 | GARZA_XF1H | GARZA | GARZA | 2 |
| 2026 | June | SNEDSTE5 | PANTER_WESMER1_1 | WESMER | PANTERA | 2 |
| 2026 | June | DSLKSOL5 | 138_FLT_FXT_1 | TNFXTAIL | FLAT_TOP | 2 |
| 2026 | June | MHARNED5 | HAINE__LA_PAL1_1 | LA_PALMA | HAINE_DR | 2 |
| 2026 | June | SCRDJON5 | HOOD_DECRDVA_1 | DCDAM | HOD | 2 |
| 2026 | June | SBRABND8 | NEWM_WAL_1 | NEWMAN | WALNUT1 | 2 |
| 2026 | June | SCROPAL8 | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 2 |
| 2026 | June | SWORBRD8 | 138_WIC_STG_1 | WICKETT | STAGHORN | 2 |
| 2026 | June | SCLCGTN8 | 6360__A | BRKTP | BRKRG | 2 |
| 2026 | June | SREAUVA8 | DOWNIES_AX1H | DOWNIES | DOWNIES | 2 |
| 2026 | June | DSALHUT5 | GABRIE_AT1 | GABRIE | GABRIE | 2 |
| 2026 | June | SHA2MAX8 | MAXWEL_WHITIN1_1 | MAXWELL | WHITING | 2 |
| 2026 | June | SBOSELM5 | 1210__B | HUBRD | HAN1 | 2 |
| 2026 | June | SHELBUL5 | 35055__A | SAMSW | VENSW | 2 |
| 2026 | June | MDBHRSA5 | 6085__E | WFSSW | NSTAR | 2 |
| 2026 | June | MNLFIWO8 | BENTS_FRTER_1B_1 | FRONTERA | S_MISSIN | 2 |
| 2026 | June | SMOOPEA8 | PALDRO_DILLEY_1 | PALODURO | DILLEYSW | 2 |
| 2026 | June | BASE CASE | REATA_ROMNE_1A_A | REATA | ROMNEY | 2 |
| 2026 | June | SMOOPEA8 | UVALDE_W_BATE1_1 | W_BATESV | UVALDE | 2 |
| 2026 | June | BASE CASE | VALEXP | n/a | n/a | 2 |
| 2026 | June | DKG_NB_5 | BCVPSA03_A | PSA | BCV | 2 |
| 2026 | June | SMDOOAS5 | BCVPSA03_A | PSA | BCV | 2 |
| 2026 | June | SMOOPEA8 | DILLY_PEARSA1_1 | DILLY | PEARSAL1 | 2 |
| 2026 | June | SLARDUS8 | LARDVN_LOBO2_1 | LOBO | LARDVNTH | 2 |
| 2026 | June | BASE CASE | TRDWEL | n/a | n/a | 2 |
| 2026 | June | SHCKEXC5 | 106__C | HCKSW | EXCSW | 2 |
| 2026 | June | SPALFRO8 | BENTS_FRTER_1B_1 | FRONTERA | S_MISSIN | 2 |
| 2026 | June | MELNHST5 | BLESSING_1382 | BLESSING | BLESSING | 2 |
| 2026 | June | DKG_NB_5 | MDOPHR99_A | MDO | PHR | 2 |
| 2026 | June | SBRAHAM8 | ESCOND_GANSO1_1 | ESCONDID | GANSO | 2 |
| 2026 | June | DFOWSMG5 | GEO_SIG_1 | GEOWEST | SIGMOR | 2 |
| 2026 | June | SBRAESC8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 2 |
| 2026 | June | SL_4RAY8 | RAYBURN_69_2 | RAYBURN | RAYBURN | 2 |
| 2026 | June | SSNYCGR8 | 6695__B | SNYDR | AMOTP | 2 |
| 2026 | June | DWO5_EU8 | DT_PK_91_A | PK | DT | 2 |
| 2026 | June | BASE CASE | FURHMAN_VANDB_1 | FURHMAN | VANBLTSS | 2 |
| 2026 | June | DSGTSCH5 | LAKENA_SAMATH1_1 | LAKENASW | SAMATHIS | 2 |
| 2026 | June | SBOSWHT8 | LKW_WHT_1 | LKWHITNY | WHTNY | 2 |
| 2026 | June | BASE CASE | RAYBUR_FURHMAN_1 | FURHMAN | RAYBURN | 2 |
| 2026 | June | SCOLBAL8 | SANA_FMR1 | SANA | SANA | 1 |
| 2026 | June | MSNDWCR5 | SNDSW_MR1L | SNDSW | SNDSW | 1 |
| 2026 | June | DSNG_TB5 | THWZEN98_A | ZEN | THW | 1 |
| 2026 | June | DSALHUT5 | 421__A | BCESW | SNDSW | 1 |
| 2026 | June | SGRSJUN8 | 6275__D | BCPSW | AZLES | 1 |
| 2026 | June | SCSDNK8 | BCVPSA03_A | PSA | BCV | 1 |
| 2026 | June | SWCPYT8 | FB_RS_60_A | RS | FB | 1 |
| 2026 | June | DHUTGEA8 | GABRIE_AT1 | GABRIE | GABRIE | 1 |
| 2026 | June | SBWDDBM5 | LPLNW_LPLMD_1 | LPLNW | LPLMD | 1 |
| 2026 | June | MSNDWCR5 | SNDSW_MR1H | SNDSW | SNDSW | 1 |
| 2026 | June | SNWEWES8 | WES_MV_W_1 | WESLACO | MV_WESL4 | 1 |
| 2026 | June | DTNFBCA8 | 138_FTS_LNC_1 | FTST | LEONCRK | 1 |
| 2026 | June | BASE CASE | 155T217_1 | BELLSO | PT | 1 |
| 2026 | June | SHLSWH28 | 2270__B | MEXTP | ITALY | 1 |
| 2026 | June | DTOKJK_5 | 260_A_1 | JEWET | SNG | 1 |
| 2026 | June | MLNGPR25 | 5025__A | RGRSW | PRMSW | 1 |
| 2026 | June | SDANBLE8 | BLESSING_69A1 | BLESSING | BLESSING | 1 |
| 2026 | June | SANGSTA5 | BLESSI_LOLITA1_1 | LOLITA | BLESSING | 1 |
| 2026 | June | SLKAWFS8 | BOW_FMR1 | BOW | BOW | 1 |
| 2026 | June | DTOKJK_5 | HRN_GOOD_1 | HRN | GOODLAND | 1 |
| 2026 | June | BASE CASE | I_KALO | n/a | n/a | 1 |
| 2026 | June | SOBWAP5 | OB_WAP98_A | WAP | OB | 1 |
| 2026 | June | MDHSRSA5 | 12020__B | BRTSW | JUNPR | 1 |
| 2026 | June | DBAKSOL5 | 225T558_1 | BIGHIL | OERSTED | 1 |
| 2026 | June | SVEAW_L5 | 6217__B | GAILS | KEYSB | 1 |
| 2026 | June | DCPSST58 | 651__B | CMNSW | CMNTP | 1 |
| 2026 | June | SHLSWDB8 | 810__B | BLUMS | RVSTP | 1 |
| 2026 | June | DCHBJO25 | CBY_AT3H | CBY | CBY | 1 |
| 2026 | June | BASE CASE | HENWAP01_A | WAP | HEN | 1 |
| 2026 | June | SOXYIN28 | I_DUPP_I_DUPS1_1 | I_DUPP1 | I_DUPSW | 1 |
| 2026 | June | DRNS_TB5 | MDOPHR99_A | MDO | PHR | 1 |
| 2026 | June | DODEMOS5 | ODEHV_MR3H | ODEHV | ODEHV | 1 |
| 2026 | June | SFURVAN8 | RAY_MOURSUND_1 | MOURSUND | RAYBURN | 1 |
| 2026 | June | MBONNED5 | WESLCO_HIDLBRG_1 | MV_HBRG4 | MV_WESL4 | 1 |
| 2026 | June | SBRESAL8 | 105T105_1 | SALEM | HIGH36 | 1 |
| 2026 | June | SBLAWDB8 | 1210__B | HUBRD | HAN1 | 1 |
| 2026 | June | SSTAPYO8 | 138_HRT_BPT_1 | BRDSPRYT | HARPOONT | 1 |
| 2026 | June | SWORBRD8 | 138_PYT_STG_1 | STAGHORN | PYOTE | 1 |
| 2026 | June | DBLBYWF5 | 155T217_1 | BELLSO | PT | 1 |
| 2026 | June | SANDFLO8 | 1715__B | TMPSW | FRYSW | 1 |
| 2026 | June | DWLV89N8 | 3410__A | ELVSW | REGST | 1 |
| 2026 | June | STAYS_M8 | BENTS_FRTER_1B_1 | FRONTERA | S_MISSIN | 1 |
| 2026 | June | SFURMOU8 | FURHMAN_VANDB_1 | FURHMAN | VANBLTSS | 1 |
| 2026 | June | BASE CASE | HENWAP01_A | HEN | WAP | 1 |
| 2026 | June | BASE CASE | KINNEY | n/a | n/a | 1 |
| 2026 | June | DRNS_TB5 | NB_THW97_A | THW | NB | 1 |
| 2026 | June | SNICBLU8 | OAKC_SERDEV1_1 | OAKC | OAKC | 1 |
| 2026 | June | DBUCRGP5 | TREADW_YELWJC1_1 | TREADWEL | YELWJCKT | 1 |
| 2026 | June | SNWEWES8 | WESLCO_HIDLBRG_1 | MV_HBRG4 | MV_WESL4 | 1 |
| 2026 | June | XTRS258 | 1210__B | HUBRD | HAN1 | 1 |
| 2026 | June | DPHRCTR5 | 138_ALV_NAL_1 | TNNALVIN | ALVIN | 1 |
| 2026 | June | SALVTNN8 | 138_FWP_MNL_1 | FRWYPARK | MAINLAND | 1 |
| 2026 | June | SSTAWIC8 | 138_HRT_BPT_1 | BRDSPRYT | HARPOONT | 1 |
| 2026 | June | DGABAN89 | 1710__A | SALDS | SONTERRA | 1 |
| 2026 | June | SECRDMT8 | 6215__A | BCKSW | CGRSW | 1 |
| 2026 | June | DBWNRGP5 | 651__B | CMNSW | CMNTP | 1 |
| 2026 | June | DKLNRGP5 | 651__C | CMNTP | SHILO | 1 |
| 2026 | June | DMGSRIC8 | 6840__A | ANARN | CRDSW | 1 |
| 2026 | June | SLCDYN8 | FB_RS_60_A | RS | FB | 1 |
| 2026 | June | STNNMDO8 | G138_8A_1 | PHR | HDNLAKES | 1 |
| 2026 | June | UJUNBES1 | HEXT_MASONS1_1 | HEXT | MASONSW | 1 |
| 2026 | June | SMDOPHR5 | MDO_AT1 | MDO | MDO | 1 |
| 2026 | June | SMCEABS8 | MERK_MKLT1_1 | MKLT | MERK | 1 |
| 2026 | June | SGIRTNW8 | M_69_N1_1 | TNFS | TNPINION | 1 |
| 2026 | June | SBELFRY8 | SEA_AAT1 | SEA | SEA | 1 |
| 2026 | June | DRAZSA89 | UVALDE_W_BATE1_1 | UVALDE | W_BATESV | 1 |
| 2026 | June | SWCOW2C8 | _WC_WCO_1 | WC | WCOLMAIN | 1 |
| 2026 | June | DSLKSOL5 | 138_FTS_LNC_1 | FTST | LEONCRK | 1 |
| 2026 | June | SFBRTHS5 | 500__B | SAMSW | TCRSW | 1 |
| 2026 | June | DCAGCO58 | 584T584_1 | KENDAL | WELFAR | 1 |
| 2026 | June | SPRMRCK5 | 6053__C | CATSW | PRLSW | 1 |
| 2026 | June | DSCOTKW5 | 6685__A | CGRSW | CLCTY | 1 |
| 2026 | June | SHLSWDB8 | 810__G | RDHSW | BLUMS | 1 |
| 2026 | June | SLARDUS8 | ASHERT_CATARI1_1 | ASHERTON | CATARINA | 1 |
| 2026 | June | BASE CASE | BAKRFLD_CEDCAN_1 | CEDACA | BAKESW | 1 |
| 2026 | June | DCHBJO25 | CBY_AT1H | CBY | CBY | 1 |
| 2026 | June | XUVA189 | CHAPAR_TURTLC1_1 | TURTLCRK | CHAPARRO | 1 |
| 2026 | June | DRAZSA89 | DOWNIES_AX1H | DOWNIES | DOWNIES | 1 |
| 2026 | June | DBUCRGP5 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 1 |
| 2026 | June | SANDFLO8 | 1710__A | SALDS | SONTERRA | 1 |
| 2026 | June | DSNDBGR5 | 36040__A | KNBSW | SALSW | 1 |
| 2026 | June | DHILMAR5 | 361T361_1 | SCHERT | PARKWA | 1 |
| 2026 | June | DVLSPAC5 | 389__A | WDDSW | MNSES | 1 |
| 2026 | June | DFVLFTS5 | 505__B | FBRSW | THSES | 1 |
| 2026 | June | DCAGCO58 | 583T583_1 | BANDER | MASOCR | 1 |
| 2026 | June | DSLKNOR5 | 6056__B | PRLSW | CONSW | 1 |
| 2026 | June | XCMB58 | 651__B | CMNSW | CMNTP | 1 |
| 2026 | June | DWLFMET5 | 6525__A | ODEHV | RTRSW | 1 |
| 2026 | June | SGRMGRS8 | 6830__C | OLNEY | GRAHM | 1 |
| 2026 | June | DBLUBUF8 | ABNTHW_SERDEV1_1 | ABNTHWST | ABNTHWST | 1 |
| 2026 | June | MXMUB58 | ABNTHW_SERDEV1_1 | ABNTHWST | ABNTHWST | 1 |
| 2026 | June | SBWSTOW9 | BOW_FMR1 | BOW | BOW | 1 |
| 2026 | June | DBIGKEN5 | CROSSO_NORTMC1_1 | NORTMC | CROSSOVE | 1 |
| 2026 | June | SHA2MAX8 | CTHR_TINSLE1_1 | CTHR | TINSLEY | 1 |
| 2026 | June | DBIGSCH5 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 1 |
| 2026 | June | DVICDUP8 | GREENL_WEAVER1_1 | WEAVERRD | GREENLK | 1 |
| 2026 | June | SFORRAY8 | RAY_L_46_1 | RAYBURN | L_463S | 1 |
| 2026 | June | SNEDSTE5 | WESLCO_HIDLBRG_1 | MV_HBRG4 | MV_WESL4 | 1 |
| 2026 | June | MMCLWLA8 | 1025__B | FROWS | MCLSW | 1 |
| 2026 | June | DTCRTHS5 | 35045__A | SAMSW | FVLSW | 1 |
| 2026 | June | MBULNAV5 | 35045__A | SAMSW | FVLSW | 1 |
| 2026 | June | DBUCRGP5 | 505__B | FBRSW | THSES | 1 |
| 2026 | June | MRNKDHM5 | 587__A | ARGYL | LWSVH | 1 |
| 2026 | June | DFRYBC58 | BELCNTY_XFMR | BELCNTY | BELCNTY | 1 |
| 2026 | June | MPASTNE5 | BENTS_FRTER_1B_1 | FRONTERA | S_MISSIN | 1 |
| 2026 | June | DFRIILL8 | CARVER_TINSLE1_1 | CARVER | TINSLEY | 1 |
| 2026 | June | SCOMHA38 | CARVER_TINSLE1_1 | CARVER | TINSLEY | 1 |
| 2026 | June | SWAATH8 | FB_RS_60_A | RS | FB | 1 |
| 2026 | June | SJRESA28 | GABRIE_AT1 | GABRIE | GABRIE | 1 |
| 2026 | June | SBRAPIN8 | GANSO_MAVERI1_1 | MAVERICK | GANSO | 1 |
| 2026 | June | XVIC89 | MAGRUD_VICTOR2_1 | VICTORIA | MAGRUDER | 1 |
| 2026 | June | SCOMHA38 | MAXWEL_WHITIN1_1 | MAXWELL | WHITING | 1 |
| 2026 | June | SGRIRAP5 | MELONC_SEADRF1_1 | SEADRFTC | MELONCRE | 1 |

Current Wind Generation Record: 29,011 MW on 05/18/2026 at 00:01 | Current Wind Penetration Record: 69.15% on 04/10/2022 at 01:43

Current Solar Generation Record: 33,981 MW on 05/13/2026 at 12:43 | Current Solar Penetration Record: 72.74% on 05/02/2026 at 11:28