## Slide 1: 2027 Ancillary Service Methodology Discussion Luis Hinojosa Manager, Ancillary Services & Operations Analytics WMWG July 27, 2026
Key Takeaways
ERCOT is not proposing any changes to the methodology for Regulation and RRS aside from the annual data update.
Interested Stakeholders are requested to attend meetings to provide any feedback on the AS Methodology.
Purpose
Provide proposed methodology to determine Ancillary Service (AS) quantities for 2027.

## Slide 2: Stakeholder Discussion Timeline
May 19, 2026 – TAC Kickoff
June 01, 2026 – BOARD Preview
June 17, 2026 – PDCWG
June 29, 2026 – WMWG
July 08, 2026 – WMS
July 09, 2026 – ROS
July 22, 2026 – PDCWG (Proposed)
July 27, 2026 – WMWG (Proposed)
July 28, 2026 – OWG (Proposed)
July 29, 2026 – TAC (2026 AS Methodology Discrepancy)
August 05, 2026 – WMS (Possible Vote)
August 06, 2026 – ROS (Possible Vote)
August 26, 2026 – TAC (Possible Vote)
September 15, 2026 – BoD
Nov, Dec 2026 – PUC

## Slide 3: Discussion Scope for Today
Discrepancy for 2026 Ancillary Services Methodology.
This presentation will discuss the proposed methodology to determine Ancillary Service (AS) quantities for 2027.
  ERCOT is not proposing any changes to the methodology used to compute the Regulation and Responsive Reserve Services for 2027.
  NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT for the 2027 Operating Year (OY) has not yet been published. Therefore, this analysis used the minimum RRS-PFR limit of 1,377 MW for 2026.
  The 2027 review focuses on refining the model to find the appropriate criteria for AS procurement quantities. ERCOT plans to compare alternative criteria using AS quantity, estimated cost, and modeled reliability-risk metrics.
Any Ancillary Service (AS) quantities for 2027 contained in this presentation are based on the methodology that was approved in December 2025 with modification based on the proposed changes. The quantities for 2027 are preliminary and reflect moving forward the historic data on which these are based, unless otherwise noted.
ERCOT is seeking stakeholder feedback on these proposed changes for the 2027 AS Methodology.

## Slide 4: Discrepancies in the 2026 Probabilistic Model
As ERCOT worked toward the 2027 AS Methodology we identified that the probabilistic model that was used to calculate the 2026 ECRS and NSRS had some discrepancies. Issues identified:
This caused the quantities to be posted (black line) for 2026 to be below the level that would have been required by the PUCT approved methodology (black dotted line).
ERCOT has utilized these lower quantities for 2026 so far and will not revise the posted quantities for August 2026. ERCOT will evaluate whether changes to the posted quantities are warranted for the remaining months of 2026 and will further coordinate with PUCT Staff on next steps in addressing this discrepancy.
The issue was only for the probabilistic portion of 2026 AS Methodology. The regulation and RRS quantities were not affected.
Market Noticed issued on 7/27/2026
2026 annual average ECRS + Non-Spin quantities shown on the below chart
Monthly comparisons are available in the posted HTML file for today’s meeting.

## Slide 5: Discrepancies in the 2026 Probabilistic Model
Identified discrepancies:
  Forecast-error inputs were not processed accordingly in all functions of the model leading to less uncertainty being observed
  Optimization was too lenient on less risky hours
  Alignment of hour ending logic on all datasets was missed
Overall Impact:
  Resulted in the model using a lower level of net load uncertainty leading to overall lower than what would have been required by the approved parameters in the 2026 AS Methodology
Reliability:
We have observed that so far in 2026 we have not seen a reliability risk due:
  RTC+B ability to procure above the Non-Spin plan relative to the Ancillary Service Demand Curve (ASDC) which has reduced the gap in the quantities
  Higher available headroom than accounted for in the 2026 AS Methodology. Particularly due to higher installed Energy Storage Resource (ESR) capacity in 2026 allowing for an increase overall available headroom. (additional slides later)
  This additional available system headroom has supported Real-Time operations.

## Slide 6: Probabilistic Framework Review
ERCOT Contingnecy Reserve Service (ECRS) & Non-Spinning Reserve (Non-Spin)

## Slide 7: Longer lead-time Ancillary Services address uncertainty and help to recover depleted reserves
ERCOT Contingency Reserve Service (ECRS)
Purpose — reserve that responds within 10 minutes to recover frequency, cover forecast errors and ramps, and replace deployed reserves.
  Why it matters — bridges the fast (RRS) and slow (Non-Spin) reserves; quantity set using the probabilistic modeling of reliability risks.
Non-Spinning Reserve Service (Non-Spin)
Purpose — Capacity that can be started in 30 minutes to cover forecast errors, ramps or forced outages and replace deployed reserves until additional resources can be committed.
Why it matters —30min lead time backstop for sustained uncertainty events; quantity set using the probabilistic modeling of reliability risks.
(Additional Event Details)

## Slide 8: Flow Diagram for Probabilistic Methodology
INPUTS
ENGINE
OUTPUTS
Risks
(X=) hour ahead ahead and 30 min ahead Net Load Forecast Error and
Accumulated Forced Outages in (X=) hours
Risk Credits
(X=) of historically available
30 min online headroom sustainable for 4 hours and
30 min start Offline capacity
Monte Carlo Optimization
Convergence Criteria+ Met?
Net Risk
ECRS + Non-Spin
Requirement
(12 Month x 24 Hour)
No
Yes
ECRS Requirement
(12 Month x 24 Hour)
Non-Spin Requirement
(12 Month x 24 Hour)
+Convergence Criteria: 1 in XX year probability of operating reserves dropping below the sum of YY% (Reg Up plus RRS) or ZZ threshold, whichever is higher. Mathematically, this equates to
𝐸𝐶𝑅𝑆 +𝑁𝑆𝑅𝑆 < 𝑁𝑒𝑡𝑅𝑖𝑠𝑘 + 𝑀𝑎𝑥 (YY(𝑅𝑒𝑔 + 𝑅𝑅𝑆), ZZ) with probability of 1 in XX year.

## Slide 9: Parameters in Probabilistic Framework
Issue | ERCOT’s Recommendation | ERCOT’s Perspective
How far ahead to look at forecast error and forced outages of conventional resources? Parameter X (in hours) | 6 Hours | ERCOT’s recommendation of 6 hours is informed by policy guidance from Summer 2021 to operate to a higher reliability threshold (i.e. operate the system more conservatively with limited RUCs) and is based on historic availability of offline resources during RUC timeframe.
What is the level of risk ERCOT should try to avoid by procuring AS to cover forecast error? Parameter ZZ (in MW) | 3,000 i.e. Watch | ERCOT has noticed minimal difference in outcomes between ZZ = 3,000, 2,500 and 1,500 MW since quantities for most hours are a function of the amount of Reg Up plus RRS that these reserves have to replace.
What level of minimum reserves (Reg+RRS) should be maintained? Parameter YY (in %) | 100% | ERCOT proposes full restoration of deployed Reg Up + RRS. With that requirement, changing the target reserve level from Watch to EEA or Load Shed may not materially reduce quantities in many hours because Reg Up + RRS restoration often controls the requirement. Restoration of these fast-response reserves is critical to maintaining reliability and staying compliant with NERC BAL requirements.
How much should we discount the AS quantities for a particular time period based on the “extra” headroom from resources that were historically committed by market in that time period? Parameter Y (in %) | Online:60% in Night and 50% in Day Offline:60% in Night and 50% in Day ESR:60% in Night and 60% in Day Sustainable for 4 hours | ERCOT has observed that although RTC+B has had an impact on available (online + offline) headroom capacity, we are seeing additional capacity available that can be accounted for in the model. ERCOT expects the trend of having higher available (online + offline) headroom capacity during night hours to continue

## Slide 10: Overall Model Improvements and Tunning
Change | Benefit
Switch to GRPP for NLFE and Solar Adjustment | Increases accuracy measure of forecast quality and model adjustments to ensure more accurate uncertainty
Improved NLFE Tail distribution method | Less reliance on tail events should lead to a reduction in quantities to cover more probabilistic events
Risk Credit Categorization | Each Risk Credit can have its own allowance based on historical performance
Tuning of optimization logic | Improve solution accuracy and adjustments to reach convergence faster
RTC+B Alignment in logic and AS Plan and AS Award Accounting | Ensures to account for the AS plan when we over procure or are short to ensure available capacity better reflects real-time availability for headroom accounting
There are overall improvements to the probabilistic model for 2027 AS Methodology which allow for a more accurate representation of quantities needed. Detailed slides on these can be found in the appendix.

## Slide 11: Online/Offline Historical Risk Credit Available
The charts to the right are showing the performance analysis of proposed risk credits of 60% at night and 50% during day hours.
Online Headroom:
  We have observed a shift in availability in online headroom to the day hours when solar is available. Indicating additional capability during these periods.
  Morning and evening hours have seen similar or slight reduction in availability.
  A seasonal effect can also be observed form these charts. There is more availability during winter months and reduced availability as we come to the summer months.
Offline Headroom:
  Has also seen an increase in availability through day and night hours with some hours seeing a reduction.
  A shift in online availability to offline can also be observed as part of the RTC+B efficiency.
In both datasets we see April has the least available and this can be attributed to more outages during this period.
This gives us confidence that we can take additional credit from online and offline in comparison to last years day time parameter of 25%.

## Slide 12: ESR Risk Credit
The chart to the right are showing the performance analysis of proposed risk credits of 60% at night and 60% during day hours sustainable for 4 hours.
It can be observed that there is significant increase through out most hours, only very few small increase. This can be attributed to the increase in installed capacity in ESR over the year.
We have explored the ability to account for more credit from just ESR, but there are evening hours where we see reduction do to SOC depletion for evening ramps.
AS of now we are projecting ESR capacity to continue to grow in 2027, allowing for further certainty of risk credit increase, but we are also aware that there may be a point when this may slow down. That is hard to predict at his moment.

## Slide 13: Risk Credit Performance Analysis
With risk credits set to the proposed parameters this show the outcome of overall headroom available from all 3 categories. There is still one single hour which see as reduction due available headroom in 2026.

## Slide 14: Preliminary Quantities with Proposed Parameters and Scenarios
To support a finding in the PUCT’s 2024 Ancillary Services Study we wanted to provide the ability to compare alternative reserve levels estimated cost, and modeled reliability-risk metrics.
Additionally, Stakeholders have asked for specific scenarios that they would like to review. We have provided an HTML with today’s postings which allows Stakeholders to add in scenarios based on the parameters available.
One note to keep in mind, to improve batch-run efficiency, scenarios that are expected to produce identical results are removed during scenario generation.
If you see a combination that you would like to see please provide that feedback.
ERCOT Proposed*

## Slide 15: Regulation Service

## Slide 16: Regulation Service Methodology
ERCOT is not proposing any change to the methodology used to compute the minimum Regulation Service requirements in 2027.
The preliminary Regulation quantities for January 2027 through June 2027 in subsequent slides have been computed using proposed methodology (with 2025 to 2026* five minute ahead Net load forecast error) and updated Wind and Solar Over Forecast Adjustment tables.
Purpose — Balances supply and demand to maintain frequency close to 60Hz between 5-minute dispatch intervals; deployed every 4 seconds.
Why it matters — keeps the system continuously balanced; needs grow as net-load variability rises.

## Slide 17: Regulation Up/Down Methodology 2027
 | 2026 Methodology | 2027 Methodology
Data Input | 5-min SCED Netload Forecast Error (2-yr) | No Change
Calculation Method | 95th of 5-min SCED Netload Forecast Error | No Change
Wind/Solar Adjustment | GE Table - Increased wind/solar forecast error per 1,000 MW installed capacity increase | No Change
ACE Integral Component | Average of ACE Integral Change (2-yr) | No Change
Load Adjustment (LL Ramps) | Not considered | No Change

## Slide 18: Hourly Average Regulation Comparison

## Slide 19: Regulation Comparison January

## Slide 20: Regulation Comparison June

## Slide 21: Responsive Reserve Service (RRS)

## Slide 22: Responsive Reserve Service (RRS) Methodology
ERCOT is not proposing any change to the methodology used to compute RRS requirements in 2027.
The preliminary RRS quantities for January 2027 through June 2027 in subsequent slides have been computed using 2025 and 2026 system inertia conditions and 2026 RRS table.
Updates to RRS Table:
  The RRS table tracks RRS requirements for different inertia conditions.
  NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT for the 2027 Operating Year (OY) has not yet been published. Therefore, this analysis used the minimum RRS-PFR limit of 1,377 MW for 2026.
  The RRS table will be updated for 2027 to when the minimum RRS-PFR limit is published.
Purpose — Responds very quickly to arrest frequency during low frequency events typically triggered by generating unit trips.
Why it matters —the first line of defense for frequency; sized to system inertia.

## Slide 23: 2026 RRS Table
Scenario | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5,960 | 5,563 | 5,200 | 4,892 | 4,622 | 4,329 | 4,114 | 3,920 | 3,744 | 3,522 | 3,314 | 3,139
*RRS Curr IFRO (MW) | 3,320 | 3,273 | 3,227 | 3,183 | 3,145 | 3,068 | 3,031 | 2,982 | 2,941 | 2,863 | 2,767 | 2,699
**RRS Upd IFRO (MW) | - | - | - | - | - | - | - | - | - | - | - | -
Scenario | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:1 | 1:1 | 1:1 | 1:1 | 1:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3,004 | 2,890 | 2,784 | 2,686 | 2,595 | 2,510 | 2,421 | 2,353 | 2,290 | 2,230 | 2,173 | 2,119 | 2,068
*RRS Curr IFRO (MW) | 2,645 | 2,595 | 2,558 | 2,514 | 2,463 | 2,425 | 2,380 | 2,343 | 2,290 | 2,230 | 2,173 | 2,119 | 2,068
**RRS Upd IFRO (MW) | - | - | - | - | - | - | - | - | - | - | - | - | -
*RRS quantity is calculated for RCC of 2,805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,377 MW.
**The 2027 IFRO assessment has not yet been reported back from NERC, preventing the calculation of RRS quantity.
***Red font in table above identifies study scenario where RRS needed < 2,300 MW. RRS requirement during these is based on the applicable floor.

## Slide 24: Monthly Average Responsive Reserve Service Comparison

## Slide 25: Responsive Reserve Service January

## Slide 26: Responsive Reserve Service June

## Slide 27: Summary
Based on the analysis ERCOT has conducted thus far,
  ERCOT is not considering any changes in the methodologies used to compute Regulation and Responsive Reserve Service requirements for 2027.
  ERCOT has incorporated several corrections/improvements to the Probabilistic model to account for RTC+B impacts along with accounting for stakeholder feedback approach to compute the ECRS and Non-Spin requirements for 2027.
The proposed timeline for this review is included alongside.
Interested Stakeholders are requested provide any feedback on the proposed 2027 AS Methodology.
2027 Methodology Review Timeline
July 28, 2026 – OWG (Proposed)
July 29, 2026 – TAC (2026 AS Methodology Discrepancy)
August 05, 2026 – WMS (Possible Vote)
August 06, 2026 – ROS (Possible Vote)
August 26, 2026 – TAC (Possible Vote)
September 15, 2026 – BoD
Nov, Dec 2026 – PUC

## Slide 28: Questions?
JoseLuis.Hinojosa@ercot.com

## Slide 29: Appendix

## Slide 30: Probabilistic

## Slide 31: Optimization Workflow for Total (ECRS + NSRS) Reserve

## Slide 32: Simplified Optimization Example – Identical Maximum Risk Across Two Hours
Key Takeaway: Reserve requirements are set by both the magnitude and frequency of risk exceedances, not by the maximum risk alone.
*Not Real Data

## Slide 33: Allocating Individual ECRS and NSRS quantities from Total Reserves
Each hour has 12 five-minute 30-min ahead errors and one 6-hour ahead error
For each 30-min under-forecast error, calculate the ratio to the 6-hour ahead under-forecast error for that same hour
Group results by Month-Hour to compute average ratio for each Month-Hour
ECRS should be reserved to restore frequency following the trip of a large generator and/or provide supply during intra-hour net load forecast errors.
ECRS = max(ECRS Frequency Recovery Requirement, Total Reserves * ECRS Ratio %)
NSRS = Total Reserves * (1-ECRS Ratio %)

## Slide 34: Full Reg Up + RRS Restoration Is Core to the Criterion
Key Takeaway: Reg Up + RRS restoration is the reliability floor in the convergence criterion; sensitivities may change ECRS + Non-Spin quantities, but should not compromise ERCOT’s frequency-control capability.
Why ERCOT Expects to Maintain It
Shorter look-ahead periods or higher headroom credits may lower modeled ECRS + Non-Spin needs.
Lower ECRS + Non-Spin quantities should not compromise ERCOT’s frequency-control capability after deployment.
Historically available headroom may not be available, deliverable, or persistent when conditions are tight.
ERCOT is an electrical island and cannot rely on synchronously connected neighbors for replacement reserves after a frequency event.
NERC BAL standards establish performance obligations for frequency control, disturbance recovery, contingency reserve restoration, and frequency response.
What This Means in the Probabilistic Model
ECRS and Non-Spin cover forecast error and forced outage risk.
ECRS and Non-Spin also restore/backfill deployed Reg Up and RRS.
The convergence criterion must explicitly preserve both functions as risk inputs, risk credits, and operating assumptions are tested.
If restoration is not explicit, the model may cover modeled uncertainty while leaving fast-response Reg Up and RRS reserves depleted after deployment.
ERCOT can evaluate lower ECRS + Non-Spin quantities under different assumptions, but the methodology should not leave deployed Reg Up + RRS unrestored. Those services provide ERCOT’s fast-response capability for frequency control and contingency response; ECRS and Non-Spin help restore that capability until additional Resources can be committed.

## Slide 35: Ancillary Services complement the energy market to efficiently ensure system reliability
Ancillary Services (AS) are an important mechanism for maintaining the reliability of the ERCOT Interconnection.
ERCOT runs an energy-only market; AS are procured and co-optimized with energy day-ahead and — since RTC+B went live (Dec 2025) — in real-time as well.
Ancillary Services are bought for two reasons:
  To balance supply and demand while meeting reliability objectives defined in NERC Reliability BAL-001, BAL-002 and BAL-003 Standards, and
  To reduce operational risks associated with variability and uncertainty.
ERCOT has four Ancillary Service products: Regulation (both Up and Down), Responsive Reserve Service (RRS), ERCOT Contingency Reserve Service (ECRS), and Non-Spinning Reserve Service (Non-Spin)
Each Ancillary Service has its qualification requirements, performance obligation, and compliance rules for underperformance. Further, the need and quantity of each Ancillary Service are not static and can vary depending on the system conditions (hourly, daily, seasonally).
  ERCOT reviews and revises the AS methodology annually to adapt to the evolving needs of the ERCOT grid and to become more efficient in responding to the additional operational risks

## Slide 36: Gross Real-Time Power Potential (GRPP) and Solar Adjustment Tuning
Net Load Forecast Error (NLFE)
  The input data for NLFE now utilizes GRPP, the power potential, for a resource before co-located load consumption. With more loads being co-located behind wind and solar generation units, GRPP represents our vendor forecast more accurately and should improve uncertainty accounting.
Solar Adjustment
  GRPP has also been incorporated into this logic to allow for uncertainty improvement.
  Due to the rapid increase in installed solar capacity, dealing with cloud cover and ramping hour forecasting has become more difficult. Some model adjustments have been made to improve our solar adjustments.
  The new method uses month-hour solar adjustment values, and we have conducted a performance analysis. We see an overall improvement in adjusted solar error predictions compared to the monthly methodology leading to better solar adjustment.

## Slide 37: Improving The Over Reliance on NLFE tails
One takeaway from the 2026 methodology was that AS quantities are highly impacted by tail events. We implemented Generalized Pareto Distribution (GPD) on the tails, to reduce the influence of extreme tail events.
Top figure is a conceptual demonstration on modeling the tails distribution using GPD model.
Bottom figure shows that the GPD method (Spliced Resample) lowers the sampled values.

## Slide 38: Gross Real-Time Power Potential (GRPP)
Nodal Protocol Section 4.2.2 and 4.2.3: ERCOT shall produce and update hourly a Short-Term Wind/ PhotoVoltaic Power Forecast (STWPF/STPPF) that provides a rolling 168-hour hourly forecast of wind/PhotoVoltaic production potential for each Wind-powered/PhotoVoltaic Generation Resource (WGR/PVGR)
GRPP is the power potential for a resource before co-located load consumption. With more loads being co-located behind wind and solar generation units, GRPP represents our vendor forecast more accurately
If there is no co-located locate at a generation site, HSL is equal to GRPP
Key Takeaway: Because the forecasts represent GRPP rather than HSL, calculating solar and wind forecast error using GRPP provides a more accurate measure of forecast quality. Solar and wind error calculation will be using GRPP moving forward.

## Slide 39: Updated Solar Adjustment Methodology
Installed solar capacity in the Far East region grew substantially in recent years.
Far East has more variable weather and cloud cover making forecasting more difficult, especially during ramping hours. This drove the switch from monthly to month-hour solar adjustment values to better capture hour-to-hour variance in solar forecast error.
Key Takeaway: Due to the rapid increase in installed solar capacity in the Far East region, ramping hour forecasting has become more difficult. The new methodology can better capture hour to hour variance in solar forecast error.
Date | CenterEast Capacity | CenterWest Capacity | FarEast Capacity | FarWest Capacity | NorthWest Capacity | SouthEast Capacity
Jun 1, 2026 | 5,997 | 4,941 | 16,499 | 5,963 | 2,526 | 3,882
Jun 1, 2025 | 4,154 | 2,978 | 13,988 | 5,368 | 1,944 | 3,818
Jun 1, 2024 | 3,084 | 2,978 | 10,034 | 4,917 | 1,344 | 1,951

## Slide 40: Risk and Risk Credits Details
Risk
Net Load Forecast Error (NLFE)
X hour ahead
30 min ahead
Accounting for Solar Capacity Growth
Forced Outages
Method pulls X hour ahead rolling forced outage for dispatchable resources
Risk Credits
Online Headroom Capacity Sustainable for X hours
Conventional unit headroom that is available to SCED, but excluding Ancillary Service Capacity
System Hourly ESR Capability is calculated using historical Real-Time telemetered hourly average ESR data (SOC, MNOS, AS Responsibility/Awards)
Reliability Unit Commitment (RUC) Capacity excluded
Offline Capacity
Conventional unit capacity that can be started within 30 minutes excluding any units with capacity reserved for Ancillary Services
Net Risk = Risk – Risk Credit*Y where the variable is configurable
  Y represents optimal multipliers on how many percent risk credit being applied

## Slide 41: Risk Credit RTC+B Impacts and Review
With the implementation of RTC+B, there was a need to align our methods with system changes such as, but not limited to, the following:
  Accounting for AS Award vs AS Responsibility
  HASL calculation removal
  Change in telemetered Resource Status
  SCED AS Duration Requirement Accounting
    Reg and RRS – 30 mins
    RRS-FFR – 15 mins
    ECRS – 1 hour
    Non-Spin – 4 hours
  AS Plan Awareness (Shortfall/Excess procurement of plan)
Additionally, ERCOT is reviewing potential impacts to online/offline/ESR energy available that is not awarded AS after implementation of RTC+B.
Key Takeaway: Although much of the probabilistic method was developed in the 2026 AS Methodology, much of the functionality needs review to ensure RTC+B impacts are accounted for.

## Slide 42: Capacity Included in the Probabilistic Methodology
During grid operation, there are varying quantities of available power output that could be dispatched that is not reserved for ancillary services
This output helps to mitigate risk as it allows for SCED to dispatch further output to meet unforeseen increased load without having to dispatch ancillary services
The available power output that we are considering is the following:
  ESR Capacity:
      This capacity is specific to ESRs as it can only be dispatched according to the charge that is available and not reserved for ancillary services
  Online Headroom:
      Unit Type: Combined Cycles and other Thermal that are ON and SCED dispatchable
      Online headroom calculation for each resource, excluding any AS that is reserved.
        New_HASL = HSL – AS awards)
        Headroom = max(0, min(SCEDURR * 30 + Base Point, New_HASL) – Base Point)
  Offline Capacity:
      HSL capability of units that are OFF and are not awarded for Offline Non-Spin Reserve Service which can be online within 30 minutes.
Key Takeaway: There is available power output not reserved for ancillary services that can be used to mitigate load forecast. Capacity accounting is impacted by changes in RTC+B

## Slide 43: Offline Capacity RTC+B changes
In RTC+B, units no longer have a specific status for carrying OFFNS. Instead, OFFNS is awarded, but the status of 'OFF' remains
These awards can now be changed every SCED interval. This change required a modification for quantifying Offline capacity
Offline capacity is now calculated as the capacity of offline units (OFF) during intervals where units are not awarded OFFNS. Intervals that are awarded OFFNS are not considered for Offline capacity
The selection of only considering units with a start time of 30 minutes or less was maintained
Key Takeaways: Resource status accounting change was reviewed and modified to only consider intervals where no OFFNS is awarded for Offline capacity

## Slide 44: ESR SOC Reserved for AS Accounting
ESRs vary in the amount of SOC they have available for dispatch that is not reserved for ancillary services (AS). The amount of SOC reserved for AS can be calculated based on Responsibility/Award and the duration required for each AS.
In the pre-RTC method, a 1 hour duration was being considered when accounting the amount of SOC that is reserved for AS for all AS types. For example:
In RTC+B, SCED is now 'SOC aware’ and now respects the AS durations when awarding AS:
Key Takeaway: In RTC+B, SCED is SOC aware and awards AS based on the defined AS durations. The SOC reserved for AS should be considered when accounting for ESR credit.

## Slide 45: ESR SOC Reserved for AS Accounting
In RTC, it can clearly be seen that the updated durations in AS types have caused a different 'shape' in the expected SOC reserved for AS. Complete data for 2026 will allow for further analysis.

## Slide 46: Forced Outages
Forced generator outages as an input are needed to define the the uncertaintly that were unanticipated by the Operators and would not have been seen by RUC comitment proccess.
The current method only uses Forced (FR), and Forced Extended (FE) to align them by hour and only looks at outages that started within a window of observation for any particular hour.
RTC+B introduced single model batteries but had no impact on the core logic and functionality of the tool.
Doesn’t include equipment that have a nature or work of 'Mothballed’, ‘New Equipment Energization’, 'Retirement of Old Equipment’, or 'Seasonal Resource.’
The process uses a X-hour ahead variable that can be changed to look at different scenarios.
Outage overlaps are also accounted for by looking at individual units and removing any outage that was present during another outage.
  If an outage was found to be overlapping with another, the outage with a higher loss of HSL will take priority and overwrite the bigger outage, but only for its timeframe.
Key Takeaway: Battery outages are included and RTC+B brought no impacts to the core functions of the tool. The tool is flexible enough to look at X-hour ahead scenarios.
80 HSL Lost
100 HSL Lost
100
80
80

## Slide 47: Forced Outages (cont’d)
12:00
06:00
13:00
10:00
13:30
12:45
12:15
13:35
Hour + 1
Hour
Hour - X
Start Time
Scenario 1
Hour – X ≤ Start Time ≤ Hour
Hour + 1 ≤ End Time
Scenario 2
Hour – X ≤ Start Time ≤ Hour Hour < End Time ≤ Hour + 1
Scenario 3
Hour ≤ Start Time < Hour + 1
12:45
X Hour variable can be changed to desired time
Hour of Interest

## Slide 48: Sampling methods and performance
Normal Distribution: Fit a Gaussian distribution using the sample mean and standard deviation
Kernel Density Estimation (KDE) Sampling: Estimate a smooth probability density from historical observations and sample from it
Inverse (Empirical Cumulative Distribution Function) ECDF: Sample from the empirical CDF using linear interpolation between historical observations
Key takeaway: ECDF preserves the data distribution very well comparing to Normal distribution, and also it does not need parameter tuning as KDE.

## Slide 49: Data Sampling Example
Scattered points (red) are the original data points, the blue and yellow lines are the resampled data points by ECDF and GPD methods.
*Figure for demonstration purposes only

## Slide 50: Data Sampling Method Comparison

## Slide 51: Regulation

## Slide 52: Recap – Generation To Be Dispatched (GTBD)
ERCOT has incorporated intra-hour wind/solar forecast- based ramp into GTBD to give SCED an indication of how renewables may ramp.
  Predicted Wind Ramp Rate (PWRR) was incorporated in GTBD in Dec.2018
  Predicted Solar Ramp Rate (PSRR) was incorporated in GTBD in Jun.2021
In absence of PSRR/PWRR, SCED dispatches uncurtailed solar/wind units to their max output (HSL).
  This means that SCED assumes output of uncurtailed solar/wind units will persist for the next 5-min at the unit’s HSL that was telemetered at the start of the interval.
GTBD = Total Gen
+K3*5*PLDRR
+K4*Regulation Deployed
+ K5*ACE Integral
– K6*5*PWRR
+ K7*5*DCTRR
– K8*5*PSRR
5-min Load Ramp Forecast
Previous Reg Deployment
Historical Accumulated ACE
5-min Wind Ramp Forecast
5-min DC Tie Ramp Forecast
5-min Solar Ramp Forecast

## Slide 53: Recap – Dynamic PSRR Threshold in GTBD
ERCOT started to apply a dynamic PSRR threshold in GTBD calculation on 6/12/2023
PSRR thresholds change with 4 pre-defined day periods - Night, Sunrise, Sunset and Other
ERCOT started with a threshold of 80MW/min for Sunrise and Sunset periods on 6/12/23. Today, the threshold is set to 280MW/min.
ERCOT continues to update the thresholds and the definition of day periods seasonally*
* Seasons will be defined by shift in solar ramping patterns
Chart: Dynamic PSRR Threshold
 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 100 | 100 | 100 | 0 | 0 | 0
Night

## Slide 54: Regulation Comparison February

## Slide 55: Regulation Comparison April

## Slide 56: Regulation Comparison May

## Slide 57: RRS

## Slide 58: Total Inertia (2016 – 2026.7*)
The average inertia in 2025 was comparable to 2024, but currently 2026 is trending lower than in 2024. Summer months which typically have higher inertia have not all occurred.
[Total inertia for 2016 - 2026.07*]

## Slide 59: Responsive Reserve Service February

## Slide 60: Responsive Reserve Service March

## Slide 61: Responsive Reserve Service April

## Slide 62: Reg + RRS Monthly Average
Chart: Monthly Average Reg + RRS
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
2026 Final | 3119 | 3495.5417 | 3633.4583 | 3576.8333 | 3193.6667 | 3082.625 | 2946.125 | 2775.75 | 2897.875 | 3220.375 | 3489.3333 | 3309.5
2027 (Proposed) | 3224.6927 | 3449.4093 | 3669.1153 | 3598.5367 | 3256.8034 | 3080.051

## Slide 63: Average Inertia per Hour 2021-2026.7*
From 2025 and onwards the lowest hours of inertia have moved from the night hours to the middle of the day.
Chart: Average Inertia per Hour
2021 | 231.0167 | 220.1128 | 213.1623 | 211.6564 | 212.9705 | 218.081 | 227.1576 | 230.2275 | 233.8436 | 238.6224 | 244.5739 | 251.63 | 257.1866 | 261.1305 | 263.7966 | 265.7325 | 267.5027 | 268.5498 | 269.1126 | 268.8539 | 267.2982 | 264.21 | 258.4143 | 247.7114
2022 | 242.2104 | 230.1495 | 225.6586 | 224.6807 | 225.7149 | 228.976 | 235.0458 | 238.5265 | 240.9776 | 244.447 | 249.2677 | 255.2333 | 261.0441 | 265.7481 | 269.5065 | 272.7489 | 275.5718 | 277.8449 | 279.4513 | 279.8506 | 278.6995 | 275.841 | 269.0215 | 256.0439
2023 | 252.8735 | 244.8053 | 242.5019 | 242.0444 | 243.2221 | 246.0671 | 249.7546 | 251.87 | 253.1422 | 253.8195 | 254.6727 | 257.4508 | 261.2272 | 264.9961 | 268.538 | 272.2741 | 275.936 | 278.6422 | 280.4322 | 281.5987 | 281.8577 | 280.1138 | 274.4063 | 263.7
2024 | 258.0981 | 250.7432 | 247.7776 | 247.4828 | 248.0455 | 249.5654 | 251.0366 | 252.0673 | 252.7508 | 251.963 | 250.2722 | 250.5321 | 252.0039 | 254.1677 | 257.3306 | 261.4172 | 266.7966 | 271.0318 | 274.0031 | 276.1466 | 277.2741 | 276.6432 | 273.3345 | 266.0568
2025 | 265.3627 | 257.1726 | 253.0719 | 251.8397 | 251.8678 | 252.2827 | 252.9021 | 253.4262 | 253.363 | 249.9522 | 244.3523 | 242.108 | 242.9884 | 245.4785 | 249.0457 | 253.5288 | 260.4978 | 267.5324 | 272.9577 | 276.2678 | 278.3478 | 278.3629 | 276.2722 | 271.6489
2026^ | 249.8076 | 242.9699 | 238.7987 | 237.3165 | 236.6611 | 236.4224 | 236.489 | 236.5763 | 235.606 | 229.7704 | 221.1654 | 218.1252 | 218.6538 | 220.2005 | 222.7299 | 226.3442 | 233.1995 | 242.6697 | 249.4509 | 252.9033 | 255.0781 | 255.6681 | 255.4966 | 253.5893
Data only includes up to partial July 2026

## Slide 64: Average Inertia per Hour 2020-2026^ (Seasonal)
Winter average Inertia contains previous year December data
Y-Axis scales are different in each chart
Data only includes up to partial July 2026
Chart: Average Inertia Spring (Mar, Apr, May)
2021 | 185.9502 | 175.8399 | 169.6966 | 168.6311 | 170.572 | 176.6297 | 186.8383 | 190.4608 | 194.1961 | 197.9359 | 201.0632 | 205.0378 | 208.2958 | 210.6084 | 212.7019 | 214.6676 | 216.1042 | 217.1516 | 217.4677 | 217.0241 | 216.2858 | 215.2108 | 210.9741 | 202.2843
2022 | 196.9504 | 182.3661 | 176.4316 | 175.2807 | 176.4326 | 180.0276 | 187.1903 | 191.3261 | 194.4763 | 196.9829 | 201.1027 | 207.152 | 214.3316 | 220.6017 | 225.9639 | 230.4873 | 234.4815 | 237.6098 | 239.867 | 240.5644 | 239.8911 | 237.9689 | 230.7227 | 214.7741
2023 | 212.938 | 202.6991 | 199.7299 | 198.8015 | 199.9499 | 203.9514 | 209.79 | 212.8745 | 214.6934 | 215.449 | 216.326 | 218.9089 | 222.7381 | 226.3392 | 229.4122 | 232.7184 | 235.7502 | 238.039 | 239.6931 | 241.1881 | 242.6956 | 242.3412 | 237.5096 | 226.0262
2024 | 227.0081 | 217.9089 | 213.4009 | 213.2587 | 213.7276 | 215.3404 | 217.2888 | 218.9293 | 220.1294 | 219.5077 | 218.5323 | 219.0765 | 220.6513 | 222.3341 | 225.1333 | 228.8965 | 233.4774 | 237.7684 | 240.5024 | 242.2308 | 244.3269 | 245.0678 | 242.4712 | 235.9701
2025 | 228.8604 | 217.508 | 211.5859 | 210.1544 | 209.9419 | 210.2377 | 210.5683 | 211.1888 | 211.1943 | 206.3573 | 199.1103 | 196.8392 | 197.5242 | 200.1083 | 204.1384 | 209.5696 | 217.0864 | 226.8194 | 236.0842 | 240.1951 | 243.5274 | 244.2939 | 242.2611 | 237.0104
2026 | 225.6745 | 217.5001 | 211.5868 | 209.9144 | 208.9741 | 208.6366 | 208.754 | 208.9488 | 208.2658 | 203.0342 | 196.0522 | 193.6571 | 194.0926 | 195.65 | 198.322 | 201.6094 | 207.433 | 215.7794 | 224.3789 | 229.1829 | 232.2566 | 233.131 | 232.6852 | 230.7111
Chart: Average Inertia Summer (Jun, Jul, Aug)
2021 | 299.8666 | 285.3027 | 275.2407 | 271.7313 | 271.628 | 273.1549 | 278.5989 | 281.6131 | 286.4617 | 294.8302 | 307.4973 | 323.2319 | 333.8416 | 341.581 | 345.6841 | 347.6431 | 348.5123 | 348.7572 | 348.3766 | 346.7865 | 343.9982 | 341.4715 | 335.8299 | 322.3839
2022 | 308.0992 | 292.236 | 283.9732 | 281.1737 | 280.7539 | 281.4554 | 284.6418 | 287.6245 | 290.181 | 297.1319 | 310.0318 | 324.0939 | 335.4529 | 343.9443 | 349.4322 | 352.256 | 353.7515 | 354.3708 | 354.16 | 352.8654 | 350.7299 | 347.9683 | 340.8343 | 325.6454
2023 | 325.8413 | 316.0266 | 311.997 | 310.6571 | 310.2446 | 310.1723 | 311.0168 | 311.7467 | 312.5111 | 314.0396 | 318.3798 | 325.7922 | 334.0315 | 341.4488 | 347.9009 | 353.1886 | 356.6491 | 358.6699 | 359.9214 | 360.3458 | 360.9724 | 360.5227 | 353.5499 | 339.2618
2024 | 315.4939 | 308.7546 | 305.145 | 304.2903 | 304.1636 | 304.2483 | 304.4731 | 304.8087 | 305.0156 | 305.215 | 306.6373 | 309.9473 | 313.8139 | 317.4411 | 321.1203 | 323.8463 | 325.9518 | 327.5164 | 329.2128 | 330.7814 | 332.6752 | 333.7171 | 331.0144 | 322.9924
2025 | 314.5727 | 306.0185 | 300.0712 | 297.7002 | 296.9028 | 296.7009 | 296.6218 | 296.52 | 295.9606 | 294.3217 | 293.8829 | 294.8994 | 297.8684 | 301.8191 | 306.1125 | 309.4971 | 313.2009 | 316.5797 | 319.8725 | 322.6572 | 326.1544 | 327.6307 | 326.1711 | 321.3507
2026^ | 300.0598 | 293.7967 | 289.9566 | 287.985 | 287.1143 | 286.6426 | 286.2738 | 285.7979 | 283.3303 | 278.2568 | 275.923 | 276.3519 | 278.9974 | 281.7581 | 284.8176 | 288.0841 | 291.2139 | 295.1249 | 299.5882 | 301.6351 | 304.2102 | 305.4922 | 306.1266 | 304.1142
Chart: Average Inertia Fall (Sep, Oct, Nov)
2021 | 226.0699 | 211.8177 | 202.7918 | 201.6181 | 202.2725 | 207.6131 | 219.7383 | 223.2821 | 227.413 | 233.0207 | 240.3681 | 249.1726 | 257.358 | 263.184 | 267.7286 | 270.4849 | 272.9902 | 274.308 | 275.3232 | 275.3009 | 273.832 | 269.1135 | 260.3958 | 245.5666
2022 | 232.7218 | 220.0598 | 216.723 | 216.1406 | 216.8247 | 219.8732 | 226.5856 | 230.0273 | 231.7504 | 234.7994 | 238.6793 | 245.2228 | 252.807 | 258.4594 | 262.509 | 266.4033 | 269.5594 | 271.7269 | 273.5526 | 274.619 | 274.1475 | 269.8586 | 260.2322 | 245.8119
2023 | 259.013 | 250.8791 | 249.2032 | 248.913 | 249.4528 | 250.7121 | 253.1197 | 254.5671 | 255.6966 | 256.9835 | 258.1978 | 261.9509 | 266.8325 | 271.8737 | 276.1796 | 280.4613 | 283.8376 | 286.035 | 287.9439 | 289.463 | 289.2568 | 285.61 | 278.3686 | 267.9869
2024 | 256.3181 | 248.2253 | 246.1093 | 245.8965 | 246.1083 | 246.9351 | 247.6228 | 248.0843 | 248.4197 | 247.2382 | 246.0411 | 246.7561 | 249.3671 | 253.1712 | 257.5385 | 263.036 | 268.3873 | 272.1672 | 276.0225 | 279.4194 | 280.1602 | 277.5538 | 272.5298 | 264.0212
2025 | 264.092 | 254.5768 | 250.6163 | 249.7056 | 249.6443 | 249.664 | 250.1539 | 250.1938 | 249.588 | 245.4787 | 241.7658 | 241.2326 | 243.2925 | 246.9918 | 251.2468 | 256.5381 | 264.6949 | 271.8378 | 276.6389 | 280.9564 | 282.2667 | 280.879 | 277.4551 | 271.5819
Chart: Average Inertia Winter (Jan, Feb, Dec*)
2021 | 213.7983 | 211.6785 | 210.5511 | 212.0087 | 215.5655 | 222.6961 | 228.7705 | 230.8776 | 232.2852 | 232.4304 | 231.5578 | 230.239 | 229.3062 | 227.5937 | 226.5242 | 226.7178 | 228.5763 | 230.2344 | 231.5465 | 232.2337 | 231.1264 | 228.3036 | 224.3654 | 219.0983
2022 | 215.0224 | 209.1727 | 207.4775 | 208.2404 | 211.639 | 219.3115 | 228.5732 | 231.5775 | 233.6116 | 235.1351 | 234.3403 | 232.493 | 230.5992 | 230.0536 | 230.4823 | 232.5729 | 235.3696 | 237.9798 | 240.1261 | 240.84 | 239.0984 | 235.4773 | 231.553 | 224.6158
2023 | 216.9184 | 211.8408 | 210.4542 | 211.3322 | 213.781 | 219.2589 | 226.215 | 230.0222 | 232.2642 | 232.8125 | 231.2017 | 229.0871 | 227.4222 | 226.4739 | 226.7636 | 228.7848 | 232.5569 | 236.2378 | 238.6974 | 240.2043 | 239.0056 | 236.0796 | 231.6801 | 224.094
2024 | 232.2633 | 227.4344 | 225.9865 | 226.7066 | 229.3167 | 233.8143 | 237.3708 | 239.3652 | 240.3635 | 238.851 | 233.6023 | 229.9018 | 227.6673 | 226.701 | 227.9463 | 230.8534 | 238.0345 | 244.8052 | 247.9503 | 249.8158 | 249.6885 | 247.8131 | 245.1975 | 240.176
2025 | 249.2931 | 245.4614 | 243.7656 | 244.2771 | 245.8649 | 247.9568 | 249.9639 | 251.5373 | 252.4722 | 250.1982 | 240.6327 | 234.6978 | 232.3586 | 231.9018 | 233.4155 | 237.4487 | 246.6375 | 254.4153 | 258.5774 | 260.62 | 260.4208 | 259.4694 | 257.6119 | 253.5564
2026 | 243.0559 | 238.9346 | 237.2329 | 236.8749 | 236.965 | 237.4117 | 238.0267 | 238.5362 | 238.6329 | 232.274 | 217.6516 | 210.6633 | 209.5465 | 210.2649 | 212.5667 | 217.5623 | 228.8928 | 241.5693 | 246.8941 | 248.7566 | 249.0281 | 248.3951 | 247.4621 | 245.2568

## Slide 65: Monthly Inertia from 2022-2026*
Data only includes up to partial July 2026