## Slide 1: 2027 Ancillary Service Methodology Discussion Luis Hinojosa Manager, Ancillary Services & Operations Analytics ROS August 06, 2026
Key Takeaways
ERCOT is not proposing any changes to the methodology for Regulation and RRS aside from the annual data update.
Interested Stakeholders are requested to provide any feedback on the AS Methodology.
Purpose
Provide proposed methodology to determine Ancillary Service (AS) quantities for 2027.
ERCOT is seeking endorsement on ERCOT’s proposed methodology for computing minimum AS quantities for 2027.

## Slide 2: Introduction
Discrepancy for 2026 Ancillary Services Methodology.
ERCOT has reviewed the methodology to determine minimum Ancillary Service (AS) requirements.
ERCOT is proposing the following changes for 2027.
  Increased risk credit accounting in the proposed probabilistic methodology to compute ERCOT Contingency Reserve Service (ECRS) and Non-Spinning Reserve Service (Non-Spin) requirements.
ERCOT is not proposing any changes in the methodologies used to compute Responsive Reserve Service or Regulation Service.
  NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT for the 2027 Operating Year (OY) has not yet been published. Therefore, this analysis used the minimum RRS-PFR limit of 1,377 MW for 2026.
An HTML with preliminary 2027 AS quantities and redline document of the AS Methodology document are available with todays posting. The HTML also includes 546 scenarios for the probabilistic model with resulting ECRS and NSRS quantities.
  Please note, the data includes values for all monthly quantities for 2027, but 2026 data has not been included yet for months after June and will change once that data is included.
The following slides share the preliminary quantities for each AS based on ERCOT’s proposed methodologies.
2027 Methodology Review Timeline
May 19, 2026 – TAC Kickoff
June 01, 2026 – BOARD Preview
June 17, 2026 – PDCWG
June 29, 2026 – WMWG
July 08, 2026 – WMS
July 09, 2026 – ROS
July 22, 2026 – PDCWG (Proposed)
July 27, 2026 – WMWG (Proposed)
July 28, 2026 – OWG (Proposed)
July 29, 2026 – TAC (2026 AS Methodology Discrepancy)
August 05, 2026 – WMS (Possible Vote)
August 06, 2026 – ROS (Possible Vote)
August 26, 2026 – TAC (Possible Vote)
September 15, 2026 – BoD
Nov, Dec 2026 – PUC

## Slide 3: Discrepancies in the 2026 Probabilistic Model
ERCOT issued a Market Notice on 7/27/2026, indicating ERCOT worked toward the 2027 AS Methodology we identified that the probabilistic model that was used to calculate the 2026 ECRS and NSRS had some discrepancies.
The discrepancies resulted in the model using a lower level of net load uncertainty leading to overall lower quantities than what would have been required by the approved parameters in the 2026 AS Methodology.
The issue only impacts the probabilistic portion of 2026 AS Methodology. The regulation and RRS quantities were not affected.
Going forward, ERCOT will not revise the quantities for August 2026 and has submitted a request for good cause exception with the PUCT under Project 55999. ERCOT will continue to coordinating with PUCT Commissioners and Staff on additional steps required.
ERCOT is also reviewing potential process improvements to prevent similar issues from occurring in the future. This includes immediate implementation of peer review of logic along with potential implementation of AI tools.
Monthly comparisons of the 2026 quantities (black line) and the corrected values (black dotted line) are available in the posted HTML file for today’s meeting

## Slide 4: Good Cause Exception Related Data
ERCOT has requested to continue utilizing the posted quantities for the remaining months of 2026 except for certain hours where the posted ECRS + Non-Spin quantity is not sufficient to cover the restoration of Regulation Up +RRS. The Ancillary Services Methodology gives ERCOT authority to make incremental adjustments to the minimum MW quantities for a particular month, if necessary.
For Jan-Jun months, ERCOT's Real-Time procurement of Non-Spin under the RTC+B paradigm has resulted in actual procurement above the combined Reg Up and RRS level in these hours, so no reliability shortfall has occurred.
For Sep-Dec months, ERCOT will increase the Non-Spin requirement in the limited hours where the posted quantities fall below the combined Reg Up and RRS level (12 month-hour combinations out of 96 (=24 hours x 4 months)), primarily overnight) so that the combined ECRS and Non-Spin quantities are at least sufficient to cover the combined Reg Up and RRS quantities.

## Slide 5: Ancillary Services
Ancillary Services are procured to balance supply and demand while meeting reliability objectives defined in NERC Reliability BAL-001, BAL-002 and BAL-003 Standards, and to reduce operational risks associated with variability and uncertainty
Service | Purpose/Cause | Requirement Basis | NERC Relation
Regulation | SCED dispatches dispatchable resources to forecasted net load (load minus wind minus solar). Regulation offsets the ongoing mismatch between metered and dispatched net load. That mismatch is driven by movement in load, wind, and solar. | Error in the net load forecast SCED used, i.e., 5-minute-ahead load, wind and solar forecast errors | Frequency Control, normal operations and unexpected forced outages Capacity and energy for unexpected forecast errors and forced outages
RRS | Arrest frequency when a unit trips without triggering under-frequency load shed (UFLS). The credible single-resource loss large enough to move system frequency is a dispatchable/synchronous generator; loss of a single wind-turbine or solar-inverter is too small to affect frequency comparably. RRS is held to cover that contingency. | Arrest the loss of the two largest single-resource contingencies without triggering UFLS. Inertia determines how much RRS is needed to avoid triggering UFLS. | 
ECRS | A fast reserve that covers net-load movement within the operating hour that the hourly commitment did not anticipate, bridging until Non-Spin and other resources respond. | 30-minute-ahead load, wind and solar forecast errors | 
Non-Spin | A reserve that is used to cover multi-hour capacity shortfalls the hourly commitment did not anticipate — caused by net load forecast error and resource forced outages — until additional resources are committed. | 6-hour-ahead load, wind and solar forecast errors and 6-hour-cumulative forced outage risk | 

## Slide 6: Uncertainty Growth Analysis
Uncertainty is growing year over year with a majority of growth coming from solar. This is due to overall increase in solar capacity and correlated forecast error.
A deeper dive into solar uncertainty, shows that we have seen an increase in installed capacity in Far East region of Texas in 2025 and 2026.
Far East has more variable weather and cloud cover making forecasting more difficult, especially during ramping hours. This drove the switch from monthly to month-hour solar adjustment values to better capture hour-to-hour variance in solar forecast error.
Additionally, we have observed an overall growth in forced outage MWs which contributes to total risk.

## Slide 7: Hourly Average Regulation Comparison

## Slide 8: Monthly Average Responsive Reserve Service Comparison

## Slide 9: Probabilistic Framework Review
ERCOT Contingnecy Reserve Service (ECRS) & Non-Spinning Reserve (Non-Spin)

## Slide 10: Flow Diagram for Probabilistic Methodology
ERCOT has worked to make several improvements to the model to improve NLFE accounting, solar adjustment for capacity growth, and reduce reliance on tail events. These improvements better account for uncertainty and quantities required.
INPUTS
ENGINE
OUTPUTS
Risks
(X=) hour ahead ahead and 30 min ahead Net Load Forecast Error and
Accumulated Forced Outages in (X=) hours
Risk Credits
(Y=) % of historically available
30 min online headroom
30 min start Offline capacity
ESR capacity sustainable for (W=) hours
Monte Carlo Optimization
Convergence Criteria+ Met?
Net Risk
ECRS + Non-Spin
Requirement
(12 Month x 24 Hour)
No
Yes
ECRS Requirement
(12 Month x 24 Hour)
Non-Spin Requirement
(12 Month x 24 Hour)
+Convergence Criteria: 1 in XX year probability of operating reserves dropping below the sum of YY% (Reg Up plus RRS) or ZZ threshold, whichever is higher. Mathematically, this equates to
𝐸𝐶𝑅𝑆 +𝑁𝑆𝑅𝑆 < 𝑁𝑒𝑡𝑅𝑖𝑠𝑘 + 𝑀𝑎𝑥 (YY(𝑅𝑒𝑔 + 𝑅𝑅𝑆), ZZ) with probability of 1 in XX year.

## Slide 11: Parameters in Probabilistic Framework
Issue | ERCOT’s Recommendation | ERCOT’s Perspective
How far ahead to look at forecast error and forced outages of conventional resources? Parameter X (in hours) | 6 Hours | ERCOT’s recommendation of 6 hours is informed by policy guidance from Summer 2021 to operate to a higher reliability threshold (i.e. operate the system more conservatively with limited RUCs) and is based on historic availability of offline resources during RUC timeframe.
What is the level of risk ERCOT should try to avoid by procuring AS to cover forecast error? Parameter ZZ (in MW) | 3,000 i.e. Watch | ERCOT has noticed minimal difference in outcomes between ZZ = 3,000, 2,500 and 1,500 MW since quantities for most hours are a function of the amount of Reg Up plus RRS that these reserves have to replace.
What level of minimum reserves (Reg+RRS) should be maintained? Parameter YY (in %) | 100% | ERCOT proposes full restoration of deployed Reg Up + RRS. With that requirement, changing the target reserve level from Watch to EEA or Load Shed may not materially reduce quantities in many hours because Reg Up + RRS restoration often controls the requirement. Restoration of these fast-response reserves is critical to maintaining reliability and staying compliant with NERC BAL requirements.
How much should we discount the AS quantities for a particular time period based on the “extra” headroom from resources that were historically committed by market in that time period? Parameter Y (in %), W (in hours) | Online:60% in Night and 50% in Day Offline:60% in Night and 50% in Day ESR:60% in Night and 60% in Day Sustainable for 4 hours | ERCOT has observed that although RTC+B has had an impact on available (online + offline) headroom capacity, we are seeing additional capacity available that can be accounted for in the model. ERCOT expects the trend of having higher available (online + offline) headroom capacity during night hours to continue

## Slide 12: Risk Credit Review
The charts to the right are showing the performance analysis of proposed risk credits for online and offline of 60% at night and 50% during day hours. With ESR credits of 60% at night and 60% during day hours with 4 hours sustainable capacity.
Online/Offline Headroom:
  We have observed a shift in availability in online headroom to the day hours when solar is available. Morning and evening hours have seen a reduction in online headroom as it shifts to offline headroom availability. This was expected as an outcome of RTC+B.
ESR Headroom:
  Overall, here is where we see the largest increase in capability in each category. It can be observed that there is significant increase through out most hours, only very few small increase or reduction during evening hours. This increase in capability is largely due to an increase in installed capacity in ESR over the year.
  A of now we are projecting ESR capacity to continue to grow in 2027, allowing for further certainty of risk credit increase, but we are also aware that there may be a point when this may slow down and the risk credit should be reevaluated.
A seasonal effect can also be observed form these charts. There is more availability during winter months and reduced availability as we come to the summer months. We also see April has the least increase in availability due to high outages during this period.

## Slide 13: Preliminary Quantities with Proposed Parameters and Scenarios
To support a finding in the PUCT’s 2024 Ancillary Services Study we wanted to provide the ability to compare alternative reserve levels estimated cost, and modeled reliability-risk metrics.
Additionally, Stakeholders have asked for specific scenarios that they would like to review. We have provided an HTML with today’s postings which allows Stakeholders to add in scenarios based on the parameters available. 546 Scenarios are included.
  Scenarios that are expected to produce identical results to other parameter selections are not included in the HTML. We have provided an additional document indicating duplicate scenarios for tracking purposes.
  Please note, the data includes values for all monthly quantities for 2027, but 2026 data has not been included yet for months after June and will change once that data is included.
If you see a combination that you would like to see please provide that feedback.

## Slide 14: Summary
Based on the analysis ERCOT has conducted thus far,
  ERCOT is not considering any changes in the methodologies used to compute Regulation and Responsive Reserve Service requirements for 2027.
  ERCOT is proposing an increase in risk credit accounting and has incorporated several corrections/improvements to the Probabilistic model to account for RTC+B impacts along with accounting for stakeholder feedback approach to compute the ECRS and Non-Spin requirements for 2027.
An HTML with preliminary proposed quantities for Regulation, RRS, ECRS and NSRS. Additionally, there are 546 scenarios for the probabilistic model for ECRS and NSRS are included with resulting preliminary quantities.
The proposed timeline for this review is included alongside.
ERCOT is seeking endorsement on ERCOT’s proposed methodology for computing minimum AS quantities for 2027.
2027 Methodology Review Timeline
August 05, 2026 – WMS (Possible Vote)
August 06, 2026 – ROS (Possible Vote)
August 26, 2026 – TAC (Possible Vote)
September 15, 2026 – BoD
Nov, Dec 2026 – PUC

## Slide 15: Questions?
JoseLuis.Hinojosa@ercot.com

## Slide 16: Appendix

## Slide 17: Fast-moving Ancillary Services respond immediately maintain system balance
Regulation Up & Down Service
  Purpose — Balances supply and demand to maintain frequency close to 60Hz between 5-minute dispatch intervals; deployed every 4 seconds.
  Why it matters — keeps the system continuously balanced; needs grow as net-load variability rises.
Responsive Reserve Service (RRS)
Purpose — Responds very quickly to arrest frequency during low frequency events typically triggered by generating unit trips.
Why it matters —the first line of defense for frequency; sized to system inertia (2,300 MW floor).
June 4, 2022
Unit Trip
Increase in output from supply resources providing RRS
Decrease in demand from load providing RRS using relay

## Slide 18: Longer lead-time Ancillary Services address uncertainty and help to recover depleted reserves
ERCOT Contingency Reserve Service (ECRS)
Purpose — reserve that responds within 10 minutes to recover frequency, cover forecast errors and ramps, and replace deployed reserves.
  Why it matters — bridges the fast (RRS) and slow (Non-Spin) reserves; quantity set using the probabilistic modeling of reliability risks.
Non-Spinning Reserve Service (Non-Spin)
Purpose — Capacity that can be started in 30 minutes to cover forecast errors, ramps or forced outages and replace deployed reserves until additional resources can be committed.
Why it matters —30min lead time backstop for sustained uncertainty events; quantity set using the probabilistic modeling of reliability risks.
(Additional Event Details)

## Slide 19: Expected Battery Installation in ERCOT
Projecting indicate ESR capacity to continue to grow in 2027, allowing for further increase in risk credit accounting for ESR, but we are also aware that there may be a point when the rate of install may slow down. Taking high risk credit should be evaluated at least annually.

## Slide 20: Average Inertia per Hour 2021-2026.7*
From 2025 and onwards the lowest hours of inertia have moved from the night hours to the middle of the day.
Chart: Average Inertia per Hour
2021 | 231.0167 | 220.1128 | 213.1623 | 211.6564 | 212.9705 | 218.081 | 227.1576 | 230.2275 | 233.8436 | 238.6224 | 244.5739 | 251.63 | 257.1866 | 261.1305 | 263.7966 | 265.7325 | 267.5027 | 268.5498 | 269.1126 | 268.8539 | 267.2982 | 264.21 | 258.4143 | 247.7114
2022 | 242.2104 | 230.1495 | 225.6586 | 224.6807 | 225.7149 | 228.976 | 235.0458 | 238.5265 | 240.9776 | 244.447 | 249.2677 | 255.2333 | 261.0441 | 265.7481 | 269.5065 | 272.7489 | 275.5718 | 277.8449 | 279.4513 | 279.8506 | 278.6995 | 275.841 | 269.0215 | 256.0439
2023 | 252.8735 | 244.8053 | 242.5019 | 242.0444 | 243.2221 | 246.0671 | 249.7546 | 251.87 | 253.1422 | 253.8195 | 254.6727 | 257.4508 | 261.2272 | 264.9961 | 268.538 | 272.2741 | 275.936 | 278.6422 | 280.4322 | 281.5987 | 281.8577 | 280.1138 | 274.4063 | 263.7
2024 | 258.0981 | 250.7432 | 247.7776 | 247.4828 | 248.0455 | 249.5654 | 251.0366 | 252.0673 | 252.7508 | 251.963 | 250.2722 | 250.5321 | 252.0039 | 254.1677 | 257.3306 | 261.4172 | 266.7966 | 271.0318 | 274.0031 | 276.1466 | 277.2741 | 276.6432 | 273.3345 | 266.0568
2025 | 265.3627 | 257.1726 | 253.0719 | 251.8397 | 251.8678 | 252.2827 | 252.9021 | 253.4262 | 253.363 | 249.9522 | 244.3523 | 242.108 | 242.9884 | 245.4785 | 249.0457 | 253.5288 | 260.4978 | 267.5324 | 272.9577 | 276.2678 | 278.3478 | 278.3629 | 276.2722 | 271.6489
2026^ | 249.8076 | 242.9699 | 238.7987 | 237.3165 | 236.6611 | 236.4224 | 236.489 | 236.5763 | 235.606 | 229.7704 | 221.1654 | 218.1252 | 218.6538 | 220.2005 | 222.7299 | 226.3442 | 233.1995 | 242.6697 | 249.4509 | 252.9033 | 255.0781 | 255.6681 | 255.4966 | 253.5893
Data only includes up to partial July 2026