## Slide 1
PDCWG Report to ROS
Chair: Paul Messmann
Vice Chair: Open (ERCOT Interim)
ROS
August 6th, 2026

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
    BAL-001-TRE-2 Process Update
    Texas RE Report
    Frequency Control & Regulation Reports
    Analysis of Disturbances
  BAL-001-TRE-2 Process Update
  Frequency Control Report

## Slide 3: BAL-001-TRE process overview
ERCOT Identifies Frequency Measurable Events (FMEs)
1
ERCOT Posts FME Notification within 14 Calendar Days
2
ERCOT Calculates Initial & Sustained Primary Frequency Response (PFR) per BAL-001-TRE Standard
3
ERCOT Posts the Initial and Sustained Primary Frequency Response Unit Performance Reports(FME Reports) to MIS
4
ERCOT Calculates and Posts in MIS the Rolling 12-Month Average Initial and Sustained PFR Scores
6
ERCOT Evaluates RRS MW Limits for Resources Not Meeting the performance Criteria and Posts the RRS Limit Reports to MIS
7
Market Participants to Review Reports and Submit Exclusion Requests for Legitimate Operating Conditions within 30 days
5

## Slide 4: Frequency Control Report

## Slide 5: CPS1 Performance
Current 12-Month Rolling Average: 181.97%
Notes: 12 month rolling average CPS1 score is 181.97 which is continuing the increasing trend of CPS1 scores.

## Slide 6: RMS1 Performance of ERCOT Frequency
Notes: A More granular look at last 15 years of RMS1 by month
11.93 mHz on avg for June 2026

## Slide 7: Frequency Profile Analysis
Notes: Comparison of frequency profile between June 2025 and June 2026.

## Slide 8: Time Error Corrections
Notes: No time error corrections in the month of June

## Slide 9: ERCOT Total Energy
Notes: 35,438,4249 MWh

## Slide 10: ERCOT Total Energy from Wind Generation
Notes: 6,741,089 MWh

## Slide 11: ERCOT % Energy from Wind Generation
Notes: 19.02% of total energy was provided by wind generation

## Slide 12: ERCOT Total Energy from Solar Generation
Notes: 6,472,397 MWh

## Slide 13: ERCOT % Energy from Solar Generation
Notes: 18.26% of total energy was provided by solar generation

## Slide 14: ERCOT Daily Minimum System Inertia
Notes: Minimum Inertia in June 2026 = 218,377 MW*s
Historical Overall Minimum was 109,029 MW*s on 3/22/2021
June Data:
Mean: 261,685 MW*s
Max: 300,365 MW*s on June 19th
Min: 218,377 MW*s on June 28th

## Slide 15: Total Inertia 2016-2026
Date and Time | 2016 4/10 2:00 AM | 2017 10/27 4:00 AM | 2018 11/03 3:30 AM | 2019 3/27 1:00 AM | 2020 05/01 2:00 AM | 2021 03/22 1:00 AM | 2022 03/21 2:00 AM | 2023 04/18 3:00 AM | 2024 03/29 4:00 AM | 2025 03/18 12:00 PM | 2026* 03/14 12:00 PM
Min synch. Inertia (GW*s) | 143 | 130 | 128.8 | 134.5 | 131.1 | 116.6 | 115.0 | 124.3 | 129.9 | 118.3 | 114.7
System load at minimum synch. Inertia (MW) | 27,831 | 28,425 | 28,397 | 29,883 | 30,679 | 31,767 | 33,784 | 35,578 | 37,039 | 49,130 | 48,013
Non-synch. Gen. in % of System Load | 47 | 54 | 53 | 50 | 57 | 66 | 65 | 61 | 68 | 74 | 81
FFR Award | N/A | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 134 | 298 | 430
Critical Inertia (GW*s) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 93 | 92 | 87
Red circles denote inertia at max IRR penetration (= IRR Gen/Total Gen)
Notes: Summary of ERCOT inertia for the previous 10 years. Lowest inertia this year was on March 14th.
For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.

## Slide 16
Questions?