## Info
Header Information
TDSP | Operator of the Major Transmission Element.
Major Transmission Element (MTE) | Transmission Element which was, or scheduled to be, on outage and has been associated with one or more high congestion(s).
Equip. Type | Equipment Type of the MTE.
kV | Voltage Level of the MTE. High-side voltage for transformers
Congestion Year/Month | Year and Month the associated congestion occurred.
Contingency | Contingency associated with the MTE.
Overload | Overload associated with the MTE.
Source | Source of the information: RT = Based on historical Real-Time congestion, ST = Based on Outage Coordination Studies. ADD = Addition Requests (both Private and Public)
Outage Type | Outage Type is categorized to be either Planned (PL) and Forced (FR, FE, UE, M1, M2, M3)
Cancel | Outage(s) for the specific MTE was Cancelled, Rejected, or Withdrawn.
Removal Requestor | Stakeholder who is requesting to remove the MTE from the list (Organization)
Addition Requestor | Stakeholder who is requesting to add the MTE from the list (Organization)
Reason for Addition | Justification for adding the MTE to the list. Details of the specific scenarios that the MTE may cause high congestion, including but not limited to: 1. ERCOT Load Level: Peak, Off-Peak (or 35GW, 70GW, etc). 2. Any specific regional load condition: High Houston Load, etc. 3. Wind Generation Level: High, Mid, Low, or N/A. 4. Solar Geneartion Level: High, Mid, Low, or N/A. 5. Any specific abnormal transmission equipment status: i.e. 345 kV line from A to B out-of-service, etc. 6. For Private Submissions, any specific generator output level: i.e. Resource A at 300 MW or above, etc. 7. (Optional) PSSE or PowerWorld case if available.
Reason for Removal | Justification for removing the MTE from the list. Usually entails a Transmission Upgrade Project.
OCITF Consensus | Consensus after OCITF meetings.
Decision | Final (TAC) Decision of the Addition/Removal Request for Non-Consensus items.
Discussion Items | Any other information that stakeholder(s) want to discuss during the OCITF meetings.

## MTE(2026)
TDSP | Update Action | Removal / Edit Requestor | Reason for Removal | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year/Month | Contingency | Overload | Source | Outage Type | Cancel | OCITF Consensus | Decision | Discussion Items | From Acronym | To Acronym | ERCOT Equip Name | ERCOT Contingency ID
AEP |  |  |  | Abilene Elmcreek - Abilene Northwest | LN | 138 | 25/2 | Sweetwater East Switch -…- Perigee 345kV | Abilene Northwest Series Device 1 | RT | Planned |  |  |  |  | ELMCRK | ABNTHWST | ABNTHW_ELMCRK1 | SABEABN8
AEP |  |  |  | Abilene Mulberry Creek - Abilene Northwest | LN | 138 | 25/3 | Foxtail To Oklaunion Lin 1 345kV | Abilene Elmcreek - Abilene Industrial Park 138kV | RT | Planned |  |  |  |  | MULBERRY | ABNTHWST | ABNTHW_MULBER1 | SABNABM8
AEP |  |  |  | Abilene Mulberry Creek - Bluff Creek | LN | 345 | 25/3, 25/4 | Sweetwater East Switch To Long Creek Lin _a 345kV, DCKT Riley - Bowman Switch 345kV | Abilene Mulberry Creek - Long Creek 345kV, Fisher Road Switch - Riley 345kV | RT | Planned |  |  |  |  | BLUF_CRK | MULBERRY | BLUF_C_MULBER1 | SABMBLU5
AEP |  |  |  | Abilene Mulberry Creek - Perigee | LN | 345 | 25/6 | Comanche Peak SES - Comanche Switch 345KV | Comanche Switch - Comanche TAP 345KV | RT | Planned |  |  |  |  | MULBERRY | PERIGEE | MULBER_PERIGE1 | SPERMUL5
LCRA | REMOVE | LCRA | No congestion on T629 Goldthwaite - San Saba Switch 138KV | Adamsville - Evant | LN | 138 | 26/4 | DCKT Buckhorn Switch - Killeen Switch 345KV & Russell Gap Switch - Killeen Switch 345KV | Goldthwaite - San Saba Switch 138KV | RT | Planned |  |  |  |  | ADAMSV | EVANT | 672T672 | SLAMADA8
CNPE |  |  |  | Addicks - TH Wharton | LN | 345 | 22/4 | Roans Prairie - Singleton 345 kV & Singleton - Tomball 345 kV | TH Wharton - Zenith 345 kV | RT | Planned |  |  |  |  | THW | ADK | ADKTHW71A | SADKTHW5
CNPE |  |  |  | Addicks - White Oak | LN | 345 | 23/1 | DCKT Obrien-WAP (OB-WAP98 & OB-WAP99) 345 kV | Jeanetta - Westwood 138 kV | RT | Planned |  |  |  |  | WO | ADK | ADKWO_71 | SWOADK5
CNPE |  |  |  | Airpro - Boggy | LN | 138 | 23/1 | Jefferson - College 138 kV | Conial - Philip 138 kV | RT | Planned |  |  |  |  | AZ | BOG | AZ_BOG85A | SAZBOG8
AEP |  |  |  | Ajo - Cebolla | LN | 345 | 25/4 | Lon Hill To Nelson Sharpe Lin 1 345kV | Celanese Bishop - Nelson Sharpe 138kV | RT | Forced |  |  |  |  | CEBOLLA | AJO | AJO_CEBOLL1 | SAJ2CEB5
AEP |  |  |  | Ajo - Nelson Sharpe | LN | 345 | 25/11 | Kleberg Aep - Loyola Sub 138 KV | Ricardo Sub - Riviera Sub 69KV | RT | Planned |  |  |  |  | AJO | N_SHARPE | AJO_N_SHAR1 | SN_SAJO5
TNMP |  |  |  | Alvin TNP - Mainland TNP | LN | 138 | 21/11 | Meadow - Ph Robinson 345 kV | Magnolia Tnp - Seminole Tnp 138 kV | RT | Planned |  |  |  |  | MAINLAND | ALVIN | 138_ALV_MNL | SALVMAI8
TNMP |  |  |  | Alvin Tnp - North Alvin Tnp | LN | 138 | 23/5 | Meadow - PH Robinson 345 kV | Magnolia Tnp - Seminole Tnp 138 kV | RT | Planned |  |  |  |  | ALVIN | TNNALVIN | 138_ALV_NAL | SALVTNN8
AEP |  |  |  | Angstrom - Grissom | LN | 345 | 25/10 | Lon Hill - Whitepoint 345KV | Nueces Bay - Whitepoint 138KV | RT | Planned |  |  |  |  | ANGSTROM | GRISSOM | ANGSTR_GRISSO1 | SANGGRI5
AEP, CNPE |  |  |  | Angstrom - South Texas Project | LN | 345 | 25/2 | DCKT South Texas Project - Elmcreek 345kV | Blessing Auto 1382 345/138kV | RT | Planned |  |  |  |  | STP | ANGSTROM | ANGSTR_STP1 | MANGNAI5
AEP, CNPE |  |  |  | Angstrom - Static | LN | 345 | 25/11, 26/1 | DCKT South Texas Project - Elmcreek & Wa Parish 345kV | Blessing 345_1382 345/138kV | ST | Forced |  |  |  |  | ANGSTROM | STATIC | ANGSTR_STATIC1 | SANGSTA5
ONCOR | REMOVE | ONCOR | Remove this MTE due to Oncor establishing Gunter Switch, Dunham Switch and Ramhorn Hill Switch which increased 345 kV connectivities in the areas where the MTEs and Contingencies are located. This MTE, Anna Switch - Cedar Elm Switch, no longer exists due to Gunter Switch being cut in between Anna Switch and Cedar Elm Switch | Anna Switch - Cedar Elm Switch | LN | 345 | 22/3 | Krum West Switch - Lewisville Switch 345 kV & Lewisville Switch - Roanoke Switch 345 kV | Argyle - Highlands Tnp 138 kV | RT | Planned |  |  |  |  | CDESW | ANASW | 38025_A | SCDEANA5
ONCOR | REMOVE | ONCOR | Remove this MTE due to Oncor establishing Gunter Switch, Dunham Switch and Ramhorn Hill Switch which increased 345 kV connectivities in the areas where the MTEs and Contingencies are located. This MTE, Anna Switch - Krum West Switch, no longer exists due to Gunter Switch being cut in between.Anna Switch and Krum West Switch | Anna Switch - Krum West Switch | LN | 345 | 21/12, 22/3 | Krum West Switch - Lewisville Switch 345 kV & Lewisville Switch - Roanoke Switch 345 kV | Argyle - Highlands Tnp 138 kV | RT | Planned |  |  |  |  | KRWSW | ANASW | 38010_A | SANAKR15
LCRA |  |  |  | Antler - Highway 46 | LN | 138 | 23/7 | DCKT Bergheim - Kendall 345 kV & Kendall - Welfare 138 kV | Cranes Mill - Sattler 138 kV, Hunter - Purgatoy Road 138 kV | RT | Forced |  |  |  |  | ANTLER | HIGH46 | 610T610 | SANTRIV8
AEP |  |  |  | Armstrong Aep - Yturria Sub | LN | 138 | 23/7, 25/2 | Lon Hill To Nelson Sharpe Lin 1 345kV, Ajo - Nelson Sharpe 345 kV | Celane Bishop - Nelson Sharpe 138kV, Falfurias - Premont 69 kV | RT | Forced, Planned |  |  |  |  | LOYOLA | ARMSTRON | ARMSTR_LOYOLA1 | SARMRA38
AEP |  |  |  | Arroz - … - Lane City | LN | 138 | 23/10 | Esperanza - STP Switch 138 kV | Blessing - Lavlov 138 kV | RT | Planned |  |  |  |  | ARROZ | LANCTY | ARROZ_LANCTY1 | SLANARR8
LCRA, ONCOR | REMOVE | ONCOR | Remove this MTE due to Austrop - Sandow Switch (450) no longer being a valid MTE circuit as new Walleye Creek Switch was cut in between Austrop and Sandow Switch. MTE is no longer valid because of Walleye Creek Switch/Beulah Switch cut-ins into Austrop-Sandow | Austrop - Sandow Switch (450) | LN | 345 | 22/4 | Hutto Switch - Zorn 345 kV & Hutto Switch - Gilleland Creek 345 kV, AEN Gilleland Creek - Techridge 138 kV | Round Rock - Round Rock Northeast 138 kV (1661_A), Gilleland Creek - Mcneil 138 kV | RT | Planned |  |  |  |  | SNDSW | AUSTRO | 450 | SSNDAUS5
LCRA, ONCOR | REMOVE | ONCOR | Remove this MTE due to Austrop - … -Sandow Switch (440) no longer being a valid MTE circuit as new Walleye Creek Switch was cut in between Austrop and Sandow Switch. MTE is no longer valid because of Walleye Creek Switch/Beulah Switch cut-ins into Austrop-Sandow | Austrop -…- Sandow Switch (440) | LN | 345 | 22/4 | Hutto Switch - Zorn 345 kV & Hutto Switch - Gilleland Creek 345 kV, AEN Gilleland Creek - Techridge 138 kV | Round Rock - Round Rock Northeast 138 kV (1661_A), Gilleland Creek - Mcneil 138 kV | RT | Planned |  |  |  |  | SNDSW | AUSTRO | 440 | SSNDAU15
LCRA, STEC |  |  |  | Bakersfield - Cedar Canyon (BAKRFLD_CEDCA2) | LN | 345 | 24/9, 24/10 | Meteor Switch to Wolf Switching Station Lin_A, Meteor Switch to Moss Switch Lin_B | Odessa Ehv Switch - Yarbrough Sub 138kV, Penwell Pod - Wolf Switching Station 138kV | RT | Planned |  |  |  |  | CEDACA | BAKESW | BAKRFLD_CEDCA2 | SBAKCED5
LCRA, STEC |  |  |  | Bakersfield - Cedar Canyon (BAKRFLD_CEDCAN) | LN | 345 | 22/4 | Midessa South Sw - Odessa EHV Switch 345 kV & Morgan Creek Ses -…- Quail Switch 345 kV, DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses, Moss Switch - Odessa EHV Switch 345 kV & Odessa EHV Switch - Wolf Switching Station 345 Kv | Midessa South SW AXFMR1 345/138 kV, Dewey Lake Tap - Polecat Creek Switch 138 kV, Falcon Seaboard - Morgan Creek Ses 345 kV, Odessa - Odessa North 138 kV | RT | Planned |  |  |  |  | CEDACA | BAKESW | BAKRFLD_CEDCAN | SBAKSCH5
ONCOR | MODIFY | ONCOR | MTE should be changed from "Barber Lake Switch - Ranger Camp Switch (14035_B)" to "Barber Lake Switch - Ranger Camp Switch (14035_A)" | Barber Lake Switch - Ranger Camp Switch (14035_A) | LN | 138 | 24/5 | Wett_long_draw To Vealmoor 345kV | Ranger Camp Switch - Moser Canyon POD 138 kV | RT | Planned |  |  |  |  | BRBSW | MGSES | 14035_A | SBRBMG38
AEP |  |  |  | Barney Davis -...- Nelson Sharpe | LN | 138 | 25/3 | Lon Hill To Nelson Sharpe Lin 1 345kV | Celanese Bishop - Nelson Sharpe 138kV | RT | Planned |  |  |  |  | B_DAVIS | ALAZAN | ALAZAN_B_DAVI1 | SALAN_28
CNPE |  |  |  | Bayou Cogen - Big Bay | LN | 138 | 24/11 | Twr (138) Arm-ft35 & Ft-phr35 | Drouet - Garden Villas 138kV | RT | Forced |  |  |  |  | BYU | BBP | BBPBYU79 | SBBPBYU8
BRAZOS |  |  |  | Bell County -…- Gabriel & Bartlett | LN | 69 | 25/1, 25/2 | DCKT Georgetown East -…- Bell County 345kV, DCKT Salado Switch - Knob Creek Switch 345 And Temple Switch - Bell County | Bell Country Auto XFMR 138/69 kV | RT | Planned |  |  |  |  | BELCNTY | BARTLTSW | BEL_BART | SBARGAB9
ONCOR |  |  |  | Bell County -…- Temple Switch | LN | 138 | 25/4 | DCKT Chief Brady -…- Spanish Oak 138kv, Round Rock To Hutto Switch Lin 138kV | Round Rock - Round Rock Westinghouse 138kV | RT | Planned |  |  |  |  | BELCNTY | TMPSW | 1715_A | SBELTMP8
ONCOR | MODIFY | ONCOR | MTE should be changed from "Bell County East Switch - Sandow Switch" to "Bell County East Switch - … - Sandow Switch" | Bell County East Switch - … - Sandow Switch | LN | 345 | 24/6, 24/7, 24/8, 25/10, 25/11 | DCKT Salado Switch - Hutto Switch 345 Dblckt | Sandow Switch - Bell County East Switch Lin 421 345kV | RT | Planned |  |  |  |  | SNDSW | BCESW | 421 | SBCESN35
CNPE |  |  |  | Bellaire - Kirby | LN | 138 | 21/10 | Eastside - Polk 138 kV | Downtown - Polk 138 kV | RT | Planned |  |  |  |  | BI | KB | BI_KB_37A | SKBBI8
CNPE |  |  |  | Bellaire - Smithers | LN | 345 | 24/9, 24/10 | Twr (345) Jn-wap64 & Jn-wap72 | Bellaire - Wa Parish 345kV | RT | Forced |  |  |  |  | BI | SMITHERS | BI_SMR98 | SBISMI5
ONCOR |  |  |  | Belton - … - Killeen Switch (641) | LN | 138 | 24/4 | DCKT Killeen Switch - Salado Switch 345 kV | Killeen Switch - Harker Heights South 138 kV | RT | Planned |  |  |  |  | KLELM | KLNTF | 641_B | SHKHKLN8
ONCOR |  |  |  | Benbrook -...- Wedgewood Switch (6120_J) | LN | 138 | 25/4 | DCKT Mitchell Bend Switch - Rocky Creek & Timberview Switch - Benbrook Switch 345 kV | Hemphil - Mistletoe Heights 138kV | RT | Planned |  |  |  |  | BNBRK | BRIRV | 6120_J | SBNBBNB8
ONCOR |  |  |  | Benbrook -…- Wedgewood Switch (6115_J) | LN | 138 | 25/4 | DCKT Mitchell Bend Switch - Rocky Creek & Timberview Switch - Benbrook Switch 345 kV | Hemphil - Mistletoe Heights 138kV | RT | Planned |  |  |  |  | BNBRK | BRIRV | 6115_J | SBNBBN28
ONCOR |  |  |  | Benbrook Switch - Parker Switch (6005_A) | LN | 345 | 21/10 | Comanche Peak Ses - Mitchell Bend Switch 345 kV & Comanche Peak Ses - Wolf Hollow 345 Switch 345 kV, DBCKT Comanche Peak Ses - Parker Switch 345 kV | Benbrook Switch - Parker Switch 345 kV (6042_A) | RT | Planned |  |  |  |  | BNBSW | PKRSW | 6005_A | SBNBPKR5
ONCOR |  |  |  | Benbrook Switch - Parker Switch (6042) | LN | 345 | 25/3 | DCKT Comanche Peak SES - Wolf Hollow Switch & Mitchell Bend Switch 345kV, DCKT Mitchell Bend Switch - Carmichael Bend Switch & Rocky Creek 345kV | Benbrook Switch - Parker Switch 345kV (6005) | RT | Planned |  |  |  |  | PKRSW | BNBSW | 6042 | SBNBPK25
ONCOR |  |  |  | Benbrook Swith - … - Timberview Switch | LN | 345 | 17/2, 17/3, 19/11, 20/10 | DCKT Wedgewood Sw - Benbrook Switch 138 kV, DCKT Timberview Switch - Comanche Peak SES & Carmichael Bend Switch 345 KV | Hemphill - Mistletoe Heights 138 kV | RT | Forced, Planned | N |  |  |  | BNBSW | SYCRK | 6000_A | SSYCEV25
LCRA |  |  |  | Bergheim - Hays Energy | LN | 345 | 21/10, 22/7, 22/8, 23/2, 23/3 | Cagnon - Kendall 345 kV & Cico - Menger Creek 138 kV, Cagnon - Kendall 345 kV & Cico - Comfort 138 kV, DCKT Cagnon-Kendall 345 kV&Txresch-Tally_Rd 138 kV | Medina Lake - Pipe Creek 138 kV, Bergeim - Kendall 345 kV, Bergheim Auto AT1 345/138kV, Helotes - Ranchtwn 138 kV, Medila Lake - Pipec Creek 138 kV | RT | Forced |  |  |  |  | BERGHE | HAYSEN | 398T3891 | SHAYBER5
LCRA |  |  |  | Bergheim - Kendall | LN | 345 | 20/12, 25/4, 25/5 | DCKT Cagnon-Kendall 345 kV & Cico-Comfort 138 kV, Zorn - Haysen 345KV, Cagnon-kendal 345 &cico-mengcr 138 | Mason Creek - Bandera 138 kV, Bergheim Auto, Txresrch - Tally_rd 138kV | RT | Forced, Planned | N |  |  |  | BERGHE | KENDAL | 656T6561 | SKENBER5
STEC |  |  |  | Bevo Auto BEVO 138/69 kV | XF | 138 | 15/6 | Bevo Sub to Asherton 138 kV | Hamilton Road - Maverick 138 kV | RT | Planned |  |  |  |  | BEVO |  | BEVO | XBEV89
ONCOR |  |  |  | Bird Dog Switch - Jacksboro Switching (37010) | LN | 345 | 23/5 | Hicks Switch - Exchange Switch 345 kV (106) | Hicks Switch - Exchange Switch 345 kV (107) | RT | Planned |  |  |  |  | JCKSW | KRWSW | 37010 | SJCKBDG5
ONCOR |  |  |  | Bluff Creek Switch - China Grove Switch | LN | 138 | 25/8, 25/9, 25/10, 25/11 | DCKT Dermott Switch - Scurry County South Switch 345kV | Deep Creek Sub - Sacroc 138KV | ST | Forced |  |  |  |  | BCKSW | CGRSW | 6215 | SBCKCGR8
ONCOR |  |  |  | Bluff Creek Switch -…- Dermott Switch | LN | 138 | 25/4 | DCKT Dermott Switch - Scurry County South Switch 345 kV | Deep Creek Sub - Sacroc 138kV | RT | Planned |  |  |  |  | KNAPP | SCRCV | 6437_F | SKNADM48
LCRA |  |  |  | Boerne - Welfare | LN | 138 | 25/5 | DCKT BERGHEIM - Hays Energy 345KV & Henne - River Oaks 138KV | Purgatory Road - Sattler 138KV | RT | Planned |  |  |  |  | BOERNE | WELFAR | 385T228 | SBOEWEL8
CNPE |  |  |  | Boggy - Pair | LN | 138 | 22/10 | DCKT Exxon - Baytown & SR Bertron - Texas 138 kV, DCKT SR Bertron - Quanab & Dowlap 138 kV | Jefferson - Sc Channel 138 kV | RT | Forced, Planned |  |  |  |  | BCV | PSA | BCVPSA | SBCVPSA8
BRAZOS |  |  |  | Bosque Switch - Whitney | LN | 345 | 26/3 | Bosque Switch - Whitney 345KV | Lake Whitney TNP - Whitney 138KV | RT | Planned |  |  |  |  | BOSQUESW | WHTNY | BOS_WHI | SBOSWHT8
CPS | REMOVE | CPS | Removal due to Cagnon to Calaveras line no longer exists with the addition of Station S2 (Howard Rd 345kV) and conductor upgrades | Braunig - Calaveras | LN | 345 | 21/1 | DCKT Skyline-Calaveras 345 kV | Cagnon - Calaveras 345 kV | RT | Planned | N |  |  |  | CALAVERS | BRAUNIG | N5_U31 | SBRACAL5
ONCOR |  |  |  | Brown Switch - Buckhorn Switch | LN | 345 | 20/12, 21/6, 22/9, 22/12 | Comanche Sw (Oncor)-Comanche Peak 345 kV, DCKT Bighil-Kendall 345kV | Comanche Tap - Comanche Switch (oncor) 138 kV, Yellow Jacket - Treadwell 138 kV | RT | Forced, Planned | N |  |  |  | BUCSW | BWNSW | 35095 | SBWNBUC5
AEP | REMOVE | AEP | Long time since last occurred. | Bruni - Crestonio | LN | 138 | 15/5, 15/6 | Laquinta to Lobo 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y, N |  |  |  | BRUNI4 | CRESTONI | BRUNI4_CRESTO1 | SCREBRU8
TMPA |  |  |  | Btu_Jack_Creek - Gibbons Creek | LN | 345 | 16/1, 17/4 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Twin Oak Sw 345 kV, BTU_Jack_Creek Auto XF1 345/138 kV | RT, ST | Planned | Y |  |  |  | GIBCRK | JK_CK | GC_JK | SJK_GIB5
ONCOR |  |  |  | Buckhorn Switch - Killeen Switch (35092) | LN | 345 | 22/12 | Comanche Sw (Oncor)-Comanche Peak 345 kV | Comanche Tap - Comanche Switch (oncor) 138 kV | RT | Planned |  |  |  |  | KLNSW | BUCSW | 35092 | SBUCKLN5
CNPE |  |  |  | Bunker - H O Clarke | LN | 138 | 21/9 | Meadow - Oasis 345 kV | Blodgett - Garrott 138 kV | RT | Planned |  |  |  |  | BUN | HOC | BUNHOC08 | SBUNHO28
ONCOR |  |  |  | Burwick Switching Station - Graham SES | LN | 345 | 21/10 | DBCKT Graham Ses - Parker Switch 345 kV | Barton Chapel Wind Farm - Graham Switch 138 kV, Barton Chapel Wind Farm - Juniper 138 kV | RT | Planned |  |  |  |  | BURSW | GRSES | 36030_A | SGRSJC25
CPS, STEC |  |  |  | Calaveras - Pawnee Switching Station | LN | 345 | 24/3, 25/2 | DCKT Elmcreek - San Miguel Gen 345 Kv | Coy City Tap - Pleasanton 138kV, Blessing - Lolita 138 kV | RT | Forced, Planned |  |  |  |  | PAWNEE | CALAVERS | PAWNEE_SPRUCE | SPAWCAL5
CPS | REMOVE | CPS | Removal due to Cagnon to Calaveras and Cagnon to Braunig lines no longer exists with the addition of Station S2 (Howard Rd 345kV) and conductor upgrades | Calaveras - Skyline (N5_P4_1) | LN | 345 | 17/5, 17/12, 22/3, 22/4, 22/5 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, DCKT Hill Country to Marion 345 kV, HILL COUNTRY to CAGNON 345 kV | Skyline - Calaveras 345 kV, Pawnee Switching Station - Calaveras 345 kV, Skyline - Elmcreek 345 kV, Coleto Creek - Rosata Tap 138 kV, Cagnon - Calaveras 345 kV, Pawnee Swithing Station Auto XF1 345/138 kV, Cagnon Auto XFMR4L-H 345/138 kV | RT | Forced, Planned |  |  |  |  | CALAVERS | SKYLINE | N5_P4_1 | SSKYCA25
CPS | REMOVE | CPS | Removal due to Cagnon to Calaveras and Cagnon to Braunig lines no longer exists with the addition of Station S2 (Howard Rd 345kV) and conductor upgrades | Calaveras - Skyline (N5_P4_2) | LN | 345 | 17/12, 22/3, 22/4, 22/5 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, DCKT Hill Country to Marion 345 kV, HILL COUNTRY to CAGNON 345 kV, CAGNON to BRAUNIG 345 kV | Pawnee Switching Station - Calaveras 345 kV, Pawnee Switching Station Auto XF1 345/138 kV, Skyline - Elmcreek 345 kV, Coleto Creek - Rosata Tap 138 kV, Cagnon - Calaveras 345 kV, Cagnon Auto XFMR4L-H 345/138 kV | RT | Planned |  |  |  |  | CALAVERS | SKYLINE | N5_P4_2 | SSKYCAL5
AEP |  |  |  | Campwood - … - Rock Springs | LN | 69 | 21/9, 24/1 | Bandera Auto AT3 138/69 kV , DBCKT Big Hill - Kendall 345 kV | Bandera Auto AT2 138/69 kV, Friess Ranch - Rocksprings 69 kV | RT | Forced, Planned |  |  |  |  | NEWBARKS | CAMPWOOD | CAMPWO_NEWBAR1 | SCAMROC9
ONCOR |  |  |  | Carmichael Bend Switch - Mitchell Bend Switch | LN | 345 | 23/3 | Benbrook Switch - Parker Switch (6042) 345 kV | Benbrook Switch - Parker Switch (6005) 345 kV | RT | Planned |  |  |  |  | MBDSW | CMBSW | 6017 | SMBDCMB5
AEP |  |  |  | Carrizo Springs - Crystal City | LN | 69 | 20/10 | Asherton-Bevo 138 kV | Bevo - Brundage Sub 69 kV | RT | Planned | Y, N |  |  |  | CARRIZO | CRYSTAL | CARRIZ_CRYSTA11 | SCARCRY9
ONCOR, TNMP |  |  |  | Carrollton Northwest - Lakepointe Tnp | LN | 138 | 22/12, 23/4 | DCKT Carrollton Northwest to Lewisville Switch 345 kV | South Tnp - Ti TNP 138 kV | RT | Planned |  |  |  |  | CRLNW | LKPNT | 591_A | SLKPCRL8
BRAZOS, ONCOR |  |  |  | Carrollton Northwest - Lewisville Switch (105_A) | LN | 345 | 2018 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | ADD | [5 empty] | CRLNW | LWSSW | 105_A | SLWSCRL5
BRAZOS, ONCOR |  |  |  | Carrollton Northwest - Lewisville Switch (83) | LN | 345 | 17/3 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned |  |  |  |  | CRLNW | LWSSW | 83 | SKRWCR25
AEP |  |  |  | Carver - Live Oak Aep | LN | 138 | 23/2 | DCKT Twin Buttes-DivideSwitchyard 345 kV | Hargrove - Twin Buttes 138 kV | RT | Forced |  |  |  |  | LVOK | CARVER | CARVER_LVOK1 | SCARLVO8
ONCOR |  |  |  | Cash Switch -…- Sulphur Springs Switch | LN | 345 | 25/4 | DCKT Farmersville Switch - Cyclone Switch & Farmersville Switch - Saltillo Switch 345kV | Sulfur Springs Switch - Liberty Pod 138kV | RT | Planned |  |  |  |  | SSPSW | CSHSW | 214_A | MSSPSDY5
AEP |  |  |  | Cassava - … - San Angelo Mathis Field | LN | 69 | 23/10, 23/12, 24/12 | Carver - Friend Ranch 138 kV, Bakersfield - Cedar Canyon 345 kV, Twin Buttes - Hargrove 138kV | Atlantic Sonora - Sonora 69 kV, San Angelo Concho - San Angelo Lake Nasworthy 69 kV, Lake Nasworthy - San Angelo Mathis Field 69kV | RT | Forced |  |  |  |  | CASSAVA | MERR | CASSAV_MERR1 | SPHBBGL9
LCRA |  |  |  | Castle Mountain - Crane Lcra | LN | 138 | 22/5, 22/7 | DCKT LCRA Crane - King Mountain West Tap & AND Castillo 138 kV, LCRA Crane - Castiollo 138 kV | Rio Pecos - LCRA crane Lcra 138 kV | RT | Planned |  |  |  |  | LCRANE | CASTMO | 716T716 | SLC2CAS8
CNPE |  |  |  | Cedar Bayou Plant - … - Quanum | LN | 138 | 24/3 | DCKT Boggy - Derick & South Channel 138 kV | Baytown - Miller 138 kV | RT | Planned |  |  |  |  | CBY | WKR | CBYWKR85 | SQNMCB28
CNPE |  |  |  | Cedar Bayou Plant - Center | LN | 345 | 22/3, 24/12, 25/2 | Jordan - King & Jordan - North Belt 345 kV, North Belt - Th Wharton 345 kV, DCKT North Belt - Jorr & Jorr - King, Wa Parish To Obrien OB_WAP99 345kV | Jefferson - South Channel 138 kV, Highlands - Power Systems Arco Cogen 138kV, Wa Parish - Obrien 345kV | RT | Planned |  |  |  |  | CTR | CBY | CBYCTR97A | SCBYCTR5
ONCOR | MODIFY | ONCOR | Contingency should be changed from "DCKT Cedar Hill Switch - Mountain Creek Ses 345 kV" to "DCKT Cedar Hill Switch - Mountain Creek Ses 138 kV" | Cedar Crest Switch - ... - Mountain Creek Ses (3150) | LN | 138 | 23/9 | DCKT Cedar Hill Switch - Mountain Creek Ses 138 kV | Cedar Crest Switch - Oak Cliff South 138 kV | RT | Forced |  |  |  |  | PLKTM | HMTRD | 3150_D | SPLKMCS8
ONCOR | MODIFY | ONCOR | Contingency should be changed from "Krum West Switch - Lewisville Switch 345 kV & Lewisville Switch - Roanoke Switch 345 kV" to "Dunham Switch - Krum West Switch & Roanoke Switch 345 kV" | Cedar Elm Switch - Krum West Switch | LN | 345 | 22/4 | Dunham Switch - Krum West Switch & Roanoke Switch 345 kV | Argyle - Highlands Tnp 138 kV | RT | Planned |  |  |  |  | KRWSW | CDESW | 38020 | SANAKR25
ONCOR | MODIFY | ONCOR | Contingency should be changed from "DCKT Liggett Switch - Venus Switch 345 kV" to "DCKT Liggett Switch - Venus Switch & Endeavor Switch 345 kV | Cedar Hill Switch - … - Timberview Switch (6020) | LN | 345 | 23/8 | DCKT Liggett Switch - Venus Switch & Endeavor Switch 345 kV | Cedar Hill Switch - Webb Sub 345 kV | RT | Planned |  |  |  |  | CRTLD | TVWSW | 6020_B | STVWCRT5
ONCOR |  |  |  | Cedar Hill Switch - Courtland | LN | 345 | 18/5, 18/9, 19/10 | DCKT Venus Switch to Timberview Switch & Everman Switch 345 KV | Cedar Hill Switch - Fish Crek Switch (3180) 138 kV | RT | Forced, Planned |  |  |  |  | CRTLD | CDHSW | 6020_A | STVWCRT5
AEP |  |  |  | Celanese Bishop - Kleberg AEP | LN | 138 | 23/11, 24/1, 25/1 | DCKT Lon Hill - Bunsen & Wil Tract 138 kV, Lon Hill - Nelson Sharpe 345 Kv, Lon Hill - Robstown Tap 69kV | Calallen Sub - Lon Hill 69 kV, Nelson Sharpe Auto XF1 345/138 kV | RT | Planned |  |  |  |  | CELANEBI | KLEBERG | CELANE_KLEBER1 | SCELKLE8
CNPE |  |  |  | Center - Cedar Bayou Plant | LN | 345 | 25/11, 25/12 | DCKT Jordan - King 345KV & Jordan - North Belt 345KV | Channelview - Lynch 138KV | RT | Planned |  |  |  |  | CTR | CBY | CBYCTR97 | SCBYCTR5
CNPE |  |  |  | Center - PH Robinson | LN | 345 | 23/11, 23/12 | DCKT Cedar Bayou Plant - Jordan & Chambers - Jordan 345 kV | Cedar Bayou Plant Auto AT3 345/138 kV | RT | Forced |  |  |  |  | CTR | PHR | CTRPHR97 | SPHRCTR5
GAR |  |  |  | Centerville - Mccree | LN | 138 | 25/9 | Mccree - Shiloh 138KV | Brand - College 138KV | RT | Planned |  |  |  |  | CENTRVIL | MCCREE | CNT_MCCR | SCENMCC8
ONCOR |  |  |  | Centerville Road Switch - … - Judd Court & Kirkland Park | LN | 138 | 19/3, 19/9 | DCKT Centerville Road Switch to Parkdale Switch 138 kV | Prairie Creek - Scyene Road 138 kV | RT | Planned |  |  |  |  | CNRSW | GRLRD | 3250_A, 3250_I | SLKHCNR8
ONCOR |  |  |  | Centerville Road Switch - Forney Switch | LN | 345 | 2017 | DCKT Forney Switch - Royse Switch 345 kV | Forney Switch 345/138 kV Auto MR3 | ADD | [5 empty] | CNRSW | FORSW | 110 | SCNRFOR5
ONCOR | REMOVE | ONCOR | Remove this MTE due to Oncor completing the Centerville Road Switch - Lake Hubbard Ses 138 kV line upgrade project | Centerville Road Switch - Lake Hubbard Ses (3681) | LN | 138 | 23/11 | DCKT Lake Hubbard Ses - … - Prairie Creek Switch 138 kV | Centerville Road Switch - Lake Hubbard Ses 138 kV (3671) | RT | Forced |  |  |  |  | CNRSW | LHSES | 3681 | SLHSCNR8
CNPE |  |  |  | Chanel - Deepwater | LN | 138 | 21/11 | Eastside - Gable Stree 138 kV | Downtown - Polk 138 kV | RT | Planned |  |  |  |  | DPW | CHL | CHLDPW70A | SCHLDPW8
LCRA | REMOVE | LCRA | All the overloaded elements in column G have been upgraded | Chief Brady - Georgetown | LN | 138 | 25/2 | Georgetown South -…- Georgetown East 138kV, Hutto Switch -…- Georgetown Switch 138kV, Bell County - Temple Switch 138kV, DCKT Temple Switch - Knob Creek Switch 345 kV & Temple Switch - Bell County 138kV | Bell County - Salado Switch 138kV, Salado South - Salado Switch 138kV, Georgetown South - Midnight Sub 138kV | RT | Planned |  |  |  |  | CHIEBR | GEORGE | 221T355 | SCHIGEO8
LCRA | REMOVE | LCRA | The overloaded elements in column G have been upgraded | Chief Brady - Round Rock | LN | 138 | 24/6 | Bell County - Temple Switch 138kV, DCKT Temple Switch - Knob Creek Switch 345 kV & Temple Switch - Bell County 138kV, DCKT Round Rock -...- Georgetown South 138kV, DCKT Salado Switch To Knob Creek Switch 345kV And Temple Switch To Bell County 138kV | Georgetown South - Round Rock Westinghouse 138kV, Bell County - Salado Switch 138kV | RT | Forced |  |  |  |  | RNDRK | CHIEBR | 213T378 | SCHIRND8
ONCOR |  |  |  | China Grove Switch - Snyder | LN | 138 | 19/5, 24/9 | DCKT Dermott Switch - Bluff Creek Switch & Ennis Creek Switch 138 kV, | Ranger Camp Switch - Sun Switch 138 kV, Snyder Auto FMR1 138/69 kV | RT | Planned |  |  |  |  | CGRSW | SNYDR | 6235 | SSNYCGR8
STEC |  |  |  | Choate_station - Four Corners Sub | LN | 138 | 24/12 | Manual Stp To Hlj & Anstrom345 Kv Double | Blessing Auto 1382 345/138kV | RT | Planned |  |  |  |  | FORCRNS | CHOATE | CHOATE_FORCRNS | SFORPAW8
LCRA |  |  |  | Citgo N Oak Park - Nueces Bay | LN | 138 | 25/5 | DCKT Nueces Bay - Saxet 138KV & Lon Hill - Saxet 138KV | Morris Street - Nueces Bay 138KV | RT | Planned |  |  |  |  | CITGO_NO | NUECES_B | 434T434 | SCITNUE8
AEP, ONCOR |  |  |  | Clear Crossing - ... - Willow Creek Switch | LN | 345 | 21/11 | DBCKT Edith Clarke - Riley 345 kV, Abilene Mulberry Creek - Sweetwater East Switch 345 kV & Long Creek - Sweetwater East Switch 345 kV | Abilene Mulberry Creek - Long Creek 345 kV, Abilene Mulberry Creek - Bluff Creek 345 kV | RT | Planned |  |  |  |  | CLEARCRO | TOMSW | 35150 | SCLEWC25
AEP, ONCOR |  |  |  | Clear Crossing - … - Dermott Switch (CLEARC_KIRCHH1) | LN | 345 | 18/4, 18/5, 18/6, 18/7, 18/8, 18/9, 18/11, 18/12 | DCKT Dermott Sw to Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned |  |  |  |  | CLEARCRO | KIRCHHOF | CLEARC_KIRCHH1 | SKIRDMT5
AEP, ONCOR |  |  |  | Clear Crossing - … - Dermott Switch (CLEARC_KIRCHH2) | LN | 345 | 18/4, 18/5 | DCKT Dermott Switch to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned |  |  |  |  | CLEARCRO | KIRCHHOF | CLEARC_KIRCHH2 | SKIRDM35
AEP |  |  |  | Clear Crossing - … - Edith Clarke (CLEARC_GAUSS2) | LN | 345 | 17/7, 17/8, 17/9 | Basecase | Panhandle GTC | RT | Planned |  |  |  |  | CLEARCRO | GAUSS | CLEARC_GAUSS2 | SGAUED35
ONCOR | REMOVE | ONCOR | Oncor's LODF analysis showed marginal impact on the constraint due to this MTE. This MTE does not appear to be linked to the contingency/constraint and can be removed. | Clear Crossing - QUASAR | LN | 345 | 25/12, 26/1, 26/3 | DCKT Dermott Switch - Scurry County South Switch 345kV | Knapp - Scurry Chevron 138kV | RT | Planned |  |  |  |  | QUASAR | CLEARCRO | CLEARC_QUASAR2 | SCLEQUA5
AEP |  |  |  | Clear Crossing - West Shackelford (CLEARC_WSHACK1) | LN | 345 | 19/1, 19/2, 19/3, 21/9 | DCKT Dermott Switch - Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned |  |  |  |  | CLEARCRO | WSHACK | CLEARC_WSHACK1 | SCLEWS15
AEP |  |  |  | Clear Crossing - West Shackelford (CLEARC_WSHACK2) | LN | 345 | 19/1, 19/2, 19/3 | DCKT Dermott Switch - Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned |  |  |  |  | CLEARCRO | WSHACK | CLEARC_WSHACK2 | SCLEWS25
AEP |  |  |  | Coleto Creek - Victoria | LN | 138 | 25/12 | Coleto Creek - Pawnee Switching Station 345KV | Coleto Creek - Victoria 138KV | RT | Planned |  |  |  |  | COLETO | VICTORIA | COLETO_VICTOR2 | SVICCOL8
LCRA | REMOVE | LCRA | Reconfiguration of Henne makes congestion unlikely | Comal - Henne | LN | 138 | 25/10 | Bergheim AT1H_H AT1L_H 138/345KV | Comal - Henne 138KV | RT | Planned |  |  |  |  | COMAL | HENNE | 88T234 | SHENCO28
ONCOR |  |  |  | Comanche Peak Ses - Comanche Switch | LN | 345 | 18/11, 21/4, 22/4 | DCKT Killeen Switch - Buckhorn Switch & Russell Gap Switch 345 kV | Comanche Tap - Comanche Switch 138 kV | RT | Forced, Planned |  |  |  |  | CMNSW | CPSES | 662 | SCMNCPS5
ONCOR |  |  |  | Comanche Peak Ses - Mitchell Bend Switch | LN | 345 | 20/3 | DCKT Comanche Peak SES - Timberview Switch & Johnson Switch 345 kV | Comanche Peak SES - Wolf Hollow 345 Switch 345 kV, Mitchell Bend Switch - Wolf Hollow 345 Switch 345 kV | RT | Planned |  |  |  |  | CPSES | MBDSW | 6033 | SDCSCPS5
ONCOR | MODIFY | ONCOR | MTE should be changed from "Consavvy Switch - Morgan Creek Ses" to "Consavvy Switch - … - Morgan Creek Ses". Overload should be changed from "Longshore Switch - Consavvy Switch 345kV" to "Longshore Switch - Prairieland Switch 345kV" | Consavvy Switch - … - Morgan Creek Ses | LN | 345 | 24/6, 24/11, 25/3 | Wett_long_draw To Volta Lin 1, DCKT Bakersfield - Cedar Canyon 345kV, | Longshore Switch - Prairieland Switch 345kV | RT | Planned |  |  |  |  | MGSES | CONSW | 6053 | SCONMGS5
LPL |  |  |  | Coop Substatoin - Slaton Sub | LN | 138 | 23/9, 23/10 | Double Mountain Switch - Fiddlewood Switch 345 kV | Dunbar Sub - Holly Sub 138 kV | RT | Planned |  |  |  |  | LPLCO | LPLSL | LPLCO_LPLSL | SL11LPL0
STEC |  |  |  | Cotulla Sub - … - Freer Sub | LN | 69 | 22/1 | Fowlerton - Lobo 345 kV | Bruni Sub Auto 138/69 kV | RT | Planned |  |  |  |  | COTULAS | HOLANDS | COT_HOLA | SFREBRU9
LCRA |  |  |  | Crane Lcra - King Mountain West Tap | LN | 138 | 22/5 | Crane LCRA - Castillo 138 kV | Rio Pecos - LCRA Crane 138 kV | RT | Planned |  |  |  |  | LCRANE | KINGMO | 664T664 | SLCRKIN8
CNPE |  |  |  | Crown -Jefferson | LN | 138 | 23/3 | PAIR to BOGGY 138 kV | Conial - Philip 138 kV | RT | Planned |  |  |  |  | JFS | CRN | CRNJFS94 | SCRNJFS8
LCRA |  |  |  | Cypress Creek - Raymond F Barker | LN | 138 | 25/4 | Cagnon - Kendall 345kV & Cico - Comfort 138kV | Raymond F Barker - Comfort 138kV | RT | Planned |  |  |  |  | RAYBAR | CYPRCR | 662T662 | SCYPCOM8
CNPE |  |  |  | Deepwater - Greens Bayou | LN | 345 | 25/9 | Greens Bayou - Sheldon 345KV | Greens Bayou - Lydell 138KV | ST | Forced |  |  |  |  | DPW | GBY | DPWGBY69 | SGBYDPW5
AEP |  |  |  | Dermott Switch - … - Figaro | LN | 345 | 21/10 | DBCKT Dermott Switch - Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned |  |  |  |  | DMTSW | FIGARO | DMTSW_FIGARO1 | SFIGDMT5
ONCOR, WETT |  |  |  | Dermott Switch - Mhos (T-301) | LN | 345 | 22/5, 22/9, 22/10 | Double Mountain Switch - Fiddlewood Switch 345 kV, Blackwater Draw Switch - Double Mountain Switch 345 kV | Holly Substation - Dunbar Substation 115 kV, MacKenzie Substation - Northeastern Substation 115 kV | RT | Forced |  |  |  |  | MHOS | DMTSW | T-301 | SDMTW_15
ONCOR, WETT |  |  |  | Dermott Switch - Mhos (T-302) | LN | 345 | 22/5, 22/9, 22/10 | Double Mountain Switch - Fiddlewood Switch 345 kV, Blackwater Draw Switch - Double Mountain Switch 345 kV | Holly Substation - Dunbar Substation 115 kV, MacKenzie Substation - Northeastern Substation 115 kV | RT | Forced |  |  |  |  | MHOS | DMTSW | T-302 | SDMTW_25
ONCOR |  |  |  | Dermott Switch - Scurry County South Switch (34540) | LN | 345 | 20/11 | DCKT Clear Crossing-…-Figaro & Clear Crossing-…-Dermott Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | N |  |  |  | DMTSW | SCOSW | 34540_A | SDMTSC15
ONCOR |  |  |  | Dermott Switch - Scurry County South Switch (34550) | LN | 345 | 20/11 | DCKT Clear Crossing-…-Figaro & Clear Crossing-…-Dermott Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | N |  |  |  | DMTSW | SCOSW | 34550_A | SDMTSC25
BRAZOS, ONCOR |  |  |  | Desoto Switch -…- Sterrett | LN | 138 | 22/12 | JOHNSON SWITCH (ONCOR) to CONCORD 345 kV, ENNIS WEST SWITCH - ENNIS TRACTEBEL 138 kV, DCKT Kemp Ranch Switch - Sardis & Soap Creek Switch -Cedar Hill Tu 138 kV | Midlothian Txi -…- Midlothian South 138 kV, Wilmer Auto FMR1 138/69 Kv | RT | Planned |  |  |  |  | DESSW | GLNHT | 945_A | SGLNDES8
TNMP |  |  |  | Dickinson Tnp - Freeway Park Tnp | LN | 138 | 23/5 | Hastings Tnp - North Alvin Tnp 138 kV | Dickinson Tnp - Freeway Park Tnp 138 kV | RT | Planned |  |  |  |  | DICKNSON | FRWYPARK | G138_14 | SDICFR28
TNMP |  |  |  | Dickinson Tnp - League City Tnp | LN | 138 | 20/10, 24/10 | North Alvin TNP-Hastings Tnp 138 kV | League City Tnp - Hidden Lakes Tnp 138 kV | RT | Planned | N |  |  |  | DICKNSON | LEAGCITY | G138_091 | SLEADIC8
GEUS, TMPA |  |  |  | Diesel - Greenville Steam | LN | 69 | 15/7 | Shelby Auto BT1 138/69 kV | Greenville Steam Auto XT1 138/69 kV | ST | Planned |  |  |  |  | DIESEL | GN_S_I | DIE_GNS | SDIEGN_9
AEP |  |  |  | Dolan Tap - Whiting | LN | 138 | 21/10 | Odlaw Switch -…- Uvalde AEP 138 kV | Hamilton Road - Maverick 138 kV | RT | Planned |  |  |  |  | DOLAN | WHITING | DOLAN_WHITIN1 | SCT2CAR8
ONCOR |  |  |  | Double Mountain Switch - Fiddlewood Switch | LN | 345 | 24/5 | Dunbar Substation - Wadsworth Susbsation 115kV | Dunbar Substation - Holly Substation 115kV | RT | Planned |  |  |  |  | FIDSW | DBMSW | ONCFW_ONCDM | SDBMFID5
CNPE |  |  |  | Dow Chemical - Oasis (DOWOAS18) | LN | 345 | 21/4, 22/4, 22/9, 24/5, 24/6, 24/9, 25/4 | DCKT Jones Creek-South Texas Project & Refuge 345 kV, Wa Parish - Waley & Wa Parish - Wolf 345kV | South Texas Project - WA Parish 345 kV, Bay City Sub - Sargent Sub 69 kV, Oasis - Dow Chemical 345kV | RT | Forced, Planned | N |  |  |  | OAS | DOW | DOWOAS18A | SOASDO25
STEC |  |  |  | Driscoll Sub - … - Loyola Sub | LN | 69 | 20/4 | Ajo-Nelson Sharpe 138 kV | Falfurrias - Premont 69 kV | RT | Planned | N |  |  |  | DRSCOLS | RICRDOS | DRS_RICR | SRICLOY9
LPL |  |  |  | Dunbar Sub - Holly Sub | LN | 115 | 24/2 | Double Mountain Switch - Fiddlewood Switch 345 kV | Dunbar Sub - Wadsworth Sub 115 kV | RT | Planned |  |  |  |  | LPLDB | LPLHY | LPLHY_LPLDB | SL13LPL0
LCRA | REMOVE | LCRA | T361 Parkway-Schertz has been dynamically rated and so congestion is not likely | E C Mornhinweg - Parkway | LN | 138 | 25/8 | DCKT Hill Country - Marion 345KV | Parkway - Schertz 138KV | RT | Planned |  |  |  |  | ECMORN | PARKWA | 581T581 | SECMPAR8
ONCOR | MODIFY | ONCOR | Contingency should be changed from "DCKT Seagoville Switch - Forney Switch & Tri Corner 345kV" to "DCKT Seagoville Switch - Tyler Grande & Forney 345 kV" | Eastside Filt Pump South - Mesquite East | LN | 138 | 25/9 | DCKT Seagoville Switch - Tyler Grande & Forney 345 kV | Crandall - Crandoll POI 138kV | ST | Forced |  |  |  |  | MESQE | EFTPS | 1400_F | SBSPSGV8
AEP |  |  |  | Edith Clarke - Riley (Edithc_Riley1) | LN | 345 | 17/10, 17/11, 17/12, 18/1, 18/2, 18/3 | Basecase | Panhandle GTC | RT | Planned |  |  |  |  | EDITHCLA | RILEY | EDITHC_RILEY1 | SRILED15
AEP |  |  |  | Edith Clarke - Riley (Edithc_Riley2) | LN | 345 | 17/10, 17/11, 17/12, 18/1, 18/2, 18/3 | Basecase | Panhandle GTC | RT | Planned |  |  |  |  | EDITHCLA | RILEY | EDITHC_RILEY2 | SRILED25
AEP, WET |  |  |  | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC3) | LN | 345 | 16/11, 16/12, 17/1, 17/2, 17/3, 17/4, 17/5, 17/6 | Basecase | Panhandle GTC | RT, ST | Forced, Planned |  |  |  |  | EDITHCLA | W_CW_345 | COTTON_EDITHC3 | SW_CED55
AEP, WET |  |  |  | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC4) | LN | 345 | 16/11, 16/12, 17/1, 17/2, 17/3, 17/4, 17/5, 17/6 | Basecase | Panhandle GTC | RT, ST | Forced, Planned |  |  |  |  | EDITHCLA | W_CW_345 | COTTON_EDITHC4 | SW_CED45
AEP, LCRA |  |  |  | El Campo - Ricebird | LN | 138 | 23/3 | DCKT Vanderbilt Switching Station - Energy Transfer Partners 138kV & EL Toro Switching Station - Edna Substation 69kV | Danevang Switching Station Auto 138_69 138/69 kV | RT | Planned |  |  |  |  | RICEBI | EL_CAMPO | 589T589 | SRICEL_8
ONCOR | MODIFY | ONCOR | MTE should be changed from "Elkton - Martin Lake Ses" to "Elkton - … - Martin Lake SES" Contingency should be changed from "Martin Lake - Styker and - Enterprise DCKT" to "Martin Lake SES - Stryker Creek SES & Mt Enterprise 345kV" | Elkton - … - Martin Lake SES | LN | 345 | 2017 | Martin Lake - Styker and - Enterprise DCKT | Martin Lake SES - Stryker Creek SES & Mt Enterprise 345kV | ADD | [5 empty] | ELKTN | MLSES | 180 | SELKMLS5
ONCOR |  |  |  | Elkton - Tri Corner | LN | 345 | 17/11, 18/11, 18/12, 2017 | DCKT Trinidad Ses- Mt Enterprise & Stryker Creek Ses, DCKT Martin Lake Ses - Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV Auto MR3, Lufkin Switch - Nacogdoches South Tap 138 kV | ADD, RT | Planned |  |  |  |  | ELKTN | TRCNR | 170 | SELKFOR5
CNPE, CPS |  |  |  | Elmcreek - South Texas Project | LN | 345 | 22/4 | Elmcreek - South Texas Project 345 kV & South Texas Project - WA Parish 345 kV | Hillje - South Texas Project 345 kV | RT | Planned |  |  |  |  | STP | ELMCREEK | STPELM271 | SELMSTP5
GAR |  |  |  | Elmgrove - Wylie Switch | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned |  |  |  |  | ELMGROVE | WYLIESW | WYL_ELMG | SWYLELM8
LCRA |  |  |  | Engle -…- Schulenburg | LN | 138 | 22/5 | Joslin - Formasa 138 kV | Lolita - Victoria 138 kV | RT | Planned |  |  |  |  | ENGLE | FLATON | 145T112 | SENGFLA8
ONCOR |  |  |  | Ennis West Switch - Ennis South (941_C) | LN | 138 | 19/4 | WXHCH-WXOCF_69kV & ENWSW-STERT_138kV | ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (943) | ADD | Planned |  |  |  |  | ENWSW | ENSSO | 941_C | SENSENW8
ONCOR |  |  |  | ENNIS WEST SWITCH -...- SHANKLE SWITCH (941) | LN | 138 | 19/6 | ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (943) | Ennis West Switch- Wahaxhachie - Sterrett | ADD | Planned |  |  |  |  | ENWSW | SHKSW | 941 | SENWSHK8
ONCOR |  |  |  | Ennis West Switch -…- Sterrett (940) | LN | 138 | 18/11 | ENNIS WEST SWITCH -...- SHANKLE SWITCH 138 kV (941) | ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (943) | ADD | Planned |  |  |  |  | ENWSW | TMPTN | 940_A | SMGIENW8
ONCOR |  |  |  | Eskota Switch - … - Ranger Camp Switch (6285) | LN | 345 | 23/11 | McElmurray - … - Moore 138 kV | Capella - Merkel 69 kV, Eskota Switch - Trent 69 kV | RT | Planned |  |  |  |  | LSPOI | MGSES | 6285_B | SSWDMGS8
AEP |  |  |  | Esperanza - Stp Switch | LN | 138 | 24/1 | Arroz - El Campo 138 kV | Blessing - Pavlov 138 kV | RT | Planned |  |  |  |  | ESPERANZ | STPSW | ESPERA_STPSW1 | SSTPESP8
ONCOR |  |  |  | Everman Switch - Oakhill Tap 1 | LN | 138 | 21/12, 22/2 | Davis -…-Everman Switch 138 kV, DBCKT Deen Switch -…- Hicks Switch 138 kV | Hemphill - Mistletoe Heights 138 kV | RT | Forced, Planned |  |  |  |  | EVRSW | OAKT1 | 6310_A | SOAKEVR8
ONCOR |  |  |  | Exchange Switch - Roanoke Switch (109) | LN | 345 | 24/10, 24/11 | DCKT Krum West Switch - West Denton & Lewisville Switch 345 kV, Krum West Switch - Bird Dog Switch 345kV | Roanoke Switch - Exchange Switch 345 kV (108) | RT | Planned |  |  |  |  | RNKSW | EXCSW | 109 | SRNKEXC5
ONCOR, WETT |  |  |  | Farmland - Wett_long_draw | LN | 345 | 24/8 | Blackwater Draw Switch - Double Mountain Switch 345kV | MacKenzie Substation - Northeast Substation 115 kV | RT | Planned |  |  |  |  | FARMLAND | W_LD_345 | FARMLAND_LONGD | SW_LFAR5
LCRA | REMOVE | LCRA | New Fayetteville auto has a higher emergency rating of 826 MVA compared to 739 MVA previously | Fayette Plant 3 - Lytton Springs | LN | 345 | 23/2, 25/11, 25/12 | DCKT Fayette Plant 1 and 2 - Lostpine & Winches 345kV | Fayetteville Auto AT2H 345/138 kV | RT | Planned |  |  |  |  | FPPYD2 | LYTTON_S | 355T255 | SFPPLYT5
ONCOR |  |  |  | Forney Switch - Royse Switch (200) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney Switch 345/138 kV Auto MR3 | ADD | [5 empty] | FORSW | RYSSW | 200 | SFORRYS5
ONCOR |  |  |  | Forney Switch - Royse Switch (210) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney Switch 345/138 kV Auto MR3 | ADD | [5 empty] | FORSW | RYSSW | 210 | SFORRY25
AEP |  |  |  | Fort Mason - Yellow Jacket | LN | 138 | 22/11 | DCKT Bighill -Kendall 345kV | Yello Jacket - Hext LCRA 138 kV | RT | Forced |  |  |  |  | YELWJCKT | FORTMA | FORTMA_YELWJC1 | SFORYEL8
STEC |  |  |  | Fowlerton - San Miguel Gen (FOWRTN_SMIGL) | LN | 345 | 21/2, 24/2, 25/3 | DCKT North Edinburg - Pomelo 345 kV, DCKT Dilley Switch - San Miguel Switch & Dilley Switch - Cotulla Sub 138 kV, DCKT Fowlerton To Avanzada & Lobo To Fowlerton 345kV | Freer - Lobo 69 kV, Dilley Switch Aep - Cotulla Sub 69 Kv, Laredo Vft North - Las Cruces 138kV, North Laredo Switch - Mines Road 138kV | RT | Forced, Planned |  |  |  |  | FOWLRTON | SANMIGL | FOWRTN_SMIGL | SSANFOW5
TNMP |  |  |  | Freeway Park Tnp - Mainland Tnp | LN | 138 | 21/2, 22/3, 22/4 | Meadow - Ph Robinson 345 kV, PH Robinson-Gaf Tnp 138 kV | Magnolia Tnp - Seminole Tnp 138 kV, Freeway Park Tnp - Dickinson Tnp 138 kV | RT | Planned | N |  |  |  | MAINLAND | FRWYPARK | 138_FWP_MNL1 | SFRWMAI8
LCRA |  |  |  | Friend Ranch - Fort Lancaster | LN | 138 | 24/9 | DCKT Bakersfield - Cedar Canyon 345kv | Crossover - Palouse 138kV | RT | Planned |  |  |  |  | FRIEND_R | FTLN | 438T438 | SFRIFTL8
TNMP |  |  |  | Friendswood TNP - Seminole Tnp | LN | 138 | 23/10 | Meadow - PH Robinson 345 kV | Alvin Tnp - North Alvin Tnp 138 kV | RT | Planned |  |  |  |  | FRDSWOOD | SEMINOLE | G138_10C | SFRDSEM8
ONCOR | REMOVE | ONCOR | Oncor's LODF analysis showed marginal impact on the constraint due to this MTE. This MTE does not appear to be linked to the contingency/constraint and can be removed. Also, Fryers Creek - Temple 138 kV Line is radial therefore cannot affect loading on Seaton 138/69 kV Auto | Fryers Creek - Temple | LN | 138 | 25/9 | DCKT Temple Switch - Fryers Creek 138kV & Salado Switch - Knob Creek Switch 345kV | SEAAT1 138/345KV | RT | Planned |  |  |  |  | FRYSW | TMPLE | 1840_C | STMPFRY8
ONCOR | MODIFY | ONCOR | Contingency should be changed from "Chief Brady -…- Spanish Oak 138kV" to "DCKT Round Rock - Chief Brady & Spanish Oak 138 kV" | Fryers Creek - Temple Switch | LN | 138 | 25/8 | DCKT Round Rock - Chief Brady & Spanish Oak 138 kV | Georgetown South - Round Rock Westinghouse 138kV | RT | Planned |  |  |  |  | TMPSW | FRYSW | 1715_B | SFRYTMP8
STEC |  |  |  | Furhman - Sam Rayburn Switchyd | LN | 138 | 26/4 | DCKT Elmcreek - South Texas Project 345kV | Vanderbilt 69 Sub - Placedo Sub 69kV | RT | Planned |  |  |  |  | RAYBURN | FURHMAN | RAYBUR_FURHMAN | SFURRAY8
ONCOR |  |  |  | Garland - Rowlett Tap | LN | 138 | 24/8 | Walnut - Naaman 138kV | College - Jupiter 138kV | RT | Planned |  |  |  |  | RWLTP | GRLND | 1630_H | SFSTRYS8
CNPE |  |  |  | Garrott - Kirby | LN | 138 | 21/11 | Eastside - Gable Stree 138 kV | Downtown - Polk 138 kV | RT | Planned |  |  |  |  | GT | KB | GT_KB_37A | SGTKB8
AEP | REMOVE | AEP | Upgrades to the area | Gateway - Gateway East Tap | LN | 138 | 25/8, 25/9 | DCKT Avanzada - Fowlrton 345KV & Avanzada - Lobo 345KV | Las Cruces - Milo 138KV | RT | Planned |  |  |  |  | GATE_WAY | GATEETP | GATEET_GATE_W1 | SGATW028
CNPE, CROSS, GAR, TMPA |  |  |  | Gibbons Creek - Limestone Plant (GIB_LIME181) | LN | 345 | 21/3, 23/5 | DCKT Twin Oak Switch - Gibbons Creek & Jack Creek 345 kV, DCKT Jewett-Singleton 345 kV | Jewett - Singleton 345 kV, Gibbons Creek - Twin Oak Switch 345 kV | RT | Planned | N |  |  |  | GIBCRK | LEG | GIB_LIME181 | SLE2GIB5
CNPE, CROSS, GAR, TMPA | REMOVE | CROSS | Yellow Wolf (YLW_WOLF) substation cut into GIB_LIME50, splitting the original GIBCRK–LEG circuit into two segments. CTT requests removal until congestion is identified under the new configuration. | Gibbons Creek - Limestone Plant (GIB_LIME501) | LN | 345 | 21/3, 23/5, 25/3 | DCKT Twin Oak Switch - Gibbons Creek & Jack Creek 345 kV, DCKT Jewett-Singleton 345 kV | Jewett - Singleton 345 kV, Gibbons Creek - Twin Oak Switch 345 kV | RT | Planned | N |  |  |  | GIBCRK | LEG | GIB_LIME501 | SLEGGIB5
CNPE, TMPA |  |  |  | Gibbons Creek - Singleton | LN | 345 | 25/5 | Singleton - Jewett (240) 345kV | Jewett - Singleton 345kV (260_A) | ST | Forced |  |  |  |  | SNG | GIBCRK | SNGXGC75 | SGIBSNG5
TMPA |  |  |  | Gibbons Creek - Twin Oak Switch | LN | 345 | 20/5, 20/11 | DCKT GibbonsCreek-Limestone 345 kV, DCKT Jewett-Singleton 345 kV | Jewett - Singleton 345 kV | RT | Planned | N |  |  |  | GIBCRK | TOKSW | 256_A1 | SGIBTOK5
ONCOR |  |  |  | Golden Switch - Sun Switch | LN | 138 | 20/3 | DCKT Dermott Switch to Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Forced |  |  |  |  | GLDSW | SUNSW | 6438 | SGLDSUN8
ONCOR | MODIFY | ONCOR | MTE should be changed from "Graham SES - Tonkawa Switch" to Graham SES - … - Tonkawa Switch" | Graham SES - … - Tonkawa Switch | LN | 345 | 21/11 | Abilene Mulberry Creek - Sweetwater East Switch 345 kV & Long Creek - Sweetwater East Switch 345 kV | Abilene Mulberry Creek - Bluff Creek 345 kV | RT | Planned |  |  |  |  | GRSES | TKWSW | 6035_A | STKWGRS5
ONCOR |  |  |  | Graham SES - Rice Switch | LN | 138 | 22/4 | Windthorst Switch -…- Wichita Falls South Switch 138 kV | Cottonwood Road Switch - Olney Pod 69 kV | RT | Planned |  |  |  |  | GRSES | RICSW | 6560_A | SRICGRS8
CROSS |  |  |  | Gray - Railhead | LN | 345 | 16/3, 16/5 | Basecase, DCKT Alibates to Tule Canyon 345 kV | Panhandle GTC, Low Voltage in Panhandle area | RT, ST | Planned | Y |  |  |  | RAILHEAD | CTT_GRAY | RAILHD_GRAY | SRAICTT5
AEP, CROSS |  |  |  | Gray - Tesla (GRAY_TESLA_1) | LN | 345 | 17/1 | Basecase | Panhandle GTC | RT | Forced |  |  |  |  | CTT_GRAY | TESLA | GRAY_TESLA_1 | SCTTTES5
CROSS |  |  |  | Gray South Bus (CB GY_BKR_G130, etc.) | BUS | 345 | 16/5 | DCKT Alibates to Tule Canyon 345 kV | Low Voltage in Panhandle area | ST | Planned | Y |  |  |  | GTT_GRAY |  | 1002 | N/A
AEP |  |  |  | Gregory - Rincon | LN | 69 | 25/11 | Aransas Pass TRX 69A1 138/69 | Naval Base - North Padre 69KV | RT | Planned |  |  |  |  | GREGORY | RINCON | GREGOR_RINCON1 | SGRERIN9
ONCOR |  |  |  | Gresham Road Switch - … - Nacogdoches Se | LN | 138 | 17/12, 18/7, 18/8, 18/10, 18/12, 19/1 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Lufkin Switch - Nacogdoches South Tap 138 kV | RT | Planned |  |  |  |  | CSHNG | GRDSW | 1450_F | SNCDCMI8
LCRA |  |  |  | Hamilton Road - Pinto Creek | LN | 138 | 23/3, 23/4 | DCKT Bighill-Kendall 345kV | Hamilton Road - Maverick 138 kV, Escondido - Ganso 138 kV | RT | Planned |  |  |  |  | PINTCR | HAMILTON | 464T464 | SBRAHAM8
AEP, ETT | MODIFY | ONCOR | Change TDSP from "Oncor" to "Electric Transmission Texas" | Hamilton Road - Rgec Rough Canyon | LN | 138 | 25/5 | DCKT Big Hill -…- Omega 345kV | Carver - Tinsley Tap 138kV | RT | Planned |  |  |  |  | ROUGHCAN | HAMILTON | HAMILT_ROUGHC1 | SCOMHA38
ONCOR |  |  |  | Harker Heights -...- Nolanville | LN | 138 | 25/2, 25/3 | DCKT Salado Switch - Killeen Switch 345kV | Belton - Belton Southwest 138kV | RT | Planned |  |  |  |  | NLNVL | HKHTS | 640_N | SNLNHKH8
AEP |  |  |  | Harlingen Switch - Oleander | LN | 138 | 25/5, 25/6, 25/7, 25/12, 26/4 | South Santa Rosa - Primera & Rio Hondo 138kV & North Edinburg - Bonilla 345kV | Harlingen #1 - Harlingen Switch 69kV | RT | Planned |  |  |  |  | OLEANDER | HARLNSW | HARLNS_OLEAND1 | SHAIHAR8
ONCOR |  |  |  | Hawk Hollow Switch - … - Rivercrest Ses (1561) | LN | 138 | 23/8 | DCKT Hawk Hollow Switch - Paris Switch 138 kV | Tenaska (TXU) - Toco Switch 138 kV | RT | Planned |  |  |  |  | DRPEA | HWKSW | 1561_C | SHWKDPR8
ONCOR |  |  |  | Hawk Hollow Switch - … - Tenaska (TXU) (1560) | LN | 138 | 23/8 | DCKT Hawk Hollow Switch - Paris Switch 138 kV | Deport REA - Rivercrest Ses 138 kV | RT | Planned |  |  |  |  | PREST | RENTP | 1560_A | SHWLBL8
LCRA |  |  |  | Hays Energy Center - Zorn (388T3881) | LN | 345 | 2021 | DCKT Cagnon - Kendal 345kV & Cico - Comfor 138kV | Hays Energy Center - Zorn 345 kV (6T227) | ADD | [5 empty] | HAYSEN | ZORN | 388T3881 | SHAYZO25
LCRA |  |  |  | Hays Energy Center - Zorn (6T227) | LN | 345 | 2021 | DCKT Cagnon - Kendal 345kV & Cico - Comfor 138kV | Hays Energy Center - Zorn 345 kV (388T3881) | ADD | [5 empty] | HAYSEN | ZORN | 6T227 | SHAYZOR5
AEP |  |  |  | Hicks Switch - Roanoke Switch | LN | 345 | 24/9 | DCKT Krum West Switch - West Denton & Krum West Switch - Lewisville Switch 345kV | Alliance - Roanoke Switch 345kV | RT | Planned |  |  |  |  | RNKSW | HCKSW | 107 | SHCKEXC5
AEN |  |  |  | Hicross Aen - Slaughter Lane | LN | 138 | 26/1 | DCKT Bluff Springs - Lytton Springs 138KV & Lytton Springs - Turnersville 138KV | Barton - Vega 138KV | RT | Planned |  |  |  |  | HICROSS | SLAUGHTE | CKT_987 | SSLAHIC8
AEP |  |  |  | Hidalgo Energy Center - North Edinburg | LN | 138 | 25/4 | Mccoll Road - North Edinburg & North Edinburg - North Mcallen 138kV | North Edinburg - Hidalgo Energy Center 138kV | RT | Forced |  |  |  |  | NEDIN | HEC | HEC_NEDIN1 | SDUKNED8
ONCOR, TNMP |  |  |  | Highlands Tnp - Lewisville Switch | LN | 138 | 20/1, 20/2, 20/3, 20/12, 21/12 | Carrollton Northwest-Lakepoint Tnp 138 kV, DCKT Carrollton Northwest to Lewisville Switch 345 kV | South Tnp - Carrollton Northwest, Argyle - Highlands Tap 138 kV, TI Tnp - West Tnp 138 kV | RT | Planned |  |  |  |  | LWSSW | LWSVH | 593 | SLWSLWS8
CPS, LCRA |  |  |  | Hill Country - Marion | LN | 345 | 19/2, 23/2 | DCKT Elmcreek - Skyline 345 kV | Hill Country - Marion 345 kV | RT | Planned |  |  |  |  | MARION | HILLCTRY | HILL_MAR_1 | SMARHI25
ONCOR | MODIFY | ONCOR | Overload should be changed from "Haney Bepc - Navarro 138kV" to "Haney Bepc - Revolutation Switch 138kV" | Hillsboro - Whitney | LN | 138 | 24/10 | Bale Switch - Stranger Switch 345kV, Jewett - Stranger Switch 345kV | Haney Bepc - Revolutation Switch 138kV | RT | Forced |  |  |  |  | HLSBR | WHTNY | 1200 | SHLSWH28
LCRA |  |  |  | Hollmig - Kendall | LN | 138 | 24/10 | Kendall To Comfort Lin 1 | Kerrville Stadium - Kendal 138kV | RT | Forced |  |  |  |  | FREDER | HOLLMI | 73T120 | SCOMKEN8
AEP |  |  |  | Holly - Westside Aep | LN | 138 | 18/11, 22/05 | Airline Aep - … - Westside Aep 138 kV | Arcadia - Southside 138 kV | RT | Forced, Planned |  |  |  |  | HOLLY4 | WESTSIDE | HOLLY4_WESTSI1 | SHOLWES8
LPL |  |  |  | Holly Sub - Southeast Sub | LN | 115 | 23/11 | Double Mountain Switch - Fiddlewood Switch 345 kV | Slaton Sub - Southeast Sub 115 kV | RT | Planned |  |  |  |  | LPLHY | LPLSE | LPLSE_LPLHY | SL17LPL0
CNPE |  |  |  | Holmes - Plaza | LN | 138 | 21/10 | Eastside - Polk 138 kV | Downtown - Polk 138 kV | RT | Planned |  |  |  |  | PZ | HM | HM_PZ_06A | SHMG1V8
CPS | REMOVE | CPS | Removal due to the addition of Station K1 (Omnicron) cut into the identified Contengency. CPS will make an addition to the MTE List with the new Contingency identifying the correct lines and stations | Howard - Somerset | LN | 138 | 17/12, 18/1, 23/9, 24/5 | DCKT Cagnon - Rafter & Rafter - Txresrch 138 kV, DCKT Castrvll to Razorbac & Txresrch 138kV | Hondo Creek Switching Station - Moore Switching Station 138 kV, Medina Lake - Pipe Creek 138kV | RT | Planned |  |  |  |  | HOWARD | E3 | E3_S1 | SE3S18
CPS |  |  |  | Howard Auto MR2 345/138 kV | XF | 345 | 25/5, 25/6, 25/8 | DCKT McCoy - Pleasanton 69KV & McCoy - Tordillo 69KV | Pearsall Switching Station - Poteet Sub 69KV | RT | Planned |  |  |  |  | HOWARD | HOWARD | MR2 | XHO158
ONCOR, TMPA |  |  |  | Jack_Creek - Twin Oak Switch | LN | 345 | 20/11 | DCKT GibbonsCreek-Limestone 345 kV | Jewett - Singleton 345 kV (260_A) | RT | Planned | N |  |  |  | JK_CK | TOKSW | JK_TOKSW1 | SJK_TOK5
BRAZOS |  |  |  | Jaybird - Rw Miller | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned |  |  |  |  | MIL | JAYBIRD | JYBRD_MIL | SSTVMIL8
BRAZOS |  |  |  | Jaybird - Stephenville Bepc | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned |  |  |  |  | JAYBIRD | STV | JYBRD_STV | SJAYSTV8
CNPE |  |  |  | Jeanetta - WA Parish | LN | 345 | 21/12 | Meadow - Ph Robinson 345 kV | Magnolia Tnp - Seminole Tnp 138 kV | RT | Planned |  |  |  |  | WAP | JN | JN_WAP72A | SJNWA1P5
CNPE |  |  |  | Jeanetta - Westchase | LN | 138 | 23/2 | DCKT Bellaire -H O Clarke 138 kV | Jeanetta - Westwood 138 kV | RT | Planned |  |  |  |  | JN | WZ | JN_WZ_05 | SWZJN8
CNPE |  |  |  | Jeanetta - White Oak | LN | 345 | 24/7 | Wa Parish To Obrien Lin OB_WAP99 | Wa Parish - Obrien Lin OB_WAP98 | RT | Forced |  |  |  |  | WO | JN | JN_WO_72 | SWOJN5
ONCOR |  |  |  | Jewett - Singleton (260_A) | LN | 345 | 2018 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | ADD | [5 empty] | JEWET | SNG | 260_A | SSNGJE25
AEP |  |  |  | Jim Treece - Riley | LN | 345 | 16/11 | Basecase | Panhandle GTC | ST | Planned |  |  |  |  | JIMTREEC | RILEY | JIMTRE_RILEY2 | SJIMRI25
AEP | REMOVE | AEP | Jim Treece to Tesla is no longer a valid cirucit. Salvare has been cut in between the two stations. | Jim Treece - Tesla | LN | 345 | 16/11, 17/2 | Basecase | Panhandle GTC | ST | Planned | Y, N |  |  |  | JIMTREEC | TESLA | JIMTRE_TESLA2 | SJIMTE25
DME, TMPA | REMOVE | DME | Rd Wells Interchange - West Denton 138 kV line upgrade project has been completed | Jimchristal - West Denton | LN | 138 | 23/10 | Fort Worth Sub - Teasley Sub 138 kV | Rd Wells Interchange - West Denton 138 kV | RT | Planned |  |  |  |  | JCHRSTL | W_DENT | AIR_W_DE | SJMCW_D8
ONCOR |  |  |  | Johnson Switch - Venus Switch | LN | 345 | 19/10, 19/11 | DCKT Venus Switch to Timberview Switch & Everman Switch 345 KV, Concord Auto CRD1 345/138 kV | Cedar Hill Switch - Fish Creek Switch 138 kV (3180), Concord Auto CRD2 345/138 kV | RT | Planned |  |  |  |  | JONSW | VENSW | 141 | SJONVEN5
CNPE |  |  |  | Jones Creek - Refuge | LN | 345 | 24/12 | Twr (345) Blu-bly72 & Hlj-wlf64 | South Texas Project - Jones Creek 345kV | RT | Planned |  |  |  |  | JCK | REF | JCKREF27 | SREFJCK5
CNPE |  |  |  | Jones Creek - South Texas Project | LN | 345 | 22/4, 22/6 | Elmcreek - South Texas Project 345 kV & South Texas Project - WA Parish 345 kV, DCKT BLUE-Bailey & Hillje - Wolf 345 kV | Hillje - South Texas Project 345 kV, Jones Creek - Refuge 345 kV | RT | Forced, Planned |  |  |  |  | JCK | STP | JCKSTP18A | SJCKSTP5
TNMP |  |  |  | Jones Street Tnp - Lakepointe Tnp | LN | 138 | 17/11, 17/12, 19/3, 20/1, 20/2, 20/3 | DCKT Carrollton Northwest to Lewisville Switch 345 kV | Ti Tnp - West Tnp 138 kV, Carrollton Northwest - Lakepointe Tnp 138kV, Argyle - Hihglands Tnp 138 kV | RT | Planned |  |  |  |  | LWVJS | LKPNT | 590_B | SLWVLKP8
BRAZOS, TNMP |  |  |  | Jones Street Tnp - Lewisville Switch | LN | 138 | 20/3 | DCKT Carrollton Northwest to Lewisville Switch 345 kV | TI Tnp - West Tnp 138 kV | RT | Planned |  |  |  |  | LWSSW | LWVJS | 590_A | SLWVLWS8
CNPE |  |  |  | Jordan - King | LN | 345 | 21/11, 22/11 | Jordan - King 345 kV & Jordan - North Belt 345 kV, DCKT Crown - Tanker 138 kV & Davson - ... - Greens Bayou 138 kV | Lychem - Power Systems Arco Cogen 138 kV | RT | Planned |  |  |  |  | KG | JOR | JORKG_97 | SKGJOR5
AEP |  |  |  | Joslin - Sand Crab | LN | 138 | 21/11 | Formosa G3 | Formosa - Lolita 138 kV | RT | Planned |  |  |  |  | JOSLIN | SANDCRAB | JOSLIN_SANDCR1 | SJOSSAN8
LCRA |  |  |  | Kendall - Kerrville Stadium | LN | 138 | 24/5 | Comfort To Cypress Creek 138kV | Raymond F Barker - Comfort 138kV | RT | Planned |  |  |  |  | KERRST | KENDAL | 115T123 | SKERKEN8
LCRA | REMOVE | LCRA | Congestion was caused by area outages. No congestion since 2022. | Kendall CTEC - Maenius Road | LN | 138 | 22/4 | Comfort - Kendall 138 kV | Hollmig - Kendall 138 kV | RT | Planned |  |  |  |  | KENDCT | MAENRO | 22T342 | SMAEKEN8
ONCOR |  |  |  | Killeen Switch - Salado Switch (271) | LN | 345 | 18/12 | Killeen Switch TRX KLNSW_3_2 345/138 | Killen Switch TRX MR1H 345/138 kV | RT | Planned |  |  |  |  | KLNSW | SALSW | 271 | SKLNSA25
ONCOR |  |  |  | Killeen Switch - Salado Switch (272) | LN | 345 | 18/12 | Killeen Switch TRX KLNSW_3_2 345/138 | Killen Switch TRX MR1H 345/138 kV | RT | Planned |  |  |  |  | KLNSW | SALSW | 272 | SKLNSAL5
ONCOR |  |  |  | Killeen Switch Auto AXFMR1 345/138 kV | XF | 345 | 22/1, 22/2, 22/3, 22/4, 22/5 | DBCKT Salado Switch - Killeen Switch 345 kV | Killeen Switch Auto AXFMR2 345/138 kV | ADD | Planned |  |  |  |  | KLNSW |  | AXFMR1 | XKLN58
ONCOR |  |  |  | Killeen Switch Auto AXFMR2 345/138 kV | XF | 345 | 2022 | DBCKT Salado Switch - Killeen Switch 345 kV | Killeen Switch Auto AXFMR1 345/138 kV | ADD | Planned |  |  |  |  | KLNSW |  | AXFMR2 | XKLN358
ONCOR |  |  |  | Knob Creek Switch - Salado Switch | LN | 345 | 19/9 | DCKT Temple Elm Creek to Belton 138 kV | Temple Southeast - Temple Switch 138 kV | RT | Planned |  |  |  |  | SALSW | KNBSW | 36040 | SKNBSAL5
ONCOR |  |  |  | Koch Tap - Vealmoor | LN | 138 | 25/5, 25/6, 25/7, 25/8, 25/9, 25/10, 25/11 | Wett_Long_Draw - Volta 345KV | Buzzard Draw Switch - Koch Tap 138KV | RT | Planned |  |  |  |  | KOCHTAP | VEALMOOR | 15060_B | SKOCBUZ8
ONCOR | REMOVE | ONCOR | Remove this MTE due to Oncor establishing Gunter Switch, Dunham Switch and Ramhorn Hill Switch which increased 345 kV connectivities in the areas where the MTEs and Contingencies are located. This MTE, Krum West Switch - Lewisville Switch, no longer exists due to Dunham Switch being cut in between Krum West Switch and Lewisville Switch | Krum West Switch - Lewisville Switch | LN | 345 | 25/3 | DCKT Anna Switch - Cedar Elm Switch & Anna Switch -Krum West Switch 345kV | Argyle - Corinth 138kV | RT | Planned |  |  |  |  | LWSSW | KRWSW | 35010 | SKRWLW25
AEP, ONCOR |  |  |  | Krum West Switch - Riley | LN | 345 | 24/11 | DCKT Bowman Switch - Riley & Byrd Road Switch 345 kV, Jacksboro Switching - Cobb Switching Station 345kV | Fisher Road Switch - Riley 345kV, Bowman Switch - Garvey Road Switch 345kV | RT | Planned |  |  |  |  | RILEY | KRWSW | 37020 | SKRWRI15
AEP |  |  |  | La Palma - Villa Cavazos | LN | 138 | 22/6, 23/3, 23/5 | STILLMAN - LOMA ALTA SUBSTATION 138 kV, WATERPORT SUBSTATION - LOMA ALTA SUBSTATION 138 kV | Titan_ Substation - Scarbi Carbide 138 kV, Paloa Alto Substation - Titan_ Substation 138 kV | RT | Forced, Planned |  |  |  |  | LA_PALMA | VCAVAZOS | LA_PAL_VCAVAZ1 | SVCALA_8
AEP |  |  |  | La Palma -...- Military Highway Aep | LN | 138 | 24/6, 24/10 | Stillman To Loma Alta Substation 138kV | Titan Substation - South Carbide 138kV | RT | Planned |  |  |  |  | VCAVAZOS | MILITARY | MILITA_VCAVAZ1 | SVCAMIL8
ONCOR | MODIFY | ONCOR | Change Contingency from "DCKT Centerville Road Switch - East Zacha 138KV & East Zacha - White Rock 138KV & Parkdale Switch - White Rock 138KV" to "DCKT Parkdale SES - Centerville Road Switch 138 kV" | Lake Hubbard Ses - Saint Augustine Tap | LN | 138 | 25/8, 25/9, 25/10 | DCKT Parkdale SES - Centerville Road Switch 138 kV | Lake Hubbard SES - Prairie Creek Switch 138KV | RT | Planned |  |  |  |  | LHSES | SATP1 | 3650_A | SLKJLHS8
CNPE |  |  |  | Langston - Mont Belvieu | LN | 138 | 26/4 | Cedar Bayou - Jordan 345KV & Chambers - Jordan 345KV | Hopson - Warvue 138KV | RT | Planned |  |  |  |  | LAN | MB | LANMB_86 | SLANMB8
AEP | REMOVE | AEP | Long time since last occurred. | Laquinta - Lobo | LN | 138 | 15/5 | Crestonio to Falfurrias 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y |  |  |  | LOBO | LAQUINTA | LAQUIN_LOBO1 | SLAQLOB8
AEP |  |  |  | Laredo Vft North - Milo | LN | 138 | 24/6, 25/7, 25/8 | University Aep To Del Mar 138kV | Catarina - Piloncillo 138kV | RT | Planned |  |  |  |  | LASCRUCE | MILO | LASCRU_MILO1 | SLARLAS8
AEP |  |  |  | Laredo VFT North -…- North Laredo Switch | LN | 138 | 22/4, 22/5, 23/4, 24/2, 24/6 | Fowlertron Auto 7TR 345/138 kV, Molina -…- Wormser Road 138 kV, Fowlerton - Lobo 345 kV, DCKT Lobo -…- Fowlerton 345kV | Del Mar - Laredo Plant 138 kV, Bruni Sub Auto1 138/69 kV, Wormser Road - Gateway West Tap 138 kV, Lardvnt Vft North - Las Cruces 138 Kv, Catarina - Piloncillo 138kV | RT | Forced, Planned |  |  |  |  | MILO | MINES_RD | MILO_MINES_1 | SMINNLA8
ONCOR | REMOVE | ONCOR | Remove this MTE due to Oncor establishing Gunter Switch, Dunham Switch and Ramhorn Hill Switch which increased 345 kV connectivities in the areas where the MTEs and Contingencies are located. This MTE, Lewisville Switch - Roanoke Switch, no longer exists due to Dunham Switch being cut in between Roanoke Switch and Lewisville Switch | Lewisville Switch - Roanoke Switch | LN | 345 | 19/3, 19/4, 25/3 | DCKT Carrollton Northwest - Lewisville Switch 345 kV, Argyle - … - Lewisville Switch 138 kV, DCKT Hicks Switch -…- Roanoke Switch 138kV, DCKT Cedar Hill Switch - Timberview Switch & Venus Switch 345 kV | Argyle - Highlands Tap 138 kV, Roanoke Switch Auto MR1L 345/138kV, Liggett Switch - Norwood Switch 345kV | RT | Forced, Planned |  |  |  |  | LWSSW | RNKSW | 105_B | SLWSRNK5
BRAZOS |  |  |  | Lewisville Switch Auto FMR2 345/138 kV | XF | 345 | 17/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned |  |  |  |  | LWSSW |  | FMR2 | XLWS158
ONCOR | MODIFY | ONCOR | Change Contingency from "DCKT Courtland - Timberview Switch 345KV & Cedar Hill Switch - ... - Venus Switch 345KV" to "Venus Switch 345/138 kV Auto 3" | Liggett Switch - Norwood Switch | LN | 345 | 26/4 | Venus Switch 345/138 kV Auto 3 | Sardis - Sterrett 138KV | RT | Planned |  |  |  |  | LIGSW | NORSW | 310 | SLIGNOR5
BPUB, ONCOR, SHARL |  |  |  | Loma Alta Substation - Stillman | LN | 138 | 23/3 | Millitary Highway Aep - Villa Cavazos 138 kV, DCKT La Palma - Villa Cavazos 138 kV & Rangerville 69 kV | Titan_ Substation - Scarbi Carbide 138 kV | RT | Forced |  |  |  |  | LOMA_ALT | STILLMAN | STLLMN_LOMA | SSTILOM8
BPUB |  |  |  | Loma Alta Substation - Waterport Substation | LN | 138 | 16/5, 18/1 | Loma Alta Sub Auto T1 138/69 kV, La Palma to East Harrison 69 kV | La Palma - Villa Cavazos 138 kV, Haine Drive - La Palma 138 kV | RT | Forced, Planned |  |  |  |  | WATERPRT | LOMA_ALT | WP_LA | SWATLO28
AEP |  |  |  | Lon Hill - … - Mathis | LN | 69 | 24/1 | George West Switching Station Auto 138_69_1 138/69 kV | Orange Grove Switching Station Auto 138_69_1 138/69 kV | RT | Planned |  |  |  |  | EDROY | SMITH | EDROY_SMITH1 | SSTELO29
ONCOR, WETT | REMOVE | WETT | Congestion was on 11/24/25. There were several outages at Consavvy Switch that contributed to the congestion. | Longshore Switch - Wett_bearkat | LN | 345 | 25/11 | Bernoulli - Wett_Bearkat 345KV | Eiland - Hillger Sub 138KV | RT | Planned |  |  |  |  | LNGSW | W_BK_345 | 6065 | SW_BLNG5
STEC |  |  |  | Loop 463 Sub - Victoria | LN | 138 | 22/4 | Coleto Creek - Victoria 138 kV (COLETO_VICTOR1) | Coleto Creek - Victoria 138 kV (COLETO_VICTOR2) | RT | Planned |  |  |  |  | L_463S | VICTORIA | LOOP_VICTORIA | SL_4VIC8
AEP, CPS |  |  |  | Loxley - Pleasanton | LN | 138 | 25/8 | Hunt_ln - Cagnon 138kV | Leon Creek - Howard 138kV | RT | Planned |  |  |  |  | LOXLEY | PLEASANT | LOXELY_PLE | SLOXPLE8
AEP, CPS |  |  |  | Loxley - Trumbo | LN | 138 | 25/8 | Hunt_ln - Cagnon 138kV | Leon Creek - Howard 138kV | RT | Planned |  |  |  |  | E4 | LOXLEY | E4_LOXLEY | SLOXPLE8
ONCOR |  |  |  | Martin Lake Ses - Mt Enterprise | LN | 345 | 2017 | Martin Lake - Elktion and Tyler Grande DCKT | Martin Lake - Shamburger | ADD | [5 empty] | MLSES | ENTPR | 360 | SENTMLS5
ONCOR | MODIFY | ONCOR | Contingency should be changed from "DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV" to "DCKT Martin Lake SES to Dorsett Switch & Tyler Grande 345 kV" | Martin Lake Ses - Styker Creek Ses | LN | 345 | 2017 | DCKT Martin Lake SES to Dorsett Switch & Tyler Grande 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD | [5 empty] | MLSES | SCSES | 370 | SMLSSCS5
ONCOR |  |  |  | Martin Lake Ses - Tyler Grande | LN | 345 | 2017 | DCKT Martin Lake Ses to Styker Creek Ses & Mt Enterprise 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD | [5 empty] | MLSES | TYGND | 340 | STYGMLS5
AEP |  |  |  | Mason Switching Station - Mason Phillips Tap | LN | 69 | 26/1 | Fort Mason Yellow Jacket 138KV | Hext LCRA - Mason Switching Station 69KV | ST | Forced |  |  |  |  | MASONSW | MASNPHT | MASNPH_MASONS1 | SPHMMAS9
ONCOR, TMPA |  |  |  | Mccree - Centerville Road Switch | LN | 345 | 25/6 | Ben Davis - Royse Switch 345KV | Mesquite North Tap - Oates 138kV | ST | Forced |  |  |  |  | MCCREE | CNRSW | MCCCENTU | SMCCCNR5
GAR |  |  |  | Mccree - Shiloh | LN | 138 | 24/5 | Ben Davis - Brand 138kV | Miller - Newman 138kV | RT | Planned |  |  |  |  | SHILOH | MCCREE | SHIL_MCC | SSHIMCC8
LPL |  |  |  | Mcdonald Substation - Northwest Substation | LN | 115 | 23/2, 23/4 | Blackwater Draw Switch - Double Mountain Switch 345 kV | MacKenzie Substation - Northeastern Substation 115 kV | RT | Planned |  |  |  |  | LPLNW | LPLMD | LPLNW_LPLMD | SL18LPL0
LCRA | REMOVE | LCRA | The overloaded elements T387 Howard Lane-Wells Branch and 1661_B Hutto-Round Rock North East have higher ratings | Mcneil - Wells Branch | LN | 138 | 22/6, 23/9, 23/11 | DCKT Techridge - Ashton Woods AEN & Howard Lane AEN, DCKT Hutto Switch - Round Rock & Georgetown South 138 kV | Hutto Switch - Round Rock Northeast 138 kV, Howard Lane - Wells Branch 138 kV | RT | Planned |  |  |  |  | WELLBR | MCNEIL_ | 96T136 | SWELMCN8
CNPE |  |  |  | Meadow - Ph Robinson | LN | 345 | 22/11, 26/3, 26/4 | DCKT Gable Street -…- Greens Bayou 138 kV, NORTH ALVIN TNP - ALVIN TNP 138 kV , DCKT Davidson - ..-Greens Bayou BY21 & Crown - Tanker 138 kV | Magnolia Tnp - Seminole Tnp 138 kV | RT | Planned |  |  |  |  | MDO | PHR | MDOPHR99 | SMDOPHR5
STEC |  |  |  | Merett Sub - Palmhurst Sub | LN | 138 | 22/10 | DCKT North Edinburg -..- North Pharr & North McAllen 138 kV | Hec Energy Center - Azteca Sub 138 kV | RT | Planned |  |  |  |  | MV_PALM4 | MERETT | MERETT_PLMHRST | SMERMV_8
ONCOR | REMOVE | ONCOR | Remove this MTE due to Mesquite North Tap - Oates 138 kV Line being rerouted as Mesquite East - Oates 138 kV Line. | Mesquite North - Mesquite Town East | LN | 138 | 25/10 | Centerville Road Switch AXFMR1 345/138kV | Mesquite North Tap - Oates 138kV | ST | Forced |  |  |  |  | MESTE | MESQN | 1100_A | SMESFO28
CNPE |  |  |  | Miller -…- Rohmas | LN | 138 | 23/1 | Jefferson - College 138 kV | Conial - Philip 138 kV | RT | Forced |  |  |  |  | BNS | MLR | BNSMLR88 | SRHMLR8
ONCOR |  |  |  | Mitchell Bend Switch - Rocky Creek | LN | 345 | 19/10, 19/11, 22/12 | DCKT Comanche Peak SES - Timberview Switch & Johnson Switch 345 kV, DCKT Timberview Switch - Comanche Peak SES & Carmichael Bend Switch 345 kV | Carmichael Bend Switch - Mitchell Bend Switch 345 kV, Benbrook SW - Sycamore Creek 345 kV | RT | Forced, Planned |  |  |  |  | RKCRK | MBDSW | 152_A | SRKCMB35
ONCOR |  |  |  | Mitchell Bend Switch - Wolf Hollow 345 Switch | LN | 345 | 22/3, 23/3, 25/11, 26/4 | Comanche Peak Ses - Johnson Switch (Oncor) 345 kV & Comanche Peak Ses - Timberview Switch 345 kV | Comanche Peak Ses - Mitchell Bend Switch 345 kV | RT | Forced |  |  |  |  | WOFHO | MBDSW | 6034_A | SRKCMB25
ONCOR |  |  |  | Montfort Switch -...- Shankle Switch | LN | 138 | 24/6 | Pebble Creek Switch -…- Shankle Switch 138kV | Ennis West Switch - Templeton 138kV | RT | Forced |  |  |  |  | ENPTP | TLC | 920_D | SSHKCRI8
ONCOR |  |  |  | Monticello Ses - … -Paris Switch | LN | 345 | 2017 | Paris Switch to Valley South 345 kV & Pacific Switch to Valley SES 345 Kv | Paris Sw 345/138 kV Auto MR1 | ADD | [5 empty] | PRSSW | WDDSW | 390 | SMNSPRS5
ONCOR |  |  |  | Monticello Ses - Sulphur Springs Switch | LN | 345 | 25/5 | DCKT Farmersville Switch - Cyclone Switch & Saltillo Switch 345 kV | Monticello SES - Woodard Switch 345kV | ST | Forced |  |  |  |  | MNSES | SSPSW | 205 | SSSPMNS5
STEC |  |  |  | Moore Sub - Pearsall Switching Station | LN | 69 | 25/6 | Pearsall Switching Station -...- San Miguel 69Kv Switchyard 69kV | Devine Sub - Moore Sub 69kV | ST | Forced |  |  |  |  | MOORES | PEARSALL | MOO_PEAR | SPEADEV9
ONCOR |  |  |  | Moss Switch - …- Odessa Ehv Switch | LN | 138 | 24/9 | DCKT Odessa EHV - Moss Switch & Wolf Switch 345kV | Odessa North - Odessa 138 kV | RT | Forced |  |  |  |  | BTHOT | ODEHV | 6500_B | SBTHOD58
ONCOR | MODIFY | ONCOR | Overload should be changed from "Odessa Ehv Switch - Yarbrough Sub 138kV" to "Reiter Switch - Yarbrough Sub 138kV" | Moss Switch -…- Yucca Drive Switch | LN | 138 | 24/12, 25/1, 25/2 | DCKT Odessa EHV - Moss Switch & Wolf Switch 345kV, DCKT Moss Switch - Meteor Switch & Odessa EHV - Wolf Switch 345kV, DCKT Wolf Switch - Meteor Switch & Odessa EHV 345kV | Reiter Switch - Yarbrough Sub 138kV, Wolf Switching Station - Sandhills Tap 138kV | RT | Forced |  |  |  |  | MOSSW | METSW | 34630 | SMOSYUC8
ONCOR |  |  |  | Mt Enterprise - Trinidad Ses | LN | 345 | 2017 | DCKT Tri Corner - Elkton & Tyler Grande 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [5 empty] | ENTPR | TRSES | 361 | SENTTR25
BRAZOS |  |  |  | Myra -…- Spring | LN | 138 | 25/1, 25/2 | DCKT Lewisville Switch -…- West Denton 345kV | Bennett Road Switch - Decatur 138kV, Allison - Krum Switch 138kV | RT | Planned |  |  |  |  | MYRA | VALYVIEW | MYRA_VAL | SMYRSPR8
ONCOR |  |  |  | Nacogdoches Se - Redland Switch | LN | 138 | 18/12 | DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Lufkin Switch - Nacogdoches South Tap 138 kV | RT | Planned |  |  |  |  | NCDSE | REDSW | 1170 | SNCDRED8
AEP |  |  |  | Nelson Sharpe Auto 345_138_AUTO 345/138 kV | XF | 345 | 23/3 | Barney Davis - Alazan 138 kV | Celanebi Bishop - Kleberg Aep 138 kV | RT | Forced |  |  |  |  | N_SHARPE | N_SHARPE | 345_138_AUTO | XN_S58
CNPE |  |  |  | New Gulf - South Lane City | LN | 138 | 22/5 | STP SWITCH -…- STP Facilites HLP & Esperanza & Blessing 138 kV | Blessing - Pavlov 138 kV | RT | Forced |  |  |  |  | LC | NEW | LC_NEW60 | SNEWGLF8
AEP |  |  |  | North Carbide - Sea Drift Coke | LN | 138 | 25/10 | Grissom - Angstrom 345kV | Warburton Road Switching Station - Victoria 138kV | ST | Forced |  |  |  |  | SEADRFTC | NCARBIDE | NCARBI_SEADRF1 | SAIRNCA8
LCRA, ONCOR |  |  |  | North McCamey - … - Odessa Ehv Switch | LN | 345 | 2018 | Basecase | McCamey GTC | ADD | [5 empty] | NORTMC | ODEHV | MCCAMEY_ODESSA | SNORODE5
STEC |  |  |  | Oaks Sub - Poteet Sub | LN | 69 | 17/12, 18/1 | DCKT Castrvll to Razorbac & Txresrch 138kV | Hondo Creek Switching Station - Moore Switching Station 138 Kv | RT | Planned |  |  |  |  | POTEETS | OAKS9 | POT_OAKS | SPOTOAK9
ONCOR |  |  |  | Oates - … - Royse Switch 138 Kv (1391) | LN | 138 | 23/9 | Centerville - Oates 138 kV | Buckner Home - Mesquite Forney Road 138 kV | RT | Planned |  |  |  |  | RYSSW | FATES | 1391_E | SDALRY28
CNPE |  |  |  | Obrien - Wa Parish (OB_WAP98) | LN | 345 | 22/8, 23/9 | DCKT Wa Parish-Jeanetta 345 kV | Wa Parish - Obrien 345 kV (OB_WAP99) | RT | Planned |  |  |  |  | WAP | OB | OB_WAP98 | SOBWA2P5
CNPE |  |  |  | Obrien - Wa Parish (OB_WAP99) | LN | 345 | 20/8, 22/8 | DCKT Wa Parish-Jeanetta 345 kV | Wa Parish - Obrien 345 kV (OB_WAP98) | RT | Forced, Planned |  |  |  |  | WAP | OB | OB_WAP99A | SOBWAP5
ONCOR, WETT | MODIFY | WETT | Gail Sub-Willow Valley Switch planned to be upgraded before 2027. Established Tredway Switch/Estacado and rebuilt Expanse Switch -Estacado 138 kV line changes the network configuration and lowers loading on Koch Tap-Vealmoor Tap. Contingency should be changed from "DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses" to "DCKT Consavvy Switch - Prairieland Switch 345 kV" Remove "Kocht Tap - Vealmoor 138 kV" from Overload. Due to completion of Tredway as well as Estacado and rebuild of Expanse Switch - Estacado 138 kV line, the overloading condition on Koch Tap - Vealmoor no longer exists. | Odessa EHV Switch - Wett_Grelton | LN | 345 | 22/3, 22/4 | DCKT Consavvy Switch - Prairieland Switch 345 kV, Scurry County South Switch - Wett_Long_draw 345 kV & Wett_Faraday - Wett_Long_Draw 345 kV, DCKT Scurry County South Switch - Tonkawa Switch 345 kV | Gail Sub - Willow Valley Switch 138 kV, Kocht Tap - Vealmoor 138 kV | RT | Planned |  |  |  |  | W_GT_345 | ODEHV | T-306 | SW_GODE5
LCRA |  |  |  | Odlaw Switch - … - Uvalde Aep | LN | 138 | 19/2, 22/11, 22/12 | Bighill - Kendal 345 kV, Big Hill - Twin Buttes 345 kV | Hamilton Road - Maverick 138kV, Ganso - Maverick 138 kV | RT | Forced, Planned |  |  |  |  | BLEWET | ASPHALT | 222T570 | SBRAUVA8
GAR |  |  |  | Olinger - Wylie Switch (WYL_OLI1) | LN | 138 | 16/4 | Greenville Steam to Shelby 138 kV | Shelby Auto BT1 138/69 kV | ST | Forced |  |  |  |  | WYLIESW | OLINGR | WYL_OLI1 | SFIRWY18
GAR |  |  |  | Olinger - Wylie Switch (WYL_OLI2) | LN | 138 | 15/9, 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned |  |  |  |  | WYLIESW | OLINGR | WYL_OLI2 | SOLIWY18
GAR |  |  |  | Olinger - Wylie Switch (WYL_OLI3) | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned |  |  |  |  | WYLIESW | OLINGR | WYL_OLI3 | SOLIEL28
AEP |  |  |  | Olmito - Palo Alto Substation | LN | 138 | 25/3 | Stillman To Loma Alta Substation 138kV | Villa Cavazos - Military Highway Aep 138kV | RT | Forced |  |  |  |  | OLMITO | PALOALTO | OLMITO_PALOAL1 | SPALMIL8
AEP |  |  |  | Owls - Santa Rita | LN | 138 | 25/1 | DCKT Big Hill - Schneenman Draw 345kV | Lake Nasworthy - San Angelo Mathis Field 69kV | RT | Forced |  |  |  |  | SANTARIT | OWLS | OWLS_SANTAR1 | SSANOWL8
AEP |  |  |  | Paint Creek Bus #1 (CB 4135, etc.) | BUS | 138 | 16/5, 16/6, 17/1 | Scurry Sw to Sun Sw 138 kV, Salt Creek Bepc to Salt Creek Reactor 138 kV | Eskota Sw - Longworth 69 kV, Aspermont Auto 69T1 138/69 kV | ST | Planned |  |  |  |  | PAINTCRE |  | 8BB1 | N/A
ONCOR | MODIFY | ONCOR | Contingency should be changed from "Woodward Switch - Monitcello Ses 345 kV" to "Woodard Switch - Monitcello Ses 345 kV" | Paris Switch - Valley South | LN | 345 | 22/11 | Woodard Switch - Monitcello Ses 345 kV | Paris Switch AXFMR1H 345/138 kV | RT | Forced |  |  |  |  | PRSSW | VLYSO | 403_A | SVLYPRS5
ONCOR | MODIFY | ONCOR | Contingency should be changed from "Woodward Switch - Monitcello Ses 345 kV" to "Woodard Switch - Monitcello Ses 345 kV" | Paris Switch -…- Valley SES | LN | 345 | 22/11 | Woodard Switch - Monitcello Ses 345 kV | Paris Switch AXFMR1H 345/138 kV | RT | Forced |  |  |  |  | PRSSW | VLSES | 391_A | SPRSVLS5
ONCOR |  |  |  | Paris Switch CB_8635 | CB | 345 | 2017 | Paris Switch to Pacific Switch & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD | [5 empty] | PRSSW |  | 8635 | N/A
STEC |  |  |  | Pawnee Switching Station - San Miguel Gen | LN | 138 | 25/4 | DCKT Skyline - Calaveras 345kv | Pawnee Switching Station - San Miguel Gen 345kV | RT | Forced |  |  |  |  | PAWNEE | SANMIGL | PAWNE_SANMI_1A1 | SPAWSAN5
AEP |  |  |  | Pharr Magic Valley - Se Edinburg | LN | 138 | 25/7 | West Edinburg Sub - Palmhurst Sub 138kV | Weslaco Switch - Val Verde Sub 138kV | ST | Forced |  |  |  |  | PHARMVEC | SE_EDINB | PHARMV_SE_EDI1 | SSE_CLO8
AEP | REMOVE | AEP | Oleander station cut-in allows flow between 138 and 69 section | Primera - Rio Hondo | LN | 138 | 20/7 | La Palma-Rangerville (MVEC) 138 kV | Haine Drive - La Palma 138 kV | RT | Forced |  |  |  |  | S_SNROSA | PRIMERA | PRIMER_S_SNRO11 | SS_SPRI8
ONCOR | MODIFY | ONCOR | MTE should be changed from "Falcon Seaboard - Ranger Camp Switch" to "Prong Moss Switch - Ranger Camp Switch" Contingency should be changed from "Consavvy Switch To Morgan Creek Ses 345kV, DCKT Morgan Creek SES - Consavvy Switch & Longshore Switch 345kV" to "Cattleman Switch To Morgan Creek Ses 345kV, DCKT Morgan Creek SES - Cattleman Switch 345kV" Overload should be changed from "Longshore Switch - Consavvy Switch 345kV" to "Longshore Switch - ... - Consavvy Switch 345 kV" | Prong Moss Switch - Ranger Camp Switch | LN | 345 | 25/1, 25/2 | Cattleman Switch To Morgan Creek Ses 345kV, DCKT Morgan Creek SES - Cattleman Switch 345kV | Morgan Creek Ses 345/138 kV Auto MR1H, Morgan Creek Ses - Ranger Camp Switch 345kV, Longshore Switch - ... - Consavvy Switch 345 kV | RT | Planned |  |  |  |  | FLCNS | MGSES | 6046_A | MRGRFLC5, MRGRMGS5
ONCOR | MODIFY | ONCOR | MTE should be changed from "Falcon Seaboard - Rockhound Switch" to "Pross Moss Switch - Rockhound Switch" | Pross Moss Switch - Rockhound Switch | LN | 345 | 20/10 | DCKT Odessa EHV Sw-Moss Sw & Wolf Switching Station 345 kV | Odessa North - Odessa 138 kV | RT | Planned | N |  |  |  | FLCNS | MDLNE | 6044 | SFLCMDL5
ONCOR | MODIFY | ONCOR | Overload should be changed from "Odessa Ehv Switch - Yarbrough Sub 138kV" to "Reiter Switch - Yarbrough Sub 138kV" | Red Lakes Switch -…- Wolf Switching Station | LN | 138 | 24/8 | DCKT Odessa EHV - Moss Switch & Wolf Switch 345kV, DCKT Moss Switch - Meteor Switch & Odessa EHV - Wolf Switch 345kV, DCKT Wolf Switch - Meteor Switch & Odessa EHV 345kV | Reiter Switch - Yarbrough Sub 138kV | RT | Forced |  |  |  |  | WLFSW | PWPOD | 6485_A | SWLFECT8
CNPE |  |  |  | Refuge - South Texas Project | LN | 345 | 24/3 | DCKT Bailey - Blue 345 kV & Hillje - Wolf 345 kV | Jones Creek - South Texas Project | RT | Planned |  |  |  |  | REF | STPSW | REFSTP27 | SSTPREF5
AEP |  |  |  | Riley - Tesla | LN | 345 | 21/11 | DBCKT Edith Clarke - Riley 345 kV | Abilene Mulberry Creek - Long Creek 345 kV | RT | Planned |  |  |  |  | RILEY | TESLA | RILEY_TESLA1 | STESRI15
AEP |  |  |  | Rio Hondo - South Santa Rosa | LN | 138 | 24/8, 25/11, 26/3 | Las Pulgas - Raymondville 2 138kV | Haine Drive - La Palma 138kV | RT | Forced |  |  |  |  | S_SNROSA | RIOHONDO | RIOHON_S_SNRO1 | MPRIRIO8
ONCOR, TMPA | MODIFY | ONCOR | Contingency should be changed from "Krum West Switch - Lewisville Switch 345kV, DCKT Lewisville Switch - Roanoke Switch & Lewisville Switch - Krum West Switch 345kV" to "Dunham Switch - Lewisville Switch 345kV, DCKT Lewisville Switch - Dunham Switch 345kV" | Roanoke Switch - West Denton | LN | 345 | 25/4 | Dunham Switch - Lewisville Switch 345kV, DCKT Lewisville Switch - Dunham Switch 345kV | Argyle - Highlands TNP 138kV, Denton Creek Switch - Decatur 138kV | RT | Planned |  |  |  |  | RNKSW | W_DENT | 165 | SW_DRNK5
ONCOR | REMOVE | ONCOR | Remove this MTE due to completion of McLane Switch - Frow Sub 138 kV line upgrade project | Robinson Northwest - Waco M/m Mars Tap 2 | LN | 138 | 25/7 | Waco East -…- Lake Creek SES 138kV | Mclane Switch - Frow Sub 138 kV | ST | Forced |  |  |  |  | ROBNW | WMMT2 | 1290_B | SWMMLCS8
ONCOR |  |  |  | Russell Gap Switch - Killeen Switch (35091) | LN | 345 | 22/9 | Comanche Switch (Oncor) to Comanche Peak SES 345 kV, DCKT Bighil-Kendal 345 kV | Comanche Tap - Comanche Switch (Oncor) 138 kV, Yellow Jacket - Treadwell 138 kV | RT | Forced |  |  |  |  | RGPSW | KLNSW | 35091 | SRGPKLN5
AEP, BRAZOS |  |  |  | Salt Creek SS - … - Spur | LN | 138 | 19/5 | DCKT Dermott Switch to Bluff Creek Switch & Golden Switch 138 kV | Morgan Creek SES - Sun Switch 138 kV | RT | Planned |  |  |  |  | SLTCRKSS | SCKR | SCKR_SCK | SSPUSLT8
STEC |  |  |  | Sam Rayburn Switch - Vanderbilt Switch | LN | 138 | 15/10 | Loop 463 to Sam Rayburn 138 kV | Sam Rayurn Swithcing Station Auto 69_2 138/69 kV | ST | Planned |  |  |  |  | RAYBURN | VANBLTSS | RAY_VANB | SVANRAY8
LSTR, ONCOR |  |  |  | Sam Switch - Venus Switch | LN | 345 | 25/1 | DCKT Navarro - Limestone Plant & Limestone Plant - Outlaw Sitch 345kV | Big Brown SES - Jewett 345kV (50) | RT | Planned |  |  |  |  | SAMSW | VENSW | 35055 | STHSVE65
AEP |  |  |  | San Angelo College Hills - … - San Angelo Power Station | LN | 138 | 19/9 | San Angelo Paulann to San Angelo Red Creek 138 kV | San Angelo Concho - San Angelo Emerson Street 69 kV | RT | Planned |  |  |  |  | SAPOWER | SOUTHLAN | SAPOWE_SOUTHL1 | SSASSA28
AEP | REMOVE | AEP | Updated SAPOWER ratings & RATLIFF SOLAR 73360_1 & ANGELO SOLAR | San Angelo Power Station - … - SA Highland Street | LN | 138 | 19/9 | San Angelo Coke Street to San Angelo Red Creek 138 kV | San Angelo Power Station - San Angelo South 69 kV | RT | Planned |  |  |  |  | SAPOWER | SAST | SAPOWE_SAST1 | SSASRED8
AEP | REMOVE | AEP | Updated SAPOWER ratings & RATLIFF SOLAR 73360_1 & ANGELO SOLAR | San Angelo Red Creek - … - San Angelo North | LN | 138 | 24/4 | San Angelo College Hills - … - San Angelo Power Station 138 kV | San Angelo Power Station Auto T1 138/69 kV | RT | Forced |  |  |  |  | PAULANN | REDCREEK | PAULAN_REDCRE1 | SPAUSAR8
AEP | REMOVE | AEP | Nicole line ratings update 97806_1 & Orient line rating updates 91699_1 & NORTON Solar 63507_1 | San Angelo Red Creek Auto T2 345/138 kV | XF | 345 | 16/10 | San Angelo Red Creek Auto T1 345/138 kV | Nicole - Orient 138 kV | RT | Planned |  |  |  |  | REDCREEK |  | T2H | XSA3R58
LCRA |  |  |  | San Marcos-Canyon | LN | 138 | 25/9 | Buda - Turnersville 138KV | Miller Creek - Henly 138KV | RT | Planned |  |  |  |  | CANYON | SANMAR | 108T273 | SBUDTUR8
AEP |  |  |  | Santa Rita - Wolfcamp | LN | 138 | 24/11 | Twin Buttes To Hargrove Lin 1 | SAMATHIS 69 - TANK | RT | Forced |  |  |  |  | SANTARIT | WOLFCAMP | SANTAR_WOLFCA1 | SWOLPAL8
ONCOR, WETT | MODIFY | ONCOR | Contingency should be changed from "DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses" to "DCKT Cattleman Switch - Morgan Creek SES 345kV" Overload should be changed from "Falcon Seaboard - Ranger Camp Switch 345 kV" to "Prong Moss Switch - Ranger Camp Switch 345 kV" | Scurry County South Switch - Wett_Long_Draw (T-304) | LN | 345 | 22/4, 22/5, 24/4 | Blackwater Draw Switch - Double Mountain Switch 345 kV, DCKT Cattleman Switch - Morgan Creek SES 345kV | MacKenzie Substation - Northeast Substation 115 kV, Prong Moss Switch - Ranger Camp Switch 345 kV | RT | Planned |  |  |  |  | W_LD_345 | SCOSW | T-304 | SW_LSCO5
AEP, BRAZOS | REMOVE | AEP | Long time since last occurance. Upgrades also done to MATADOR conencting to SPUR. | Scurry Switch - … - Spur | LN | 138 | 16/3, 16/10 | Aspermont Aep to Spur 138 kV | Spur Auto 69_1 138/69 kV | ST | Planned | Y, N |  |  |  | SCURRYSW | SCK | SLTCRK_SCRYSW | SSPUMW18
AEP |  |  |  | Silver - Sterling City & Spade Ranch | LN | 69 | 24/12 | DCKT Noelke - Cedar Canyon 345kV | Sterling City - Sterling County 69kV | RT | Forced |  |  |  |  | ANGORA | STER | ANGORA_STER1 | SSPACED9
BPUB |  |  |  | Sixth Street Substation - South Plant Substation | LN | 138 | 18/3, 18/4 | DCKT San Miguel Gen to Elmcreek 345 kV, Kendall to Cagnon 345 kV; | Pawnee Switching Station - Calaveras 345 kV, CICO - Comfort 138 kV | RT | Planned |  |  |  |  | SOUTH_PL | SIXTH_ST | 6ST_SP | SSIXSOU8
ONCOR |  |  |  | Snyder - … - Sun Switch (6240) | LN | 138 | 21/4 | DCKT Dermott Sw-…- Bluff Creek Sw & Ennis Creek Sw 138 kV | Ranger Camp Switch - Sun Switch 138 kV | RT | Planned | N |  |  |  | SNYDR | DPCRK | 6240_A | SSACSUN8
AEP |  |  |  | South Carbide - Titan Sub 138 kV | LN | 138 | 24/3 | Loma Alta Sub - Stillman 138 kV | La Palma - Villa Cavazos 138 kV | RT | Planned |  |  |  |  | TITAN_SU | SCARBIDE | SCARBI_TITAN_1 | STITSCA8
AEP, CNPE |  |  |  | South Texas Project - Static | LN | 345 | 25/11 | DCKT South Texas Project - Elmcreek & Wa Parish 345kV | Blessing 345_1382 345/138kV | ST | Forced |  |  |  |  | STATIC | STP | STATIC_STP1 | SSTPSTA5
CNPE |  |  |  | South Texas Project - WA Parish | LN | 345 | 21/9, 21/12, 22/2, 22/3, 23/2 | Jones Creek - Refuge 345 kV & Jones Creek - South Texas Project 345 kV, Jones Creek - South Texas Project 345 kV & Refuge - South Texas Project 345 kV, Hillje - Wolf 345 kV | Hillje - South Texas Project 345 kV, Blessing - Pavlov 138 kV, Jones Creek - South Texas Project 345 kV | RT | Planned |  |  |  |  | STP | WAP | STPWAP39 | STPWAP39
BPUB, STEC |  |  |  | Southmost Sub - Waterport Sub | LN | 138 | 18/1 | Lon Hill to Coleto Creek 345 kV, La Palma to East Harrison 69 kV, DCKT Jewett to Singleton 345 kV | Warburton Road Switching Station - Victoria 138 kV, Btu Jack Creek - Twin Oak Sw 345 kV | RT | Forced |  |  |  |  | WATERPRT | SOUTHMOS | WP_SM | SSOUWAT8
ONCOR |  |  |  | Stryker Creek Ses - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Tri Corner & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [5 empty] | SCSES | TRSES | 480 | STRSSCS5
ONCOR |  |  |  | Temple Elm Creek - Temple North | LN | 138 | 24/10 | DCKT Salado Switch - Knob Creek Switch 345 kV & Fryers Creek - Bell County 138 kV, DCKT Salado Switch - Knob Creek Switch 345 kV & Salado Switch - Bell County 138 kV, DCKT Salado Switch - Knob Creek Switch 345 kV | Temple South - Scott and White POI 138 kV | RT | Planned |  |  |  |  | TMECR | TMNTH | 625_C | MDPPCBN8
ONCOR |  |  |  | Temple Elm Creek - Temple Pecan Creek | LN | 138 | 25/4 | Temple Switch - Temple Pecan Creek 138 kV (1295) | Temple Switch - Temple Pecan Creek Lin 300_A 345kV | RT | Planned |  |  |  |  | TMECR | TMPCR | 1425 | STMETM48
CNPE |  |  |  | Th Wharton - Zenith (THWZEN71) | LN | 345 | 22/12, 26/2, 26/3, 26/4 | DCKT Singleton to Tomball 345 kV and Kuykendahl to Roans Prairie 345 kV and Kuykendahl to Rothwood 345 kV | Thw Wharton - Zenith (THWZEN98) 345 kV | RT | Planned |  |  |  |  | THW | ZEN | THWZEN71 | SZENTHW5
TNMP |  |  |  | TI TNP - West TNP | LN | 138 | 21/10 | DBCKT Carrollton Northwest - Lewisville Switch 345 kV | Jones Street Tnp - Lewisville Switch 138 kV | RT | Planned |  |  |  |  | LWVTI | LWSVW | 588_A | SLWSLW48
TNMP |  |  |  | Tnp One Plant - Twin Oak Switch | LN | 345 | 25/3, 25/4, 26/1 | DCKT Hillje -…- Wolf 345kV, Fort Smith Switch - Venus Switch 345kV | Twin Oak Switch -…- TNP One Plant Lin 261_A 345kV, Sam Switch - Venus Switch 345kV | RT | Planned |  |  |  |  | TOKSW | TNP_ONE | 262_A | STNPTOK5
TNMP |  |  |  | Tnp One Plant - Willow Switching Station TNP | LN | 345 | 25/5 | DCKT WA Parish - Whaley & Wolf 345kV | Twin Oak Switch - Tnp One Plant 345 kV (261_A) | RT | Planned |  |  |  |  | TNP_ONE | TNWILLOW | 345_TNP_WLO | STNPTNW5
ONCOR |  |  |  | Tri Corner - Tyler Grande | LN | 345 | 2017 | DCKT Trinidad Ses to Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [5 empty] | TRCNR | TYGND | 341 | STYGTRC5
ONCOR | MODIFY | ONCOR | Remove "Kleberg Tap - Seagoville 138 kV" from Overload due to completion of Kleberg Tap - Seagoville 138 kV Line upgrade project | Tri Corner - Watermill Switch (215) | LN | 345 | 19/9, 19/10, 20/2 | DCKT Centerville Road Switch to Parkdale Switch 138 kV, DCKT Big Brown SES to Richland Chambers 345 kV | Prairie Creek - Scyene Road 138 kV | RT | Planned |  |  |  |  | TRCNR | WTRML | 215 | STRCWTR5
ONCOR |  |  |  | Tri Corner - Watermill Switch (515) | LN | 345 | 19/9, 19/10, 20/2, 24/12, 25/9, 26/4 | DCKT Parkdale Switch - Centerville Road Switch 138 kV, DCKT Big Brown SES to Richland Chambers 345 kV, Tri Corner To Seagoville Switch Lin _b | Prairie Creek - Scyene Road 138 kV, Kleberg Tap - Seagoville 138 kV, Forney Switch - TriCorner 345 kV | RT | Planned |  |  |  |  | TRCNR | WTRML | 515 | STRSWTR5, MDWRTR25
BRAZOS |  |  |  | Trumbull Auto TRF2 138kV/69kV | XF | 138 | 25/1 | Desoto Switch -…- Pebble Creek Switch 138kV | Trumbull Auto TRF1 138/69kV | RT | Planned |  |  |  |  | TRU | TRU | TRF1 | XTRU89
TNMP |  |  |  | Twin Oak Switch - Willow Switching Station TNP | LN | 345 | 25/5, 26/4 | DCKT WA Parish - Whaley & Wolf 345kV | Twin Oak Switch - Tnp One Plant 345 kV (261_A) | RT | Planned |  |  |  |  | TOKSW | TNWILLOW | 345_TWN_WLO | STOKTNW5
ONCOR |  |  |  | Venus Switch - Fort Smith Switch | LN | 345 | 25/1, 25/3, 25/10 | Sam Switch - Tiger Creek Switch 345kV, Tiger Creek Switch - Tradinghouse SES 345kV, DCKT Navarro - Limestone Plant & Outlaw Switch 345kV, DCKT Limestone Plant - Navarro & Outlaw Switch 345kV | Jewett - Big Brown SES 345kV, Tradinghouse - Four Brothers Switch 345kV | RT | Forced, Planned |  |  |  |  | VENSW | FTSSW | 35050 | SVENFTS5
WETT | REMOVE | WETT | Alkali Lake-Jim Payne POI 138 kV was upgraded in November 2024. Established Tredway Switch-Estacado and rebuilt Expanse Switch -Estacado 138 kV line changes the network configuration and lowers loading on Koch Tap-Vealmoor Tap. | Volta - Wett_grelton | LN | 345 | 24/5, 24/6 | DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses, Wett Faraday -…- Scurry County South Switch 345kV, Odessa Ehv Switch To Wett_grelton 345kV | Alkali Lake - Jim Payne Poi 138kV, Koch Tap - Vealmoor 138kV | RT | Planned |  |  |  |  | W_GT_345 | VLTA | T-312 | SW_GVLT5
WETT | REMOVE | WETT | Alkali Lake-Jim Payne POI 138 kV was upgraded in November 2024. Established Tredway Switch/Estacado and rebuilt Expanse Switch -Estacado 138 kV line changes the network configuration and lowers loading on Koch Tap-Vealmoor Tap. | Volta - Wett_long_draw | LN | 345 | 24/5, 24/6 | DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses, Wett Faraday -…- Scurry County South Switch 345kV, Odessa Ehv Switch To Wett_grelton 345kV | Alkali Lake - Jim Payne Poi 138kV, Koch Tap - Vealmoor 138kV | RT | Planned |  |  |  |  | VLTA | W_LD_345 | T-305 | SW_LVLT5
STEC |  |  |  | Warburton Road Switching Station - Warburton Road Switching Station | CB | 69 | 24/7 | Victoria -…- Peregrine Substation 345kV, Grissom - Raptor 345kV | Warburton Road Switching Station - Victoria 138 kV | RT | Forced |  |  |  |  | WARBURTN | WARBURTN | 464 | XWAR89
LCRA |  |  |  | Wells Branch - Howard Lane Tap | LN | 138 | 26/07 | DCKT Hutto to Round Rock 138 kV and Hutto to Georgetown South 138 kV | McNeil-Wells Branch, McNeil-Howard Lane Tap | RT | Planned |  |  |  |  | WELLBR | HWRDTP | 378T387 | DHUTGEA8
ONCOR, WETT | REMOVE | ONCOR | Cannot locate binding constraint on "Northeast Substation - Dunbar Substation 115kV" for December 2025 | White River - Wrangler Switch | LN | 345 | 25/12 | Dunbar Substation - Blackwater Draw Switch 345kV | Northeast Substation - Dunbar Substation 115kV | RT | Planned |  |  |  |  | WHIT_RVR | W_CW_345 | 70150 | SWHIWRA5