## Slide 1: 2027 Ancillary Service Methodology Discussion Luis Hinojosa Manager, Ancillary Services & Operations Analytics TAC August 26, 2026
Key Takeaways
ERCOT is not proposing any changes to the methodology for Regulation and RRS aside from the annual data update.
ERCOT is proposing a measured updated to the risk credit parameter in the probabilistic model for ECRS and Non-Spin, reflecting increased historic headroom from RTC+B and growth in installed solar and ESR capacity.
Additional analysis of the probability of a Watch, EEA, or Load Shed — requested in the PUC's 2024 AS Study — has been included in today's posting.
Purpose
Provide proposed methodology to determine Ancillary Service (AS) quantities for 2027.
ERCOT is seeking endorsement on ERCOT’s proposed methodology for computing minimum AS quantities for 2027.

## Slide 2: Introduction
ERCOT has reviewed the methodology to determine minimum Ancillary Service (AS) requirements.
ERCOT is not proposing any changes in the methodologies used to compute Regulation Service and Responsive Reserve Service (RRS) requirements.
  The minimum RRS-PFR limit used in this analysis (1,377 MW) is from 2026. NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT for the 2027 Operating Year (OY) has not yet been published; an updated value is expected to be included in the September Board materials.
ERCOT is proposing a measured update to the risk credit parameter in probabilistic methodology to compute ERCOT Contingency Reserve Service (ECRS) and Non-Spinning Reserve Service (Non-Spin) requirements, reflecting increased historic headroom from RTC+B and growth in installed solar and ESR capacity.
ERCOT has included the following in today's posting:
  A redline document for 2027 AS Methodology.
  HTML with preliminary 2027 ECRS and NSRS quantities from 756 sensitivity scenarios assessed using the probabilistic model and the preliminary 2027 Regulation Up/Down and RRS quantities.
    Please note, 2026 data for August onward is not included in the probabilistic model so August through December 2027 are directional and quantities throughout the year may change once that data is included.
2027 Methodology Review Timeline
May 19, 2026 – TAC Kickoff
June 01, 2026 – BOARD Preview
June 17, 2026 – PDCWG
June 29, 2026 – WMWG
July 08, 2026 – WMS
July 09, 2026 – ROS
July 22, 2026 – PDCWG (Proposed)
July 27, 2026 – WMWG (Proposed)
July 28, 2026 – OWG (Proposed)
July 29, 2026 – TAC (2026 AS Methodology Discrepancy)
August 05, 2026 – WMS
August 06, 2026 – ROS
August 26, 2026 – TAC (Possible Vote)
September 15, 2026 – BoD
Nov, Dec 2026 – PUC

## Slide 3: Ancillary Services
Ancillary Services are procured to balance supply and demand while meeting reliability objectives defined in NERC Reliability BAL-001, BAL-002 and BAL-003 Standards, and to reduce operational risks associated with variability and uncertainty
Quantity Calculation
Regulation Up and Down
Offsets the ongoing mismatch between metered and dispatched net load (movement in load, wind, and solar).
Responsive Reserve (RRS)
Arrests frequency when a large resource trips, without triggering under-frequency load shed.
ERCOT Contingency Reserve (ECRS)
Provides frequency response and covers within-hour net-load movement the hourly commitment did not anticipate.
Non-Spinning Reserve Service (Non-Spin)
Covers multi-hour capacity shortfalls from forecast error and forced outages until more resources are committed.
Frequency control; normal and unexpected forced outages.
Capacity and energy for unexpected forecast errors and forced outages
Service
Purpose
Time Frame
Historical system response and study of system physics
Seconds to Minutes
Probabilistic analysis of forecast and outage risk.
Minutes to Hours
Key Takeaway: These services work together to meet ERCOT's NERC BAL obligations. Regulation and RRS provide frequency control and arrest events; ECRS and Non-Spin then restore those fast-response reserves so they can return to duty and remain ready for the next event. Preserving this ability to restore Reg Up and RRS is central to reliability.

## Slide 4: Regulation Quantities 2026 vs Preliminary 2027
Key Takeaway: The trend in preliminary 2027 Regulation Up and Down quantities is very similar to 2026.

## Slide 5: RRS Quantities 2026 vs Preliminary 2027
Key Takeaway: The trend in preliminary 2027 RRS quantities is very similar to 2026.

## Slide 6: ECRS & Non-Spin Probabilistic Model Recap & 2027 Recommendation
Key Takeaway: ERCOT evaluated several sensitivities on each parameter across 756 scenarios and, based on that analysis, is recommending X = 6 hours, Y = the headroom credit shown, W = 4-hour sustainability, XX = 10 years, YY = 100%, and ZZ = 3,000 MW.
INPUTS
ENGINE
OUTPUTS
Risks
(X=) hour ahead ahead and 30 min ahead Net Load Forecast Error and
Accumulated Forced Outages in (X=) hours
Risk Credits
(Y=) % of historically available
30 min online headroom
30 min start Offline capacity
ESR capacity sustainable for (W=) hours
(Night | Day) where night is HE23 to HE5 and day is HE6 to HE22
Monte Carlo Optimization
Convergence Criteria+ Met?
Net Risk
ECRS + Non-Spin
Requirement
(12 Month x 24 Hour)
No
Yes
ECRS Requirement
(12 Month x 24 Hour)
Non-Spin Requirement
(12 Month x 24 Hour)
+Convergence Criteria: 1 in XX year probability of operating reserves dropping below the sum of YY% (Reg Up plus RRS) or ZZ threshold, whichever is higher. Mathematically, this equates to
𝐸𝐶𝑅𝑆 +𝑁𝑆𝑅𝑆 < 𝑁𝑒𝑡𝑅𝑖𝑠𝑘 + 𝑀𝑎𝑥 (YY(𝑅𝑒𝑔 + 𝑅𝑅𝑆), ZZ) with probability of 1 in XX year.
2027 Recommendations
X = 6 Hours,
Y = Online: (60%:50%)
Offline (60%:50%) and
ESR: (60%:60%) with
W = 4-hour
XX = 10 years,
YY = 100%, and ZZ = 3,000 MW

## Slide 7: Why is ERCOT proposing to change headroom-related parameter Y for 2027?
Key Takeaway: ERCOT proposes a measured increase in the headroom credit (parameter Y) — Online 60% : 50%, Offline 60% : 50%, ESR 60% : 60% (night : day) — crediting more of the increased headroom than in 2026 without relying on 100% of it.
1
Uncertainty is increasing Forced outages and forecast errors still occur. As the system continues to add variable renewable resources, the risk of weather forecast errors impacting assumed resource capacity and energy is expected to increase.
2
Available headroom has increased and is likely to increase in 2027 Under RTC+B, thermal commitment efficiency has improved, shifting some online thermal to offline 30-minute-startable thermal. Growth in installed solar and ESR capacity has further increased headroom. These drivers will tend to increase headroom going forward as the solar and ESR capacity increases.
3
Load is growing — but headroom may still be available in 2027 Load growth will consume some of what would otherwise be increased headroom, so assuming 100% of historical headroom in setting reserve requirements is inappropriate. Based on 2026 experience, ERCOT does not see a need to be as cautious as in 2026, when only 25% credit was used for daytime hours.

## Slide 8: Projected Installed Capacity of Wind and Solar Resources (as of July 31, 2026)
Key Takeaway: Steady growth in installed capacity for renewable resources is expected to continue in 2027.

## Slide 9: Uncertainty Growth Analysis
Uncertainty is growing year over year with a majority of growth coming from solar. This is due to overall increase in solar capacity and correlated forecast error.
A deeper dive into solar uncertainty, shows that we have seen an increase in installed capacity in Far East region of Texas in 2025 and 2026.
Far East has more variable weather and cloud cover making forecasting more difficult, especially during ramping hours. This drove the switch from monthly to month-hour solar adjustment values to better capture hour-to-hour variance in solar forecast error.
Additionally, ERCOT has also observed an overall growth in forced outage MWs which contributes to total risk.
Key Takeaway: Growth in renewables is driving measurable growth in uncertainty — led by solar (especially the Far East) — and forced-outage MW are rising, together increasing total risk.

## Slide 10: Historic Headroom (i.e. Risk Credit) Observations
The previous methodology took a 60% credit during night hours and 25% credit during daytime hours for all historically available headroom. Minimal credit was taken during daytime hours as there was uncertainty RTC+B would impact available headroom.
When reviewing headroom post RTC+B implementation ERCOT observed a shift in online capacity to offline capacity which was an expected outcome of RTC+B. That said, ERCOT has also seen an increase in online available headroom during daytime hours due to increased solar penetration.
With a shift moving to offline headroom, ERCOT continues to see available offline capacity that can be brought on within 30 minutes.
Considering available Energy Storage Resource capacity, ERCOT observed headroom increase in all hours which is primarily due to increase installed capacity over the year. There is some lower availability in ESR during evening hours, as they are depleted to cover the net load ramp.
Current projections indicate the ESR will continue to increase into 2027, which allows for further certainty that risk credits can be increased on ESR.
These observations for all categories of headroom have shown that an increased credit can be taken in comparison to last years methodology.
Key Takeaway: ERCOT analysis indicates that there is typically headroom available in comparison to last year’s methodology credit allowance, primarily due to growth installed solar and ESR capacity. Evening net load ramp hours show lower levels of headroom as ESRs are depleted to cover the period. ERCOT expects to monitor these hour closely in 2027 to inform the 2028 methodology.

## Slide 11: ESR Capacity Is Also Growing — but So Is Load
Key Takeaway: Installed ESR capacity is growing, increasing headroom; load growth will consume some of it — which is why the proposed credit does not rely on 100% of available headroom.

## Slide 12: Summary of Feedback on Parameters & Perspective
Issue | ERCOT’s Recommendation and Summary of Stakeholder Feedback | ERCOT’s Perspective
How far ahead to look at forecast error and forced outages of conventional resources? Parameter X (in hours) | 6 Hours (ERCOT) OR 3 Hours (IMM) | Lowering look-ahead period would reduce overall amount of ECRS + Non-Spin quantities but would likely increase number of RUCs needed.
What is the level of risk ERCOT should try to avoid by procuring AS to cover forecast error? Parameter ZZ (in MW) | 3,000 i.e. Watch (ERCOT) OR Or 1,500 ie Load Shed (IMM) | The target reserve level is fundamentally a question for the Commission. ERCOT has noticed minimal difference in outcomes between ZZ = 3,000, 2,500 and 1,500 MW since quantities for most hours are a function of the amount of Reg Up plus RRS that these reserves have to replace.
What level of minimum reserves (Reg+RRS) should be maintained? Parameter YY (in %) | 100% (ERCOT) OR Less than 100% (IMM) | ERCOT proposes full restoration of deployed Reg Up + RRS. With that requirement, changing the target reserve level from Watch to EEA or Load Shed may not materially reduce quantities in many hours because Reg Up + RRS restoration often controls the requirement. Restoration of these fast-response reserves is critical to maintaining reliability and supporting compliance with NERC BAL requirements.
How much should we discount the AS quantities for a particular time period based on the “extra” headroom from resources that were historically committed by market in that time period? Parameter Y (in %), W (in hours) | Online:60% in Night and 50% in Day Offline:60% in Night and 50% in Day ESR:60% in Night and 60% in Day Sustainable for 4 hours OR 0 % Credit (Generators) OR 100% Credit and 1 Hour duration (IMM) | ERCOT has observed that although RTC+B has had an impact on available (online + offline) headroom capacity, ERCOT is observing additional capacity available that can be accounted for in the model. ERCOT expects the trend of having higher available (online + offline) headroom capacity during night hours to continue.

## Slide 13: 2027 ECRS + Non-Spin Preliminary Quantities Comparison
*2026 data for August onward is not included in the probabilistic model so August through December 2027 are directional and quantities throughout the year may change once that data is included.
Key Takeaway: Among the like-for-like comparisons, the headroom credit is the largest driver of ECRS + Non-Spin quantities (S1 → S2), while the target reserve level has little effect (S2 → S3). Quantities reduce further only in S4, where 100% headroom credit and 0% Reg Up + RRS restoration act together — an extreme ERCOT does not support. Proposed S2 is a measured recommendation.

## Slide 14: New Analysis: Probability of Watch, EEA, and Load Shed by Reserve Level
What ERCOT was also asked to analyze
As part of the PUC's 2024 Ancillary Services Study, ERCOT was asked to analyze the probability of experiencing a Watch, Emergency Alert (EEA), or Load Shed at alternative target reserve levels.
What was done to accomplish this
Utilizing the 756 scenarios generated through the probabilistic model, ERCOT conducted an analysis of the probability of an event. For each scenario, using that scenario's own criteria, the analysis measures how often the residual — its ECRS and Non-Spin, less risk after the risk credit is applied — fell below the Watch (PRC < 3,000 MW), EEA1, and EEA3 thresholds, expressed as a probability and as expected hours per year. The reserve results for each scenario are provided in the accompanying HTML files.
Key takeaway: This analysis shows how each scenario performs against its own criteria, but it is not a sound basis for comparing the relative reliability impact across scenarios. The next slide shares additional analysis developed to make that comparison.
Probability analysis requested in the 2024 AS Study

## Slide 15: Comparing Scenarios: Total Requirement vs. Reliability Benefit
The results from the analysis described on the prior slide are not directly comparable, because each scenario is measured against its own risk after applying the risk credit. To compare these scenarios in a manner that allows understanding cost vs. benefit of the reserve levels from each scenario, ERCOT re-scored every scenario against a single common risk* outlook.
Key takeaway: Each scenario reflects a different set of parameter choices — the headroom credit, the look-ahead risk basis (6, 4, or 3 hours), and the target reserve threshold (3,000, 2,500, or 1,500 MW) — which drive its reserve level. Weighed against the highest risk tested, lower-reserve scenarios show more expected hours below the Watch and EEA thresholds and higher-reserve scenarios show fewer. No credit (square) sits at the highest reserves; the IMM's proposal (diamond) at the lowest; ERCOT's proposal (star) in between.

## Slide 16: Comparing Scenarios: Total Requirement vs. Reliability Benefit, Contd.
Building on the reliability considerations discussed earlier, in this view, ERCOT has narrowed down the comparison to focus on the impact of a few parameters while holding others steady. Specifically, 100% Reg Up + RRS restoration, the 6-hour-ahead forecast-error and forced outage basis, and the 1-in-10 reliability standard are held steady. What varies is the headroom credit and the target reserve threshold (3,000 / 2,500). Each scenario is then scored against a three variations of 6-hour-ahead risk bases, so that scenarios can be assessed under equivalent conditions.
Key Takeaway: ERCOT's proposed 60% headroom credit is a measured choice. The target reserve threshold is a secondary lever, with limited effect on total quantities. Lowering the target reserve threshold from 3,000 to 2,500 MW reduces total quantities only modestly (65.3M to 65.0M MWh).
Parameters used to compute ECRS + Non-Spin* |  | Total AS (MWh) | Total AS Cost ($) | Risk Tested: 6 Hour Ahead Risk |  |  |  |  | 
 |  |  |  | Expected EEA3 Hours / Year |  |  | Expected EEA1 Hours / Year |  | 
 |  |  |  | No Headroom (Highest Risk) | Some Headroom** | Lots of Headroom*** | No Headroom (Highest Risk) | Some Headroom** | Lots of Headroom***
Headroom/Risk Credit (Y) | Target Reserve Threshold (ZZ, MW) |  |  |  |  |  |  |  | 
0% | 3,000 | 82.01M | $244.03M | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00
60% | 3,000 | 65.30M | $208.97M | 48.48 | 0.00 | 0.00 | 179 | 0.01 | 0.00
100% | 3,000 | 55.45M | $187.16M | 261.72 | 0.16 | 0.00 | 634 | 4.0 | 0.00
0% | 2,500 | 82.32M | $243.75M | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00
60% | 2,500 | 65.00M | $208.18M | 53.60 | 0.00 | 0.00 | 194 | 0.01 | 0.00
100% | 2,500 | 55.41M | $187.31M | 274.39 | 0.22 | 0.00 | 667 | 4.6 | 0.00
*Parameters that were held constant: Forecast error and forced outages (X) = 6 Hours; Reliability Standard (1-in-XX), = 10 years; Reg Up + RRS restoration (YY) = 100%; and ESR Duration in Risk Credit (W) = 4-hour **6 Hour Ahead risk basis adjusted to reflect 60% historic headroom. ***6 Hour Ahead risk basis adjusted to reflect 100% historic headroom. |  |  |  |  |  |  |  |  | 

## Slide 17: Summary and Next Steps
Below is a summary of the proposed changes to the methodology used for computing minimum AS quantities for 2027,
  No changes to the methodology to compute Regulation Service and RRS. Minimum RRS-PFR limit changes has not been published, and quantities utilize 1,377 MW but is expected to change slightly*; and
  Use a probabilistic model to establish quantities of ECRS and Non-Spin, with a measured update to the risk credit parameter in the probabilistic model for ECRS and Non-Spin, reflecting increased historic headroom from RTC+B and growth in installed solar and ESR capacity.
ERCOT thanks Market Participants, the IMM, and PUC Staff for their engagement and support throughout this work.
ERCOT is seeking endorsement on ERCOT’s proposed methodology for computing minimum AS quantities for 2027.
* An updated value is expected to be included in the September Board materials.
Remaining 2027 Methodology Review Timeline
September 15, 2026 – BoD
Nov, Dec 2026 – PUC

## Slide 18: Questions?
JoseLuis.Hinojosa@ercot.com