| Date: | September 7, 2026 |
| --- | --- |
| To: | Board of Directors |
| From: | Caitlin Smith, Technical Advisory Committee (TAC) Chair |
| Subject: | Revision Requests with Opposing Votes Recommended by TAC for Approval |

## Issue for the ERCOT Board of Directors

ERCOT Board of Directors Meeting Date: September 14 – 15, 2026 Item No.: 17.1

Issue: Consideration of the Planning Guide Revision Request (PGRR) 144, Dynamic Model Submission and Review Requirements for Large Loads including Large Computational Loads, recommended for approval by TAC (with opposing votes recorded).

Background/History: Unless otherwise noted: (i) all Market Segments participated in each vote; (ii) for NPRRs, ERCOT Credit Staff and the Credit Finance Sub Group (CFSG) have reviewed the NPRR and do not believe it requires changes to credit monitoring activity or the calculation of liability. Board Review is required of all TAC Reports and Impact Analyses (Protocol Section 21.3.10). - PGRR144, Dynamic Model Submission and Review Requirements for Large Loads including Large Computational Loads Sponsor: ERCOT Revision Description: This PGRR clarifies requirements for submitting dynamic model data for Large Loads to ensure accurate representation of each Large Load in ERCOT’s models, requiring formats compatible with PSS/E, PSCAD, and TSAT. This PGRR also requires model quality tests demonstrating voltage ride-through capability for all Large Loads and converter model validation reports benchmarking PSCAD models against actual hardware tests for all Large Computational Loads (LCLs), ensuring high-quality and accurate models; clarifies that material changes to an LCL that could impact ride-through capability must be reviewed through the Large Load Interconnection Study (LLIS) process before implementing the change; clarifies that an Interconnecting Large Load Entity (ILLE) must meet the dynamic data submission requirements before initiating a dynamic stability study; and requires the ILLE to submit updated dynamic models for the “as-built” LCL facility prior to requesting Initial Energization along with documentation identifying any differences from previously submitted model data used in the ERCOT quarterly stability assessment (“QSA”) and an attestation that the as-built data reflect the actual field settings. Impact Analysis: $200K – $250K Annual Recurring Operations and Maintenance (O&M) – 1 FTE Proposed Effective Date: The first of the month following Public Utility Commission of Texas (PUCT) approval TAC Report/Decision: On 8/26/26, TAC voted to recommend approval of PGRR144 as recommended by ROS in the 8/6/26 ROS Report. There were three opposing votes from the Consumer (CMC Steel, Air Liquide, City of Dallas) Market Segment and four abstentions from the Consumer (3) (Residential Consumer, OPUC, City of Eastland) and Independent Retail Electric Provider (IREP) (APG&E) Market Segments. ERCOT Opinion: ERCOT supports approval of PGRR144. ERCOT Market Impact Statement: ERCOT Staff has reviewed PGRR144 and believes the market impact for PGRR144 helps establish critical modeling requirements for Large Loads to identify potential reliability issues early and ensure appropriate mitigation measures are in place. Independent Market Monitor (IMM) Opinion: IMM has no opinion on PGRR144. Key Documents (including comments, ballots, reports and impact analyses)

Key Factors Influencing Issue: The ROS met, discussed the issues, and submitted a report to TAC regarding PGRR144.

Conclusion/Recommendation: As more specifically described above, TAC recommends that the Board recommend approval of PGRR144.

## ELECTRIC RELIABILITY COUNCIL OF TEXAS, INC.

## BOARD OF DIRECTORS RESOLUTION

WHEREAS, after due consideration of the alternatives, the Board of Directors (Board) of Electric Reliability Council of Texas, Inc. (ERCOT) deems it desirable and in the best interest of ERCOT to recommend approval of PGRR144, Dynamic Model Submission and Review Requirements for Large Loads including Large Computational Loads.

THEREFORE, BE IT RESOLVED, that the ERCOT Board hereby recommends approval of PGRR144.

## CORPORATE SECRETARY’S CERTIFICATE

I, Brandon Gleason, Assistant Corporate Secretary of ERCOT, do hereby certify that, at its ___________ meeting, the Board passed a motion approving the above Resolution by ______.

IN WITNESS WHEREOF, I have hereunto set my hand this ___ day of ______________, 2026.

______________________________

Brandon Gleason

Assistant Corporate Secretary