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[bookmark: _Toc235457750]Report Highlights 
The unofficial ERCOT peak load for July 2026 was 91,134 MW and occurred on 07/22/2026 during hour ending 18:00, this is 9,400 MW higher than the July 2025 peak demand of 81,734 MW on 07/30/2025.
On 15-minute settlement interval basis, maximum demand of 91,263 MW occurred on 7/22/2026 during interval ending 17:30 and minimum demand of 51,412 MW occurred on 7/15/2026 during interval ending 04:00.
There were 9 frequency events.
There were no events which required automatic/manual deployment of Load Resources that were controlled by an Under-Frequency Relays.
There were 0 OCNs
There was 1 Advisory issued for a geomagnetic disturbance of K7 until 0100 on 07/05/26.
There was 1 Watch issued due to HRUC not completing for HE18 due to timeline deviation.
There were 0 Emergency Notices.
There were 62 RUC commitments.
A PVGR Generation Record of 35,427 MW was set on 07/30/2026 at 13:33.
The following GTCs saw congestion in July: 
	GTC
	Days Congestion

	East Texas
	31

	Nelson Sharpe - Rio Hondo
	29

	North Edinburg - Lobo
	28

	South Texas Export Pawnee - Spruce
	25

	South Texas Export Pawnee - Tango
	24

	West Texas
	12

	McCamey
	11

	Panhandle
	9

	North - Houston
	8

	South Texas Import Katoen - Lonhill
	2

	Uvalde
	1

	Williamson - Burnet
	1

	Zapata Starr
	1

	Culberson
	1




[bookmark: _Toc235457751]Frequency Control
[bookmark: _Toc235457752]Frequency Events
The ERCOT Interconnection experienced 9 frequency events.
A summary of the frequency events is provided below. The reported frequency events meet one of the following criteria: Delta Frequency is 60 mHz or greater; the MW loss is 350 MW or greater; resource trip event triggered ECRS deployment. Frequency events that have been identified as Frequency Measurable Events (FME) for purposes of BAL-001-TRE-2 analysis are highlighted in blue. When analyzing frequency events, ERCOT evaluates PMU data according to industry standards. Events with an oscillating frequency of less than 1 Hz are inter-area, while higher frequencies indicate local events. Industry standards specify that damping ratio for inter-area oscillations should be 3.0% or greater. For the frequency event listed below, the ERCOT system met these standards and transitioned well after the disturbance. In the case of negative delta frequency, the MW Loss column could refer to load loss.

	Date and Time
	Delta Frequency
	Max/Min Frequency
	[bookmark: RANGE!D1]Duration of Event
	[bookmark: RANGE!E1]PMU Data 
	MW Loss
	Load
	IRR
	Inertia

	
	[bookmark: RANGE!B2](Hz)
	(Hz)
	
	Oscillation Mode (Hz)
	Damping Ratio
	
	(MW)
	% 
	[bookmark: RANGE!J2](MW-s)

	7/3/2026 14:04:33
	0.020
	59.957
	00:04:33
	0.54
	13%
	502
	 80,042 
	50%
	 303,616 

	7/7/2026 19:35:49
	0.026
	59.960
	00:03:53
	0.49
	16%
	658
	 79,529 
	26%
	 329,009 

	7/21/2026 11:35:35
	0.034
	59.961
	00:05:19
	0.41
	12%
	503
	 75,241 
	48%
	 331,000 

	7/21/2026 15:48:02
	0.040
	59.968
	00:05:25
	0.34
	9%
	515
	 86,432 
	41%
	 347,319 

	7/22/2026 13:43:32
	0.035
	59.963
	00:05:59
	0.51
	13%
	615
	 87,798 
	39%
	 351,561 

	7/22/2026 16:33:58
	0.025
	59.960
	00:03:42
	0.37
	10%
	606
	 90,865 
	37%
	 365,941 

	7/29/2026 14:41:34
	0.017
	59.966
	00:03:19
	0.59
	15%
	522
	 86,994 
	46%
	 327,452 

	7/30/2026 14:15:07
	0.017
	59.964
	00:07:39
	0.44
	11%
	467
	 87,119 
	53%
	 327,026 

	7/30/2026 22:40:25
	0.037
	59.974
	00:06:10
	0.57
	14%
	312
	 75,265 
	28%
	 343,896 
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[bookmark: _Toc90113254][bookmark: _Toc90367425](Note: All data on this graph encompasses frequency event analysis based on BAL-001-TRE-2.)

[bookmark: _Toc235457753]Automatic/Manual Load Resource Deployments
There were no events which required automatic/manual deployment of Load Resources that were controlled by an Under-Frequency Relays.

[bookmark: _Toc235457754]Reliability Unit Commitment
ERCOT reports on Reliability Unit Commitments (RUC) monthly. Commitments are reported grouped by operating day and weather zone. The total number of hours committed is the sum of the hours for all the units in the specified region. Additional information on RUC commitments can be found on the MIS secure site at Grid  Generation  Reliability Unit Commitment.
There were 62 RUC commitments.
	Resource Location
	# of Resources
	Operating Day
	Total # of Hours Committed
	 Total MWhs 
	Reason for Commitment

	 NORTH_CENTRAL 
	1
	July 2, 2026
	4
	 1,580.0 
	 E_PASP 

	 NORTH_CENTRAL 
	1
	July 3, 2026
	4
	 1,568.0 
	 Capacity 

	 NORTH_CENTRAL 
	5
	July 5, 2026
	34
	 3,791.9 
	 Capacity, E_PASP 

	 EAST, NORTH_CENTRAL 
	8
	July 6, 2026
	43
	 5,808.8 
	 Capacity 

	 NORTH_CENTRAL 
	2
	July 7, 2026
	13
	 2,320.0 
	 Capacity, MWTRWLV5 

	 EAST 
	2
	July 9, 2026
	8
	 2,688.0 
	 DCDHTVW5 

	 COAST, NORTH, NORTH_CENTRAL 
	10
	July 19, 2026
	61
	 8,458.4 
	 Capacity 

	 NORTH_CENTRAL 
	4
	July 20, 2026
	24
	 2,620.0 
	 Capacity 

	 SOUTH_CENTRAL 
	1
	July 22, 2026
	5
	 2,000.0 
	 E_PASP 

	 NORTH_CENTRAL 
	1
	July 27, 2026
	1
	 375.0 
	 Capacity 

	 EAST, NORTH_CENTRAL 
	9
	July 28, 2026
	61
	 17,149.0 
	 Capacity, DCDHTVW5 

	 NORTH_CENTRAL, SOUTH_CENTRAL, SOUTHERN 
	10
	July 29, 2026
	82
	 17,340.7 
	 Capacity, Capacity AS, E_PASP 

	 NORTH_CENTRAL 
	3
	July 30, 2026
	65
	 13,124.0 
	 Capacity AS 

	 NORTH_CENTRAL, SOUTH_CENTRAL 
	5
	July 31, 2026
	32
	 4,238.8 
	 Capacity AS, E_PASP 





[bookmark: _Toc235457755]IRR, Wind, and Solar Generation as a Percent of Load
[bookmark: _Hlk83634375]The graph below shows the maximum, minimum and average aggregate solar, wind and IRR output as a percentage of total ERCOT load when evaluated as 10-minute averaged intervals, over the past 13 months. Current wind and solar generation and penetration records are listed in the footnote below[footnoteRef:2]. Maximum IRR penetration for July 2026 was 70.90% on 7/25/2026 interval ending 10:10 and minimum IRR penetration for July 2026 was 5.10% on 7/13/2026 interval ending 06:40. [2:  Current Wind Generation Record: 29,031 MW on 06/29/2026 at 02:00 | Current Wind Penetration Record: 69.15% on 04/10/2022 at 01:43
  Current Solar Generation Record: 35,427 MW on 07/30/2026 at 13:33 | Current Solar Penetration Record: 72.74% on 05/02/2026 at 11:28] 

[image: ]
During the hour of peak load for the month, hourly integrated wind generation was 4,653 MW and solar generation was 28,710 MW. The graph below shows the wind and solar penetration percentage during the hour of the peak load in the last 13 months.
[image: ]
    

Lastly, the graph below shows the minimum wind, solar, and IRR output during the peak load hour as a percentage of the daily peak load for every day in the month.

[image: ]
[bookmark: _Toc235457756][bookmark: _Hlk80277108][bookmark: _Hlk130892461]Largest Net-Load Ramps
The net-load ramp is defined as the change in net-load (load minus wind and PVGR generation) during the defined time horizon. Such a variation in net-load needs to be accommodated in grid operations to ensure that the reliability of the grid is satisfactorily maintained. The largest net-load ramps over 5-minute, 10-minute, 15-minute, 30-minute, and 60-minute intervals in July 2026 were 1,706 MW, 2,873 MW, 3,822 MW, 6,941 MW, and 12,588 MW respectively. A comparison with historical values is provided in the table below.

	Month and Year
	5 min
	10 min
	15 min
	30 min
	60 min

	14-Jul
	674 MW
	1,169 MW
	1,589 MW
	2,854 MW
	5,201 MW

	15-Jul
	776 MW
	1,231 MW
	1,754 MW
	3,303 MW
	6,260 MW

	16-Jul
	834 MW
	1,350 MW
	1,881 MW
	3,230 MW
	6,319 MW

	17-Jul
	797 MW
	1,421 MW
	1,953 MW
	3,167 MW
	5,798 MW

	18-Jul
	1,333 MW
	1,854 MW
	2,780 MW
	3,205 MW
	6,604 MW

	19-Jul
	830 MW
	1,460 MW
	2,084 MW
	3,795 MW
	7,375 MW

	20-Jul
	954 MW
	1,536 MW
	2,221 MW
	4,101 MW
	7,690 MW

	21-Jul
	1,323 MW
	1,596 MW
	2,081 MW
	3,614 MW
	6,761 MW

	22-Jul
	977 MW
	1,837 MW
	2,664 MW
	4,529 MW
	7,716 MW

	23-Jul
	1,230 MW 
	1,793 MW 
	2,519 MW 
	4,733 MW 
	8,650 MW 

	24-Jul
	1,128 MW
	2,011 MW
	2,837 MW
	4,671 MW
	7,772 MW

	25-Jul
	1,564 MW
	2,531 MW
	3,7678 MW
	7,116 MW
	12,438 MW

	26-Jul
	1,706 MW
	2,873 MW
	3,822 MW
	6,941 MW
	12,588 MW

	
	7/27/2026
	7/6/2026
	7/20/2026
	7/30/2026
	7/20/2026

	
	(IE 11:21)
	(IE 19:08)
	(IE 19:29)
	(IE 19:18)
	(IE 19:53)

	All Months in 2014-2026
	1,771 MW
	3,107 MW
	4,588 MW
	8,901 MW
	16,522 MW

	
	5/28/2024
	1/29/2024
	1/29/2024
	1/29/2024
	1/29/2024

	
	(IE 19:01)
	(IE 17:05)
	(IE 17:10)
	(IE 17:11)
	(IE 17:17)





[bookmark: _Toc235457757]Congestion Analysis
[bookmark: _Toc235457758]Notable Constraints
[bookmark: _Hlk92804220]Nodal protocol section 3.20 specifies that ERCOT shall identify transmission constraints that are binding in Real-Time three or more Operating Days within a calendar month. As part of this process, ERCOT reports congestion that meets this criterion to ROS. In addition, ERCOT also highlights notable constraints that have an estimated congestion rent exceeding $1,000,000 for a calendar month. These constraints are detailed in the table below, including approved transmission upgrades from TPIT that may provide some congestion relief based on ERCOT’s engineering judgement. Rows highlighted in blue indicate the congestion was affected by one or more outages. For a list of all constraints activated in SCED, please see Appendix A at the end of this report.

	Data Item
	Contingency Name
	Overloaded Element
	Contingency Name
	Overloaded Element
	# of Days Constraint Binding
	Congestion Rent
	Transmission Project

	
	
	
	
	
	
	
	
	

	STP_WAP_STPWAP39_1
	DWPWFWP5
	STPWAP39_1
	TWR(345) WAP-WLF64 & WAP-WLY72
	South Texas Project - Wa Parish 345kV
	25
	$22,566,078.45
	
	

	TMPSW_FRYSW_1715__B
	DSALHUT5
	1715__B
	SALSW - HUTTO 345KV
	Temple Switch - Fryers Creek 138kV
	17
	$10,105,097.03
	Temple Area Project (24RPG001). Note that Fryers Creek is named Boggy Creek in planning cases.
	

	SEA_SEA_SEA_AAT1
	DFRYTM58
	SEA_AAT1
	DOUBLE FRYSW-TMPSW 138 & KNBSW-SALSW 345
	Seaton 138kV
	20
	$8,689,562.07
	
	

	TMPSW_TMPSE_610__B
	DPPRTEC8
	610__B
	PEPPER CREEK SW TO TEMPLE ELM CREEK 138 KV DOUBLE
	Temple Switch - Temple Southeast 138kV
	3
	$8,406,579.68
	
	

	MCNEIL__WELLBR_96T136_1
	DHUTGEA8
	96T136_1
	HUTTO TO RNDRK 138 AND HUTTO TO GEORSO 138 DBLCKT
	Wells Branch - Mcneil 138kV
	2
	$8,070,717.33
	
	

	SAMSW_VENSW_35055__A
	SVENFTS5
	35055__A
	FORT SMITH SWITCH to FORT SMITH SWITCH LIN _B
	Sam Switch - Venus Switch 345kV
	20
	$7,639,766.34
	Venus Switch to Sam Switch 345-kV Line Project (24RPG017)
	

	MGSES_CATSW_6945__A
	SRGRMGS5
	6945__A
	MORGAN CREEK SES to RANGER CAMP SWITCH LIN _A
	Morgan Creek Ses - Cattleman Switch 345kV
	14
	$4,949,105.91
	West Texas 345-kV Infrastructure Rebuild Project (23RPG034)
	

	n/a_n/a_WESTEX
	BASE CASE
	WESTEX
	Basecase
	WESTEX GTC
	7
	$4,537,911.14
	Permian Basin Relibility Plan (765-kV import paths) (The PUCT approved ,helps improve, but not fully exit, the GTC yet.)
	

	NLARSW_PILONCIL_NLARSW_PILONC1_1
	DFOAVLO5
	NLARSW_PILONC1_1
	FOWLERTON to LOBO & AVANZADA
	North Laredo Switch - Piloncillo 138kV
	17
	$3,174,440.05
	
	

	MDO_PHR_MDOPHR99_A
	DWAP_OB5
	MDOPHR99_A
	TWR (345) OB-WAP98 & OB-WAP99
	Meadow - Ph Robinson 345kV
	16
	$2,806,532.52
	CNP_28TPIT103344_PH_Robinson_to_WA_Parish_Hardening (MOD 103344 Phase 103435, 25RPG028)
	

	TYPRK_PLYAM_6200__F
	DCDHTVW5
	6200__F
	TVWSW TO CDHSW 345 AND CDHSW TO VENSW 345 DBLCKT
	Poly-America - Tyre Park Sub 138kV
	14
	$2,770,555.27
	
	

	PALOUSE_WOLFCAMP_PALOUS_WOLFCA1_1
	DBIGSCH5
	PALOUS_WOLFCA1_1
	Big Hill - Schneeman Draw & Big Hill - Schneeman Draw 2
	Palouse - Wolfcamp 138kV
	21
	$2,686,618.72
	
	

	n/a_n/a_NELRIO
	BASE CASE
	NELRIO
	Basecase
	NELRIO GTC
	29
	$2,598,104.98
	The Lower Rio Grande Valley (LRGV) System Enhancement Project (21RPG017)
	

	JN_BI_BI_JN_64_A
	DWAP_BI5
	BI_JN_64_A
	TWR (345) WAP-BI50 & SMITHERS-BI98
	Bellaire - Jeanetta 345kV
	18
	$2,518,527.11
	
	

	LPLMK_LPLNE_LPLMK_LPLNE_1
	SBWDDBM5
	LPLMK_LPLNE_1
	BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1
	Mackenzie Substation - Northeast Substation 115kV
	8
	$2,512,965.18
	
	

	SMITHERS_BI_BI_SMR98_A
	DWAP_JN5
	BI_SMR98_A
	TWR (345) JN-WAP64 & JN-WAP72
	Bellaire - Smithers 345kV
	2
	$2,354,060.48
	
	

	WAP_OB_OB_WAP98_A
	SOBWAP5
	OB_WAP98_A
	WA PARISH to OBRIEN LIN A
	Wa Parish - Obrien 345kV
	11
	$2,336,304.50
	
	

	n/a_n/a_NE_LOB
	BASE CASE
	NE_LOB
	Basecase
	NE_LOB GTC
	20
	$2,279,186.03
	San Antonio South Reliability I Project (22RPG048)
LRGV Transmission Improvement Project (21RPG017)
San Antonio South Reliability II Project (23RPG032)
	

	SEA_SEA_SEA_AAT1
	DFRYBC58
	SEA_AAT1
	DOUBLE KNBSW-SALSW 345 & FRYSW-BELCNTY 138
	Seaton 138kV
	3
	$2,098,744.93
	
	

	n/a_n/a_EASTEX
	BASE CASE
	EASTEX
	Basecase
	EASTEX GTC
	28
	$2,054,622.70
	
	

	COLLEGE_JUPITER_COLLE_JUPIT_1
	SWALNAA8
	COLLE_JUPIT_1
	NAAMAN to NAAMAN LIN 1
	College - Jupiter 138kV
	3
	$2,031,522.28
	GPL_TPIT_110751_WylieSW_LCP_Upgrades_Jupiter_College_Line (MOD 110751)
	

	MEXTP_ITALY_2270__B
	SBLURDH8
	2270__B
	BLUM to RED HILL SWITCH LIN _G
	Milford Exxon Tap - Italy 69kV
	20
	$1,620,574.42
	
	

	MV_HBRG4_MV_WESL4_WESLCO_HIDLBRG_1
	MHARNED5
	WESLCO_HIDLBRG_1
	Manual dbl ckt for NEDIN-BONILLA 345kV & RIOH-PRIM138kV
	Heidelburg Sub - Weslaco Sub 138kV
	20
	$1,614,159.44
	STEC_71928_Heidelberg_AEPWeslaco_Upgrade (MOD 71928)
	

	BALLINGE_BALLINGE_BALLINGE_FMRL
	SCOLBAL8
	BALLINGE_FMRL
	BALLINGER to COLEMAN LAKE IVIE TAP LIN 1
	Ballinger 69kV
	5
	$1,361,943.12
	
	

	LPLNW_LPLMD_LPLNW_LPLMD_1
	SBWDDBM5
	LPLNW_LPLMD_1
	BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1
	Northwest Substation - Mcdonald Substation 115kV
	3
	$1,303,618.88
	
	

	ZEN_THW_THWZEN98_A
	DRNS_TB5
	THWZEN98_A
	Rns-Rtw & Sng-Tb 345kV
	Th Wharton - Zenith 345kV
	9
	$1,278,093.25
	
	

	LONG_LIPAN_MIL_LIPAN_1
	SGRSMNW8
	MIL_LIPAN_1
	GRINDSTONE SWITCH to MILLER LIN _C
	Lipan - Long 138kV
	5
	$1,238,096.46
	
	

	TREADWEL_YELWJCKT_TREADW_YELWJC1_1
	DBIGKEN5
	TREADW_YELWJC1_1
	Bighil-Kendal 345kV
	Yellow Jacket - Treadwell 138kV
	15
	$1,235,839.94
	
	

	NEWMAN_WALNUT1_NEWM_WAL_1
	SOAKSHI8
	NEWM_WAL_1
	OAKLAND SUBSTATION to SHILOH LIN 1
	Newman - Walnut 138kV
	6
	$1,139,066.46
	
	

	HLSES_RMTPW_6405__C
	DHLSLIG8
	6405__C
	HLSES TO EVRSW 138 AND HLSES TO LIGSW 138 DBLCKT
	Handley Ses - Randol Mill Tap West 138kV
	3
	$1,072,991.73
	
	

	PGTP1_PDSES_3610__G
	MWTRWLV5
	3610__G
	MANUAL WTRML-WLVEE&WTRML-SARRD 345 DBLCKT
	Parkdale Switch - Pleasant Grove Tap 1 138kV
	3
	$1,044,638.06
	
	

	SOLSTICE_SOLSTICE_SOLSTICE_PST1
	DBAKSOL5
	SOLSTICE_PST1
	Bakersfield - Solstice line 1 and 2
	Solstice 138kV
	13
	$1,001,186.66
	Fort Stockton Switch: Expand 345 kV Station (MOD 93226)
	

	VICTORIA_MAGRUDER_MAGRUD_VICTOR2_1
	XVIC89
	MAGRUD_VICTOR2_1
	VICTORIA TRX 69A2 138/69
	Magruder - Victoria 138kV
	6
	$822,146.08
	
	

	MARSW_DEVIT_6293__C
	DEVRHLS8
	6293__C
	EVRSW TO HLSES 138 DBLCKT
	Marrs Switch - Devitt Sub 138kV
	4
	$808,339.74
	
	

	n/a_n/a_PNHNDL
	BASE CASE
	PNHNDL
	Basecase
	PNHNDL GTC
	5
	$803,246.92
	
	

	HOWARD_LEON_CRK_D5_S1_1
	SP5CAG8
	D5_S1_1
	CAGNON to CAGNON LIN 1
	Leon Creek - Howard 138kV
	15
	$802,742.20
	
	

	FLTSW_PRSSW_1545__A
	SPRSPAR8
	1545__A
	PARIS SWITCH to PARIS LIN _A
	Paris Switch - Flying Tiger Switch 138kV
	21
	$781,103.29
	
	

	CRDSW_OLNEY_6830__B
	DGRMGRS8
	6830__B
	FIREROCK TO BRNWD 138 AND FIREROCK TO BANGS 69 DBLCKT
	Cottonwood Road Switch - Olney Pod 69kV
	12
	$726,946.31
	
	

	WAP_OB_OB_WAP99_A
	SOBWA2P5
	OB_WAP99_A
	WA PARISH to OBRIEN LIN A
	Wa Parish - Obrien 345kV
	4
	$662,416.03
	
	

	PALOUSE_WOLFCAMP_PALOUS_WOLFCA1_1
	DBIGKEN5
	PALOUS_WOLFCA1_1
	Bighil-Kendal 345kV
	Palouse - Wolfcamp 138kV
	11
	$590,279.86
	
	

	BRUNI_BRUNI_BRUNI_69_1
	DFOAVLO5
	BRUNI_69_1
	FOWLERTON to LOBO & AVANZADA
	Bruni Sub 138kV
	7
	$580,200.81
	
	

	SCRCV_KNAPP_6437__F
	DMTSCOS5
	6437__F
	DMTSW TO SCOSW 345 DBLCKT
	Knapp - Scurry Chevron 138kV
	7
	$542,470.14
	
	

	HECKER_RESNIK_HECKER_RESNIK1_1
	DMCDUPS8
	HECKER_RESNIK1_1
	MCCAMPBE - RESNIK & I_DUPSW 138kV
	Hecker - Resnik 138kV
	11
	$523,418.33
	
	

	SALDS_SONTERRA_1710__A
	DSALHUT5
	1710__A
	SALSW - HUTTO 345KV
	Salado South - Sonterra 138kV
	6
	$470,143.60
	
	

	CMNSW_CMNTP_651__B
	SCMNCPS5
	651__B
	COMANCHE SWITCH (Oncor) to COMANCHE PEAK SES LIN _A
	Comanche Tap - Comanche Switch (Oncor) 138kV
	8
	$464,403.32
	
	

	CMNSW_CMNTP_651__B
	DMBDRKC5
	651__B
	MBDSW-CMBSW & MBDSW-RKCRK 345_DBLCKT
	Comanche Tap - Comanche Switch (Oncor) 138kV
	8
	$454,297.99
	
	

	n/a_n/a_E_PASP
	BASE CASE
	E_PASP
	Basecase
	E_PASP GTC
	18
	$454,103.73
	
	

	NUECES_B_WHITE_PT_NUECES_WHITE_2_1
	SMAYWHI8
	NUECES_WHITE_2_1
	GILA to MAYO LIN 1
	Nueces Bay - Whitepoint 138kV
	11
	$428,414.57
	
	

	PAWNEE_CALAVERS_PAWNEE_SPRUCE_1
	DELMSAN5
	PAWNEE_SPRUCE_1
	Elmcreek-Sanmigl 345kV
	Pawnee Switching Station - Calaveras 345kV
	10
	$416,961.38
	
	

	NORTMC_CROSSOVE_CROSSO_NORTMC1_1
	DBIGSCH5
	CROSSO_NORTMC1_1
	Big Hill - Schneeman Draw & Big Hill - Schneeman Draw 2
	North Mccamey - Crossover 138kV
	9
	$374,266.42
	
	

	VICTORIA_MAGRUDER_MAGRUD_VICTOR2_1
	DELMSAN5
	MAGRUD_VICTOR2_1
	Elmcreek-Sanmigl 345kV
	Magruder - Victoria 138kV
	8
	$359,774.24
	
	

	WLY_WAP_WAPWLY72_A
	DOASSEB5
	WAPWLY72_A
	TWR(345) DOW-OAS 18 & OAS-SEB 27
	Wa Parish - Whaley 345kV
	4
	$322,057.67
	
	

	CATARINA_ASHERTON_ASHERT_CATARI1_1
	DFOAVLO5
	ASHERT_CATARI1_1
	FOWLERTON to LOBO & AVANZADA
	Asherton - Catarina 138kV
	10
	$301,467.46
	
	

	n/a_n/a_MCCAMY
	BASE CASE
	MCCAMY
	Basecase
	MCCAMY GTC
	8
	$298,592.02
	
	

	ESCONDID_GANSO_ESCOND_GANSO1_1
	SBRAHAM8
	ESCOND_GANSO1_1
	BRACKETTVILLE to HAMILTON ROAD LIN 1
	Escondido - Ganso 138kV
	7
	$287,348.42
	
	

	TNNALVIN_ALVIN_138_ALV_NAL_1
	SMDOPHR5
	138_ALV_NAL_1
	MEADOW to PH ROBINSON LIN A
	North Alvin Tnp - Alvin Tnp 138kV
	11
	$284,310.82
	
	

	SNDSW_SNDSW_SNDSW_MR1H
	MSNDWCR5
	SNDSW_MR1H
	MANUAL SANDOW SW TO WALLEYE CREEK SW
	Sandow Switch 345kV
	3
	$278,404.22
	
	

	WLY_WAP_WAPWLY72_A
	DBLW2JC5
	WAPWLY72_A
	TWR (345) JCK-WAT62 & BLY-JCK57
	Wa Parish - Whaley 345kV
	9
	$269,816.04
	
	

	SAMSW_FVLSW_35045__A
	MBULNAV5
	35045__A
	Mnaual single contingency BULLOCK-NAVARRO 345kV
	Sam Switch - Files Valley Switch 345kV
	7
	$260,491.74
	
	

	RS_FB_FB_RS_60_A
	SWAATH8
	FB_RS_60_A
	Athena to WALLIS LIN A
	Fort Bend - Rosenberg 138kV
	7
	$230,753.90
	
	

	BCESW_SNDSW_421__A
	SSNDBGR5
	421__A
	SANDOW SWITCH to BADGER SWITCH LIN _A
	Sandow Switch - Bell County East Switch 345kV
	8
	$230,446.68
	
	

	STP_WAP_STPWAP39_1
	DBLBYWF5
	STPWAP39_1
	TWR (345) BLU-BLY72 & HLJ-WLF64
	South Texas Project - Wa Parish 345kV
	4
	$221,068.61
	
	

	ENWSW_TMPTN_940__A
	SPEBTRU8
	940__A
	GAMMA to GAMMA LIN _D
	Ennis West Switch - Templeton 138kV
	12
	$210,947.50
	
	

	GN_PZ_GN_PZ_08_A
	SMDOOAS5
	GN_PZ_08_A
	MEADOW to OASIS LIN A
	Grant - Plaza 138kV
	3
	$209,868.46
	
	

	FRONTERA_S_MISSIN_BENTS_FRTER_1B_1
	SSHAFRO8
	BENTS_FRTER_1B_1
	FRONTERA to SHARYLAND LIN 1
	Frontera - South Mission 138kV
	10
	$206,668.07
	
	

	ASHERTON_CATARINA_ASHERT_CATARI1_1
	DLOFOAV5
	ASHERT_CATARI1_1
	Double LOBO - FOWLERTON & AVANZADA
	Asherton - Catarina 138kV
	4
	$189,994.64
	
	

	PEARSALL_POTEETS_POT_PEAR_1
	SMOOPEA8
	POT_PEAR_1
	MOORE SWITCHING STATION to MOORE SWITCHING STATION LIN 1
	Poteet Sub - Pearsall Switching Station 69kV
	5
	$186,111.73
	
	

	FORTMA_YELWJCKT_FORTMA_YELWJC1_1
	DBIGKEN5
	FORTMA_YELWJC1_1
	Bighil-Kendal 345kV
	Yellow Jacket - Fort Mason 138kV
	10
	$185,310.90
	
	

	MEXTP_ITALY_2270__B
	SBLAWDB8
	2270__B
	BLANTON to WOODBURY SWITCH LIN _C
	Milford Exxon Tap - Italy 69kV
	13
	$172,825.64
	
	

	CRDSW_OLNEY_6830__B
	SGRMGRS8
	6830__B
	GRAHAM EAST to GRAHAM EAST LIN _A
	Cottonwood Road Switch - Olney Pod 69kV
	4
	$155,695.59
	
	

	RS_FB_FB_RS_60_A
	SEBATH8
	FB_RS_60_A
	Athena to EAST BERNARD LIN A
	Fort Bend - Rosenberg 138kV
	4
	$155,134.28
	
	

	REVEILLE_COTULLA_COTULL_REVEIL1_1
	DFOWSMG5
	COTULL_REVEIL1_1
	FOWLRTON TO SAN MIGUEL DOUBLE CIRCUIT CONTINGENCY
	Cotulla - Reveille 138kV
	8
	$146,785.25
	
	

	SOLSTICE_SOLSTICE_SOLSTICE_PST1
	STARLEO8
	SOLSTICE_PST1
	LEON CREEK TNP to TARBUSH TNP LIN 1
	Solstice 138kV
	7
	$139,178.65
	
	

	BERGHE_BERGHE_BERGHE_AT1H
	DZORHAY5
	BERGHE_AT1H
	ZORN - HAYSEN 345KV
	Bergheim 345kV
	6
	$136,345.69
	
	

	CMNSW_CMNTP_651__B
	DBUCRGP5
	651__B
	MANUAL DOUBLE RGPSW - KLNSW 345 KV & BUCSW - KLNSW 345 KV
	Comanche Tap - Comanche Switch (Oncor) 138kV
	4
	$135,664.12
	
	

	BGRSW_SNDSW_455__A
	SBCESN35
	455__A
	BELL COUNTY EAST SWITCH to BELL COUNTY EAST SWITCH LIN _A
	Badger Switch - Sandow Switch 345kV
	9
	$133,356.67
	
	

	BRUNI_BRUNI_BRUNI_69_1
	SLAQLOB8
	BRUNI_69_1
	LAQUINTA to LOBO LIN 1
	Bruni Sub 138kV
	16
	$131,593.78
	
	

	DPREA_RCSES_1561__A
	DVLSPAC5
	1561__A
	VLSES-PACSW 345&PRSSW-VLYSO 345 DBLCKT
	Rivercrest Ses - Deport Rea 138kV
	4
	$113,554.98
	
	

	NVKSW_ANARN_6840__B
	DMGSRIC8
	6840__B
	DBL_CKT_GRSES-RICSW_138 kV and GRSES-SGRAS_138 kV
	Anarene - Navy Kickapoo Switch 69kV
	7
	$106,618.34
	
	

	n/a_n/a_E_PATA
	BASE CASE
	E_PATA
	Basecase
	E_PATA GTC
	7
	$98,518.19
	
	

	HONDOCK_DEVINESW_HON_DEVI_1
	SHONF38
	HON_DEVI_1
	HONDO to HONDO CREEK SWITCHING STATION LIN 1
	Hondo Creek Switching Station - Devine Switch 69kV
	6
	$70,565.33
	
	

	TWINBU_HARGROVE_HARGRO_TWINBU1_1
	DBAKCED5
	HARGRO_TWINBU1_1
	BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV
	Hargrove - Twin Buttes 138kV
	3
	$65,810.45
	
	

	ESCONDID_GANSO_ESCOND_GANSO1_1
	SBRAPIN8
	ESCOND_GANSO1_1
	BRACKETTVILLE to BRACKETTVILLE LIN 1
	Escondido - Ganso 138kV
	5
	$62,197.20
	
	

	ENWSW_SHKSW_943__B
	SENSENW8
	943__B
	ENNIS SOUTH to ENNIS SOUTH LIN _C
	Shankle Switch - Ennis West Switch 138kV
	7
	$59,397.74
	
	

	DILLEYSW_DILLEYSW_DILLEYSW_XF1H
	DDILCOT8
	DILLEYSW_XF1H
	Dilleysw-Sanmgsw&Cotulas 138kV
	Dilley Switch Aep 138kV
	3
	$57,185.70
	
	

	BLESSING_PAVLOV_BLESSI_PAVLOV1_1
	SSTPESP8
	BLESSI_PAVLOV1_1
	STP SWITCH to Esperanza LIN 1
	Blessing - Pavlov 138kV
	4
	$54,058.19
	
	

	YELWJCKT_FORTMA_FORTMA_YELWJC1_1
	DBIGKEN5
	FORTMA_YELWJC1_1
	Bighil-Kendal 345kV
	Yellow Jacket - Fort Mason 138kV
	10
	$49,832.84
	
	

	SONR_ATSO_ATSO_SONR1_1
	SCARFRI8
	ATSO_SONR1_1
	Carver to Carver LIN 1
	Atlantic Sonora - Sonora 69kV
	3
	$48,239.63
	
	

	MADDUX_TREADWEL_MADDUX_TREADW1_1
	DBIGKEN5
	MADDUX_TREADW1_1
	Bighil-Kendal 345kV
	Maddux - Treadwell 138kV
	6
	$44,826.02
	
	

	FTST_SOLSTICE_FTST_SOLSTI1_1
	BASE CASE
	FTST_SOLSTI1_1
	Basecase
	Fort Stockton Plant - Solstice 138kV
	3
	$41,255.73
	
	

	PALOUSE_CROSSOVE_CROSSO_PALOUS1_1
	SWOLPAL8
	CROSSO_PALOUS1_1
	PALOUSE to Wolfcamp LIN 1
	Crossover - Palouse 138kV
	4
	$29,011.08
	
	

	SN_STR_SN_STR26_A
	SVLGLO8
	SN_STR26_A
	VELASCO to GLOBAL LIN A
	Sintek - Stratt 138kV
	3
	$22,932.31
	
	

	DOWNIES_DOWNIES_DOWNIES_AX1H
	DRAZSA89
	DOWNIES_AX1H
	Double Circuit RAZORBAC to DRYFRIO 138 kV & UVALDE to SABINAL 69 kV
	Downie Switching Station 138kV
	3
	$22,641.78
	
	

	FRONTERA_S_MISSIN_BENTS_FRTER_1B_1
	SBENS_M8
	BENTS_FRTER_1B_1
	SOUTH MCALLEN to BENTSEN LIN 1
	Frontera - South Mission 138kV
	14
	$22,482.01
	
	

	FTST_LEONCRK_138_FTS_LNC_1
	BASE CASE
	138_FTS_LNC_1
	Basecase
	Leon Creek Tnp - Fort Stockton Plant 138kV
	13
	$21,032.28
	
	

	FURHMAN_MOURSUND_MOURSUND_FUR_1
	SFURVAN8
	MOURSUND_FUR_1
	FURHMAN to VANDERBILT SWITCHING STATION LIN 1
	Moursund - Furhman 138kV
	17
	$20,403.70
	
	

	LEONCRK_FTST_138_FTS_LNC_1
	STARLEO8
	138_FTS_LNC_1
	LEON CREEK TNP to TARBUSH TNP LIN 1
	Leon Creek Tnp - Fort Stockton Plant 138kV
	5
	$19,605.99
	
	

	WLVSW_GAILS_6217__A
	SVEAW_L5
	6217__A
	wett_long_draw to VEALMOOR - Sharyland Utilities LIN 1
	Willow Valley Switch - Gail Sub 138kV
	3
	$12,133.39
	
	

	IH20_TNCOLIET_138_IH2_COT_1
	SSTAWIC8
	138_IH2_COT_1
	STAGHORN TNP to WICKETT TNP LIN 1
	Ih 20 Tnp - Collie Field Tap Tnp 138kV
	17
	$11,824.04
	
	

	LA_PALMA_HAINE_DR_HAINE__LA_PAL1_1
	SRAYRI38
	HAINE__LA_PAL1_1
	LAS PULGAS to RAYMONDVILLE 2 LIN 1
	Haine Drive - La Palma 138kV
	4
	$10,885.01
	
	

	WC_WCOLMAIN__WC_WCO_1
	SWCOW2C8
	_WC_WCO_1
	WEST COLUMBIA MAIN TNP to WEST COLUMBIA LIN 1
	West Columbia Main Tnp - West Columbia 138kV
	9
	$9,621.89
	
	

	DOWNIES_DOWNIES_DOWNIES_AX1H
	SREAUVA8
	DOWNIES_AX1H
	Reading to Reading LIN 1
	Downie Switching Station 138kV
	5
	$8,159.29
	
	

	ANGLETON_WCOLLOCL_G138_15_1
	SWCOWCO8
	G138_15_1
	WEST COLUMBIA MAIN TNP to ANGLETON TNP LIN 1
	West Columbia Local Tnp - Angleton Tnp 138kV
	19
	$7,185.89
	
	

	YELWJCKT_HEXT_HEXT_YELWJC1_1
	SJUNYEL9
	HEXT_YELWJC1_1
	MENARD PHILLIPS TAP to MENARD PHILLIPS TAP LIN 1
	Yellow Jacket - Hext Lcra 69kV
	7
	$5,560.31
	
	

	YELWJCKT_HEXT_HEXT_YELWJC1_1
	DYETRJU8
	HEXT_YELWJC1_1
	Double for YellowJacket - Treadwell & Junction
	Yellow Jacket - Hext Lcra 69kV
	10
	$5,377.78
	
	

	LON_HILL_CLARK_WD_CLARK__LON_HI1_1
	SCITWEI8
	CLARK__LON_HI1_1
	CHAMPLIN to CHAMPLIN LIN 1
	Clarkwood - Lon Hill 138kV
	7
	$5,360.76
	
	

	FTST_LEONCRK_138_FTS_LNC_1
	DTNFBCA8
	138_FTS_LNC_1
	TNFXTAIL TO TARBUSH to BCATOKA 138KV
	Leon Creek Tnp - Fort Stockton Plant 138kV
	5
	$5,182.14
	
	

	GANSO_ESCONDID_ESCOND_GANSO1_1
	SBRAPIN8
	ESCOND_GANSO1_1
	BRACKETTVILLE to BRACKETTVILLE LIN 1
	Escondido - Ganso 138kV
	5
	$5,075.45
	
	

	FRONTERA_S_MISSIN_BENTS_FRTER_1B_1
	SPALFRO8
	BENTS_FRTER_1B_1
	FRONTERA to KEY SWITCH LIN 1
	Frontera - South Mission 138kV
	4
	$4,488.93
	
	

	FTST_LEONCRK_138_FTS_LNC_1
	SSOAHOL8
	138_FTS_LNC_1
	SOAPTREE TNP to HOLIDAY SUB TNP LIN 1
	Leon Creek Tnp - Fort Stockton Plant 138kV
	4
	$2,091.02
	
	

	WLVSW_GAILS_6217__A
	SBUZHMP8
	6217__A
	BUZZARD DRAW SWITCH to HARDY MORGAN POI LIN _B
	Willow Valley Switch - Gail Sub 138kV
	4
	$1,857.71
	
	



[bookmark: _Toc235457759][bookmark: _Hlk219801104]Generic Transmission Constraint Congestion
	GTC
	Days Congestion

	East Texas
	31

	Nelson Sharpe - Rio Hondo
	29

	North Edinburg - Lobo
	28

	South Texas Export Pawnee - Spruce
	25

	South Texas Export Pawnee - Tango
	24

	West Texas
	12

	McCamey
	11

	Panhandle
	9

	North - Houston
	8

	South Texas Import Katoen - Lonhill
	2

	Uvalde
	1

	Williamson - Burnet
	1

	Zapata Starr
	1

	Culberson
	1



There was no activity on the remaining GTCs during the month.
Note: This is how many times a constraint has been activated to avoid exceeding a GTC limit, it does not imply an exceedance of the GTC occurred or that the GTC was binding.
[bookmark: _Toc235457760][bookmark: _Hlk164677736]Manual Overrides
· None
[bookmark: _Toc235457761]Congestion Costs for Calendar Year 2026
The following table represents the top twenty active constraints for the calendar year based on the estimated congestion rent attributed to the congestion. ERCOT updates this list on a monthly basis.
	Contingency
	Overloaded Element
	# of 5-min SCED
	Estimated
	Transmission

	Basecase
	WESTEX GTC
	16,629
	97,011,822.87
	Permian Basin Relibility Plan (765-kV import paths) (The PUCT approved ,helps improve, but not fully exit, the GTC yet.)

	MANUAL HCKSW-RAMSW 345 kV_2
	Hicks Switch 138kV
	1,363
	51,703,803.38
	

	BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV
	Longshore Switch - Prairieland Switch 345kV
	13,078
	50,084,697.46
	Oncor_FW_81268_Longshore – Consavvy 345 kV Double-Circuit Line Rebuild (MOD 81268)

	TWR(345) WAP-WLF64 & WAP-WLY72
	South Texas Project - Wa Parish 345kV
	6,500
	37,872,522.05
	

	Basecase
	EASTEX GTC
	8,733
	35,476,046.68
	

	MANUAL RNKSW TO DHMSW 345&KRWSW TO DHMSW 345 DBLCKT
	Argyle - Highlands Tnp 138kV
	6,658
	34,162,852.87
	

	SALSW TO KLNSW 345 DBLCKT
	Killeen Switch - Stagecoach 138kV
	2,796
	31,304,486.27
	ONCOR_SE_87703_Belton_Killeen_138 kV Line (via Nolanville) (MOD 87703, 24RPG001)

	BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1
	Mackenzie Substation - Northeast Substation 115kV
	7,908
	28,970,921.60
	

	DOUBLE NVARO-LEG & NVARO-OUTSW 345 KV
	Big Brown Ses - Jewett 345kV
	504
	26,063,843.65
	ONCOR_SE_99622_PIN_OAK_SWITCH (MOD 99622, 25RPG004)

	MORGAN CREEK SES to RANGER CAMP SWITCH LIN _A
	Morgan Creek Ses - Cattleman Switch 345kV
	4,253
	24,313,709.09
	West Texas 345-kV Infrastructure Rebuild Project  (23RPG034)

	BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV
	Hargrove - Twin Buttes 138kV
	4,915
	23,123,991.35
	

	Basecase
	Omega - Horse Hollow Generation Tie 345kV
	9,100
	21,147,903.99
	

	DMTSW TO SCOSW 345 DBLCKT
	Knapp - Scurry Chevron 138kV
	11,350
	21,126,587.99
	Oncor_FW_102849_Union 138 kV Switch (MOD 102849)

	Basecase
	NE_LOB GTC
	20,101
	20,723,375.13
	San Antonio South Reliability I Project (22RPG048)
LRGV Transmission Improvement Project (21RPG017)
San Antonio South Reliability II Project (23RPG032)

	FORT SMITH SWITCH to FORT SMITH SWITCH LIN _B
	Sam Switch - Venus Switch 345kV
	3,657
	20,598,006.36
	Venus Switch to Sam Switch 345-kV Line Project (24RPG017)

	Basecase
	E_PASP GTC
	9,798
	20,461,803.10
	San Antonio South Reliability I Project (22RPG048)
LRGV Transmission Improvement Project (21RPG017)
San Antonio South Reliability II Project (23RPG032)

	SALSW TO KLNSW 345 DBLCKT
	Harker Heights South - Killeen Switch 138kV
	3,820
	17,819,511.40
	ONCOR_SE_87699_Belton - Killeen 138 kV_Line (MOD 87699, 24RPG001)

	STP-Elmcreek&WAP 345kV
	#N/A
	355
	15,959,909.51
	

	MANUAL SINGLE SANDOW SWITCH to BADGER SWITCH 345
	Sandow Switch - Bell County East Switch 345kV
	2,202
	15,471,465.60
	

	FOWLERTON to LOBO & AVANZADA
	Lobo - Laredo Vft North 138kV
	5,426
	15,369,961.62
	



[bookmark: _Toc235457762][bookmark: _Hlk219797360]System Events
[bookmark: _Toc235457763]ERCOT Peak Load
The unofficial ERCOT peak load for July 2026 was 91,134 MW and occurred on 07/22/2026 during hour ending 18:00, this is 9,400 MW greater than the July 2025 demand of 81,734 MW on 07/30/2025 during hour ending 18:00. Instantaneous peak for July 2026 was 91,412 MW. Actual instantaneous peak for the same month last year was 82,627 MW.
[bookmark: _Toc235457764]Load Shed Events
· None.
[bookmark: _Toc235457765]Stability Events
· None.
[bookmark: _Toc235457766]Notable PMU Events
ERCOT analyzes PMU data for any significant system disturbances that do not fall into the Frequency Events category reported in section 2.1. The results are summarized in this section once the analysis has been completed.
There were no PMU events outside of those reported in section 2.1.
[bookmark: _Toc235457767]DC Tie Curtailment
None.
[bookmark: _Toc235457768][bookmark: _Hlk164863863][bookmark: _Hlk141082606][bookmark: _Hlk135641502]TRE/DOE Reportable Events
· [bookmark: _Toc13724670]CPS Submitted a DOE-417 for 07/04/2026 for complete loss of monitoring or control capability at its staffed Bulk Electric System control center for 30 continuous minutes or more.
· BPUB Submitted a DOE-417 for 07/09/2026 for Physical threat to its Facility excluding weather or
· natural disaster related threats
· CNP Submitted a DOE-417 for 07/18/2026 for Unexpected Transmission loss within its area, contrary to design, of three or more Bulk Electric System Facilities caused by a common disturbance.
[bookmark: _Toc235457769]New/Updated Constraint Management Plans
· MOD: MP_2011_08 REV38, MP_2012_07_REV 14, MP_2012_08 REV13, MP_2016_12 REV12, MP_2022_01 REV6, MP_2022_08 REV6, MP_2022_17 REV12, MP_2024_12 REV5, MP_2025_09 REV2, MP_2026_07 REV2 
[bookmark: _Toc235457770]New/Modified/Removed RAS
· None
[bookmark: _Toc235457771]New Procedures/Forms/Operating Bulletins
	[bookmark: _Hlk207973620]Date
	Subject
	Bulletin No.

	7/28/2026
	Reliability Unit Commitment V2 Rev 4
	2033



[bookmark: _Toc235457772][bookmark: _Hlk164863872]Emergency Conditions
[bookmark: _Toc235457773]OCNs
· None
[bookmark: _Toc235457774]Advisories
	Date and Time
	Message

	July 4, 2026 00:40
	Advisory issued for a geomagnetic disturbance of K7 until 0100 on 07/05/26.



[bookmark: _Toc235457775]Watches
	Date and Time
	Message

	July 9, 2026 16:50
	At 16:50, ERCOT is issuing a Watch due to HRUC not completing for HE18 due to timeline deviation.



[bookmark: _Toc235457776]Emergency Notices
· None
[bookmark: _Toc235457777]Application Performance
[bookmark: _Toc235457778]TSAT/VSAT Performance Issues
· None.
[bookmark: _Toc235457779]Communication Issues
· None.
[bookmark: _Toc235457780][bookmark: _Hlk164863883]Market System Issues
· None.

[bookmark: _Toc235457781]Model Updates
The Downstream Production Change (DPC) process allows ERCOT to make changes in the one-line Network Operations Model without loading a completely new model.  The purpose of this process is to allow for reliable grid operations as system conditions change between designated Network Operations Model database loads.  The DPC process is limited in scope to just those items listed below, with equipment ratings updates being the most common.  ERCOT has seen a rise in the use of the DPC process to make on-line updates to the Network Operations Model in recent years, instead of through the standard Network Operations Model Change Request process.
· Static Line ratings (Interim Update)
· Dynamic Line ratings (non-Interim Update)
· Autotransformer ratings (non-Interim Update)
· Breaker and Switch Normal status (Interim Update)
· Contingency Definitions (Interim Update)
· RAP and RAS changes or additions (Interim Update)
· Net Dependable and Reactive Capability (NDCRC) values (Interim Update)
· Impedance Updates (non-Interim)
[image: ]

A total of 34 DPCs were implemented in July 2026. 310 DPCs have been implemented year to date. DPCs submitted by TDSPs are mainly updates to transmission element ratings. DPCs submitted by ERCOT are mainly updates to manual contingency definitions. 
	Transmission Operator
	Number of DPCs

	AEP TEXAS COMPANY (TDSP)
	6

	BRAZOS ELECTRIC POWER CO OP INC (TDSP)
	0

	BROWNSVILLE PUBLIC UTILITIES BOARD (TDSP)
	0

	BRYAN TEXAS UTILITIES (TDSP)
	0

	CENTERPOINT ENERGY HOUSTON ELECTRIC LLC (TDSP)
	3

	CITY OF AUSTIN DBA AUSTIN ENERGY (TDSP)
	1

	CITY OF COLLEGE STATION (TDSP)
	0

	CITY OF GARLAND (TDSP)
	0

	CPS ENERGY (TDSP)
	0

	CROSS TEXAS TRANSMISSION LLC (TSP))
	0

	DENTON MUNICIPAL ELECTRIC (TDSP)
	0

	ELECTRIC TRANSMISSION TEXAS LLC (TDSP)
	0

	ERCOT
	1

	LCRA TRANSMISSION SERVICES CORPORATION (TDSP)
	12

	LONE STAR TRANSMISSION LLC (TSP)
	0

	ONCOR ELECTRIC DELIVERY COMPANY LLC (TDSP)
	8

	PEDERNALES ELECTRIC CO OP INC (TDSP)
	0

	RAYBURN COUNTRY CO OP DBA RAYBURN ELECTRIC (TDSP)
	0

	SHARYLAND UTILITIES LP (TDSP)
	0

	SOUTH TEXAS ELECTRIC CO OP INC (TDSP)
	3

	TEXAS MUNICIPAL POWER AGENCY (TDSP)
	0

	TEXAS-NEW MEXICO POWER CO (TDSP)
	0

	WIND ENERGY TRANSMISSION TEXAS LLC (TSP)
	0




[bookmark: _Toc235457782]Appendix A: Real-Time Constraints
The following is a complete list of constraints activated in SCED. Full contingency descriptions can be found in the Standard Contingencies List located on the MIS secure site at Grid  Generation  Reliability Unit Commitment.
	Year
	Month
	Contingency Name
	Overloaded Element
	From Station
	To Station
	Count of Days

	2026
	July
	BASE CASE
	EASTEX
	n/a
	n/a
	31

	2026
	July
	BASE CASE
	NELRIO
	n/a
	n/a
	29

	2026
	July
	BASE CASE
	NE_LOB
	n/a
	n/a
	28

	2026
	July
	SFURVAN8
	MOURSUND_FUR_1
	FURHMAN
	MOURSUND
	28

	2026
	July
	DWPWFWP5
	STPWAP39_1
	STP
	WAP
	26

	2026
	July
	BASE CASE
	E_PASP
	n/a
	n/a
	25

	2026
	July
	BASE CASE
	E_PATA
	n/a
	n/a
	24

	2026
	July
	SLAQLOB8
	BRUNI_69_1
	BRUNI
	BRUNI
	21

	2026
	July
	DBIGSCH5
	PALOUS_WOLFCA1_1
	PALOUSE
	WOLFCAMP
	21

	2026
	July
	DFRYTM58
	SEA_AAT1
	SEA
	SEA
	21

	2026
	July
	SPRSPAR8
	1545__A
	FLTSW
	PRSSW
	21

	2026
	July
	SVENFTS5
	35055__A
	SAMSW
	VENSW
	21

	2026
	July
	SBLURDH8
	2270__B
	MEXTP
	ITALY
	21

	2026
	July
	MHARNED5
	WESLCO_HIDLBRG_1
	MV_HBRG4
	MV_WESL4
	21

	2026
	July
	DWAP_BI5
	BI_JN_64_A
	JN
	BI
	21

	2026
	July
	SWCOWCO8
	G138_15_1
	ANGLETON
	WCOLLOCL
	20

	2026
	July
	SSTAWIC8
	138_IH2_COT_1
	IH20
	TNCOLIET
	20

	2026
	July
	SWCOWCO8
	G138_15_1
	WCOLLOCL
	ANGLETON
	20

	2026
	July
	SP5CAG8
	D5_S1_1
	HOWARD
	LEON_CRK
	19

	2026
	July
	DFOAVLO5
	NLARSW_PILONC1_1
	NLARSW
	PILONCIL
	19

	2026
	July
	DWAP_OB5
	MDOPHR99_A
	MDO
	PHR
	19

	2026
	July
	DSALHUT5
	1715__B
	TMPSW
	FRYSW
	18

	2026
	July
	SMAYWHI8
	NUECES_WHITE_2_1
	NUECES_B
	WHITE_PT
	18

	2026
	July
	SRGRMGS5
	6945__A
	MGSES
	CATSW
	17

	2026
	July
	BASE CASE
	138_FTS_LNC_1
	LEONCRK
	FTST
	15

	2026
	July
	DCDHTVW5
	6200__F
	TYPRK
	PLYAM
	15

	2026
	July
	DBIGKEN5
	TREADW_YELWJC1_1
	TREADWEL
	YELWJCKT
	15

	2026
	July
	BASE CASE
	138_FTS_LNC_1
	FTST
	LEONCRK
	15

	2026
	July
	SBENS_M8
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	14

	2026
	July
	SBENS_M8
	BENTS_FRTER_1B_1
	S_MISSIN
	FRONTERA
	14

	2026
	July
	DMCDUPS8
	HECKER_RESNIK1_1
	HECKER
	RESNIK
	14

	2026
	July
	DELMSAN5
	PAWNEE_SPRUCE_1
	PAWNEE
	CALAVERS
	14

	2026
	July
	DGRMGRS8
	6830__B
	CRDSW
	OLNEY
	14

	2026
	July
	SPEBTRU8
	940__A
	ENWSW
	TMPTN
	14

	2026
	July
	SMDOPHR5
	138_ALV_NAL_1
	TNNALVIN
	ALVIN
	14

	2026
	July
	SWCOW2C8
	_WC_WCO_1
	WC
	WCOLMAIN
	13

	2026
	July
	DYETRJU8
	HEXT_YELWJC1_1
	YELWJCKT
	HEXT
	13

	2026
	July
	SOBWAP5
	OB_WAP98_A
	WAP
	OB
	13

	2026
	July
	DBLW2JC5
	WAPWLY72_A
	WLY
	WAP
	13

	2026
	July
	SBWDDBM5
	LPLMK_LPLNE_1
	LPLMK
	LPLNE
	13

	2026
	July
	DBAKSOL5
	SOLSTICE_PST1
	SOLSTICE
	SOLSTICE
	13

	2026
	July
	DFOAVLO5
	ASHERT_CATARI1_1
	CATARINA
	ASHERTON
	13

	2026
	July
	SBLAWDB8
	2270__B
	MEXTP
	ITALY
	13

	2026
	July
	SSHAFRO8
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	12

	2026
	July
	DBIGKEN5
	FORTMA_YELWJC1_1
	YELWJCKT
	FORTMA
	12

	2026
	July
	DFOAVLO5
	BRUNI_69_1
	BRUNI
	BRUNI
	12

	2026
	July
	DBIGKEN5
	FORTMA_YELWJC1_1
	FORTMA
	YELWJCKT
	12

	2026
	July
	DFOWSMG5
	COTULL_REVEIL1_1
	REVEILLE
	COTULLA
	12

	2026
	July
	SBCESN35
	455__A
	BGRSW
	SNDSW
	12

	2026
	July
	BASE CASE
	WESTEX
	n/a
	n/a
	12

	2026
	July
	DRNS_TB5
	THWZEN98_A
	ZEN
	THW
	11

	2026
	July
	DBIGKEN5
	PALOUS_WOLFCA1_1
	PALOUSE
	WOLFCAMP
	11

	2026
	July
	BASE CASE
	MCCAMY
	n/a
	n/a
	11

	2026
	July
	DBIGSCH5
	CROSSO_NORTMC1_1
	NORTMC
	CROSSOVE
	11

	2026
	July
	SOAKSHI8
	NEWM_WAL_1
	NEWMAN
	WALNUT1
	10

	2026
	July
	SSNDBGR5
	421__A
	BCESW
	SNDSW
	10

	2026
	July
	XVIC89
	MAGRUD_VICTOR2_1
	VICTORIA
	MAGRUDER
	10

	2026
	July
	SHONF38
	HON_DEVI_1
	HONDOCK
	DEVINESW
	9

	2026
	July
	DMGSRIC8
	6840__B
	NVKSW
	ANARN
	9

	2026
	July
	STARLEO8
	SOLSTICE_PST1
	SOLSTICE
	SOLSTICE
	9

	2026
	July
	SCITWEI8
	CLARK__LON_HI1_1
	LON_HILL
	CLARK_WD
	9

	2026
	July
	BASE CASE
	PNHNDL
	n/a
	n/a
	9

	2026
	July
	DELMSAN5
	MAGRUD_VICTOR2_1
	VICTORIA
	MAGRUDER
	9

	2026
	July
	DMTSCOS5
	6437__F
	SCRCV
	KNAPP
	8

	2026
	July
	SCMNCPS5
	651__B
	CMNSW
	CMNTP
	8

	2026
	July
	SBRAHAM8
	ESCOND_GANSO1_1
	ESCONDID
	GANSO
	8

	2026
	July
	BASE CASE
	N_TO_H
	n/a
	n/a
	8

	2026
	July
	SENSENW8
	943__B
	ENWSW
	SHKSW
	8

	2026
	July
	SWAATH8
	FB_RS_60_A
	RS
	FB
	8

	2026
	July
	DSALHUT5
	1710__A
	SALDS
	SONTERRA
	8

	2026
	July
	DMBDRKC5
	651__B
	CMNSW
	CMNTP
	8

	2026
	July
	DTNFBCA8
	138_FTS_LNC_1
	LEONCRK
	FTST
	7

	2026
	July
	MBULNAV5
	35045__A
	SAMSW
	FVLSW
	7

	2026
	July
	SJUNYEL9
	HEXT_YELWJC1_1
	YELWJCKT
	HEXT
	7

	2026
	July
	SJUNYEL9
	HEXT_YELWJC1_1
	HEXT
	YELWJCKT
	7

	2026
	July
	BASE CASE
	FTST_SOLSTI1_1
	FTST
	SOLSTICE
	7

	2026
	July
	DTNFBCA8
	138_FTS_LNC_1
	FTST
	LEONCRK
	7

	2026
	July
	DVLSPAC5
	1561__A
	DPREA
	RCSES
	6

	2026
	July
	SBRAPIN8
	ESCOND_GANSO1_1
	GANSO
	ESCONDID
	6

	2026
	July
	DZORHAY5
	BERGHE_AT1H
	BERGHE
	BERGHE
	6

	2026
	July
	SSTPESP8
	BLESSI_PAVLOV1_1
	BLESSING
	PAVLOV
	6

	2026
	July
	SGRSMNW8
	MIL_LIPAN_1
	LONG
	LIPAN
	6

	2026
	July
	MSNDWCR5
	SNDSW_MR1H
	SNDSW
	SNDSW
	6

	2026
	July
	DOASSEB5
	WAPWLY72_A
	WLY
	WAP
	6

	2026
	July
	SBUZHMP8
	6217__A
	WLVSW
	GAILS
	6

	2026
	July
	DBIGKEN5
	MADDUX_TREADW1_1
	MADDUX
	TREADWEL
	6

	2026
	July
	SBRAPIN8
	ESCOND_GANSO1_1
	ESCONDID
	GANSO
	6

	2026
	July
	SMOOPEA8
	POT_PEAR_1
	PEARSALL
	POTEETS
	5

	2026
	July
	DBUCRGP5
	651__B
	CMNSW
	CMNTP
	5

	2026
	July
	SOBWA2P5
	OB_WAP99_A
	WAP
	OB
	5

	2026
	July
	SCARFRI8
	ATSO_SONR1_1
	SONR
	ATSO
	5

	2026
	July
	SSOAHOL8
	138_FTS_LNC_1
	FTST
	LEONCRK
	5

	2026
	July
	DEVRHLS8
	6293__C
	MARSW
	DEVIT
	5

	2026
	July
	SCOLBAL8
	BALLINGE_FMRL
	BALLINGE
	BALLINGE
	5

	2026
	July
	SREAUVA8
	DOWNIES_AX1H
	DOWNIES
	DOWNIES
	5

	2026
	July
	STARLEO8
	138_FTS_LNC_1
	LEONCRK
	FTST
	5

	2026
	July
	SENWSHK8
	941__C
	ENWSW
	ENSSO
	5

	2026
	July
	SEBATH8
	FB_RS_60_A
	RS
	FB
	5

	2026
	July
	SRAYRI38
	HAINE__LA_PAL1_1
	LA_PALMA
	HAINE_DR
	4

	2026
	July
	DFOWSMG5
	GEO_SIG_1
	GEOWEST
	SIGMOR
	4

	2026
	July
	SBLURDH8
	1210__B
	HUBRD
	HAN1
	4

	2026
	July
	DLONPK25
	6375__A
	GRSES
	GRMES
	4

	2026
	July
	SBLURDH8
	1275__A
	WDBSW
	HLSBR
	4

	2026
	July
	DLOFOAV5
	ASHERT_CATARI1_1
	ASHERTON
	CATARINA
	4

	2026
	July
	SPALFRO8
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	4

	2026
	July
	SWOLPAL8
	CROSSO_PALOUS1_1
	PALOUSE
	CROSSOVE
	4

	2026
	July
	BASE CASE
	SOLSTICE_PST1
	SOLSTICE
	SOLSTICE
	4

	2026
	July
	DBLBYWF5
	STPWAP39_1
	STP
	WAP
	4

	2026
	July
	SGRMGRS8
	6830__B
	CRDSW
	OLNEY
	4

	2026
	July
	SABSBLU8
	ABNTHW_SERDEV1_1
	ABNTHWST
	ABNTHWST
	3

	2026
	July
	DFRYBC58
	SEA_AAT1
	SEA
	SEA
	3

	2026
	July
	DPPRTEC8
	610__B
	TMPSW
	TMPSE
	3

	2026
	July
	XBAL89
	CONCHO_VRBS1_1
	CONCHO
	VRBS
	3

	2026
	July
	DDILCOT8
	DILLEYSW_XF1H
	DILLEYSW
	DILLEYSW
	3

	2026
	July
	SBWDDBM5
	LPLNW_LPLMD_1
	LPLNW
	LPLMD
	3

	2026
	July
	SVLGLO8
	SN_STR26_A
	SN
	STR
	3

	2026
	July
	SMDOOAS5
	GN_PZ_08_A
	GN
	PZ
	3

	2026
	July
	SMA2SAP8
	MADDUX_SAPOWE1_1
	MADDUX
	SAPOWER
	3

	2026
	July
	SMA2SAP8
	MADDUX_SAPOWE1_1
	SAPOWER
	MADDUX
	3

	2026
	July
	DBAKCED5
	HARGRO_TWINBU1_1
	TWINBU
	HARGROVE
	3

	2026
	July
	DFOWSMG5
	FWLRTN_TILDEN_1
	FOWLRTON
	TILDEN
	3

	2026
	July
	DWPWFCK5
	STPWAP39_1
	STP
	WAP
	3

	2026
	July
	SMOOPEA8
	UVALDE_W_BATE1_1
	W_BATESV
	UVALDE
	3

	2026
	July
	SSAMTCR5
	505__B
	FBRSW
	THSES
	3

	2026
	July
	SWALNAA8
	COLLE_JUPIT_1
	COLLEGE
	JUPITER
	3

	2026
	July
	DRAZSA89
	DOWNIES_AX1H
	DOWNIES
	DOWNIES
	3

	2026
	July
	DELMWWE8
	1035__A
	MCLSW
	WCOLO
	3

	2026
	July
	SVEAW_L5
	6217__A
	WLVSW
	GAILS
	3

	2026
	July
	DCC1DUKE
	WESLCO_HIDLBRG_1
	MV_HBRG4
	MV_WESL4
	3

	2026
	July
	SFMRRYS5
	400__A
	FMRVL
	RYSSW
	3

	2026
	July
	DHLSLIG8
	6405__C
	HLSES
	RMTPW
	3

	2026
	July
	MWTRWLV5
	3610__G
	PGTP1
	PDSES
	3

	2026
	July
	DSNDBGR5
	36040__A
	KNBSW
	SALSW
	2

	2026
	July
	DWAP_JN5
	BI_WAP50_A
	WAP
	BI
	2

	2026
	July
	XVE2N58
	945__B
	GLNHT
	STERT
	2

	2026
	July
	SACSARE8
	ACSSW_AX1H
	ACSSW
	ACSSW
	2

	2026
	July
	SHONMOO8
	BIG_FO_PLEASA1_1
	BIG_FOOT
	PLEASANT
	2

	2026
	July
	SCOLBAL8
	SANA_FMR1
	SANA
	SANA
	2

	2026
	July
	SALIKIN8
	SND_ORAN_1
	ORNGROV
	SNDIEGS
	2

	2026
	July
	DVLSPAC5
	389__A
	WDDSW
	MNSES
	2

	2026
	July
	DSTPSTA5
	BLESSING_1382
	BLESSING
	BLESSING
	2

	2026
	July
	SI_2RES8
	I_DUPS_RESNIK3_3
	I_DUPSW
	RESNIK
	2

	2026
	July
	SN_SLON5
	N_SHARPE_PS3
	N_SHARPE
	N_SHARPE
	2

	2026
	July
	DCDHTVW5
	6200__E
	PRKRW
	TYPRK
	2

	2026
	July
	DCPSES12
	810__G
	RDHSW
	BLUMS
	2

	2026
	July
	DBLUBUF8
	ABNTHW_SERDEV1_1
	ABNTHWST
	ABNTHWST
	2

	2026
	July
	XFTS89
	ALPINE_BRONCO1_1
	BRONCO
	ALPINE
	2

	2026
	July
	MATHEB_8
	FB_RS_60_A
	RS
	FB
	2

	2026
	July
	DWPWFWP5
	155T217_1
	BELLSO
	PT
	2

	2026
	July
	SEBHUG8
	DA_WC_89_A
	WC
	DA
	2

	2026
	July
	BASE CASE
	I_KALO
	n/a
	n/a
	2

	2026
	July
	SWCOWC8
	_WC_WCO2_1
	WC
	WCOLMAIN
	2

	2026
	July
	DRAZSA89
	2585_1
	DOWNIES
	MOORE
	2

	2026
	July
	DCDHMCS8
	3160__A
	CDCSW
	OKCLS
	2

	2026
	July
	SW_LVLT5
	6217__A
	WLVSW
	GAILS
	2

	2026
	July
	XPEA89
	DILLEYSW_XF1H
	DILLEYSW
	DILLEYSW
	2

	2026
	July
	MHARNED5
	HAINE__LA_PAL1_1
	LA_PALMA
	HAINE_DR
	2

	2026
	July
	SBGLTWI8
	LAKENA_SAMATH1_1
	LAKENASW
	SAMATHIS
	2

	2026
	July
	DTPCTHS5
	235__A
	SGRSW
	JEWET
	2

	2026
	July
	MGTNHTN5
	235__A
	SGRSW
	JEWET
	2

	2026
	July
	SHLSWDB8
	810__G
	RDHSW
	BLUMS
	2

	2026
	July
	XASH89
	CARIZOSPG_BEVO_1
	BEVO
	CARIZOS
	2

	2026
	July
	DCAGMED8
	D5_S1_1
	HOWARD
	LEON_CRK
	2

	2026
	July
	SBRABND8
	FAI_COLL_1
	FAIRDALE
	COLLEGE
	2

	2026
	July
	DPHRCTR5
	MDOPHR99_A
	MDO
	PHR
	2

	2026
	July
	SHAYZO25
	6T227_1
	HAYSEN
	ZORN
	2

	2026
	July
	DHUTGEA8
	96T136_1
	MCNEIL_
	WELLBR
	2

	2026
	July
	SPETSNU8
	AE_STR26_A
	AE
	STR
	2

	2026
	July
	DWAP_JN5
	BI_SMR98_A
	SMITHERS
	BI
	2

	2026
	July
	DBIGKEN5
	HAMILT_MAXWEL1_1
	MAXWELL
	HAMILTON
	2

	2026
	July
	DBAKCED5
	MADDUX_TREADW1_1
	TREADWEL
	MADDUX
	2

	2026
	July
	SSNYCGR8
	SNYDR_FMR1
	SNYDR
	SNYDR
	2

	2026
	July
	XPRS58
	1561__A
	DPREA
	RCSES
	2

	2026
	July
	SFMRRY25
	381__A
	FMRVL
	RYSSW
	2

	2026
	July
	DSCOTKW5
	6215__A
	BCKSW
	CGRSW
	2

	2026
	July
	MTRYBRO8
	6217__A
	WLVSW
	GAILS
	1

	2026
	July
	MGARHIC8
	CKT_1027_1
	DUNLAP
	DECKER
	1

	2026
	July
	SSOLALM8
	COCS_FTST1_1
	FTST
	COCS
	1

	2026
	July
	DBIGKEN5
	CROSSO_NORTMC1_1
	NORTMC
	CROSSOVE
	1

	2026
	July
	BASE CASE
	CULBSN
	n/a
	n/a
	1

	2026
	July
	DCAGHOW5
	D5_S1_1
	HOWARD
	LEON_CRK
	1

	2026
	July
	MDBHRSA5
	12020__B
	BRTSW
	JUNPR
	1

	2026
	July
	STNFTAR8
	138_FTS_LNC_1
	FTST
	LEONCRK
	1

	2026
	July
	DTHSFBR5
	35045__A
	SAMSW
	FVLSW
	1

	2026
	July
	SFTSFVL5
	35055__A
	SAMSW
	VENSW
	1

	2026
	July
	DLOFOAV5
	BRUNI_69_1
	BRUNI
	BRUNI
	1

	2026
	July
	SLARLAS8
	DEL_MA_LAREDO1_1
	LAREDO
	DEL_MAR
	1

	2026
	July
	DELMSAN5
	FURHMAN_VANDB_1
	FURHMAN
	VANBLTSS
	1

	2026
	July
	STREMAD8
	KATEMC_MASN1_1
	MASN
	KATEMCY
	1

	2026
	July
	DSGTSCH5
	LAKENA_SAMATH1_1
	LAKENASW
	SAMATHIS
	1

	2026
	July
	SCARLVO8
	LAKENA_SAMATH1_1
	LAKENASW
	SAMATHIS
	1

	2026
	July
	SLGDSAP8
	LAKENA_SAMATH1_1
	LAKENASW
	SAMATHIS
	1

	2026
	July
	XASH89
	LAPRYO_UVALDE1_1
	UVALDE
	LAPRYOR
	1

	2026
	July
	DRNS_TB5
	NB_THW97_A
	THW
	NB
	1

	2026
	July
	SOAKMCC8
	NEWM_WAL_1
	NEWMAN
	WALNUT1
	1

	2026
	July
	SWHILON5
	NUECES_WHITE_2_1
	NUECES_B
	WHITE_PT
	1

	2026
	July
	DELMSAN5
	POT_OAKS_1
	POTEETS
	OAKS9
	1

	2026
	July
	SFORRAY8
	RAY_L_46_1
	RAYBURN
	L_463S
	1

	2026
	July
	SWALWLN8
	SABIN_NEVAD_1
	NEVADA
	SABNCRKT
	1

	2026
	July
	MKNGSTE5
	WESLCO_HIDLBRG_1
	MV_HBRG4
	MV_WESL4
	1

	2026
	July
	SWDDMNS5
	1561__A
	DPREA
	RCSES
	1

	2026
	July
	DELMWWE8
	1880__E
	WCOLO
	MRYAV
	1

	2026
	July
	SODETES5
	6052__C
	QALSW
	TESSW
	1

	2026
	July
	XSNY89
	6690__E
	SSFTP
	SNYDR
	1

	2026
	July
	SSNYCGR8
	6695__B
	SNYDR
	AMOTP
	1

	2026
	July
	DFRIILL8
	ATSO_SONR1_1
	SONR
	ATSO
	1

	2026
	July
	DRYSALN5
	COLLE_JUPIT_1
	COLLEGE
	JUPITER
	1

	2026
	July
	BASE CASE
	FURHMAN_VANDB_1
	FURHMAN
	VANBLTSS
	1

	2026
	July
	SHASTNN8
	G138_8A_1
	PHR
	HDNLAKES
	1

	2026
	July
	SBRAESC8
	HAMILT_MAVERI1_1
	HAMILTON
	MAVERICK
	1

	2026
	July
	BASE CASE
	HHGTOM_1
	HHGT
	OMEGA
	1

	2026
	July
	DBIGKEN5
	NEVILL_NORTMC_1
	NEVILLSW
	NORTMC
	1

	2026
	July
	DLOFOAV5
	NLARSW_PILONC1_1
	PILONCIL
	NLARSW
	1

	2026
	July
	DTWLCED5
	PALOUS_WOLFCA1_1
	PALOUSE
	WOLFCAMP
	1

	2026
	July
	DDSNGBY8
	TWGWF_66_A
	WF
	TWG
	1

	2026
	July
	BASE CASE
	138_ALV_NAL_1
	TNNALVIN
	ALVIN
	1

	2026
	July
	SWORBRD8
	138_WIC_STG_1
	WICKETT
	STAGHORN
	1

	2026
	July
	DSALHUT5
	1710__B
	SONTERRA
	JREST
	1

	2026
	July
	STMPTMP5
	300__A
	TMPSW
	TMPCR
	1

	2026
	July
	DMTSCOS5
	6240__C
	SACRC
	DPCRK
	1

	2026
	July
	DMBDRKC5
	651__C
	CMNTP
	SHILO
	1

	2026
	July
	SANACN25
	835__G
	GTRSW
	EPPOI
	1

	2026
	July
	DHUTGEA8
	921T163_1
	HWRDTP
	MCNEIL_
	1

	2026
	July
	ULOPUNI1
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	1

	2026
	July
	DSTOGAR8
	CKT_1027_1
	DUNLAP
	DECKER
	1

	2026
	July
	MGARSTO8
	CKT_1027_1
	DUNLAP
	DECKER
	1

	2026
	July
	DELMSAN5
	F2_11_1
	KENEDSW
	F2
	1

	2026
	July
	DFOAVLO5
	FREER_LOBO1_1
	LOBO
	FREER
	1

	2026
	July
	SCRTIOL8
	IOLA_KEITHSW_1
	IOLA
	KEITHSW
	1

	2026
	July
	STRECFL8
	KATEMC_MASN1_1
	MASN
	KATEMCY
	1

	2026
	July
	SSTPESP8
	LAN_CT_PAVLOV1_1
	PAVLOV
	LAN_CTY
	1

	2026
	July
	SFTLMES8
	PALOUS_WOLFCA1_1
	PALOUSE
	WOLFCAMP
	1

	2026
	July
	SKINODE5
	PALOUS_WOLFCA1_1
	PALOUSE
	WOLFCAMP
	1

	2026
	July
	SFURVAN8
	RAYBURN_69_2
	RAYBURN
	RAYBURN
	1

	2026
	July
	SFURVAN8
	RAY_MOURSUND_1
	MOURSUND
	RAYBURN
	1

	2026
	July
	SBE2ASH8
	WCR_CARI_1
	WCRYSTS
	CARIZOS
	1

	2026
	July
	BASE CASE
	WILBRN
	n/a
	n/a
	1

	2026
	July
	BASE CASE
	ZAPSTR
	n/a
	n/a
	1

	2026
	July
	DWTRWLV5
	3610__G
	PGTP1
	PDSES
	1

	2026
	July
	DCPSST58
	651__B
	CMNSW
	CMNTP
	1

	2026
	July
	DVENFTS5
	810__G
	RDHSW
	BLUMS
	1

	2026
	July
	DBAKCED5
	LAKENA_SAMATH1_1
	LAKENASW
	SAMATHIS
	1

	2026
	July
	XMDO58
	MDO_AT1
	MDO
	MDO
	1

	2026
	July
	SMCEABS8
	MKLT_TRNT1_1
	TRNT
	MKLT
	1

	2026
	July
	DBIGSCH5
	SANTAR_WOLFCA1_1
	WOLFCAMP
	SANTARIT
	1

	2026
	July
	BASE CASE
	SWEETWN2_XF21
	SWEETWN2
	SWEETWN2
	1

	2026
	July
	SDIMBEV8
	UVALDE_W_BATE1_1
	W_BATESV
	UVALDE
	1

	2026
	July
	MCYPHKB8
	1160__A
	HKBRY
	VLYRN
	1

	2026
	July
	DALASOA8
	138_FTS_LNC_1
	FTST
	LEONCRK
	1

	2026
	July
	SSTAWIC8
	138_WOR_HRT_1
	HARPOONT
	WORSHAM
	1

	2026
	July
	SHELBUL5
	35045__A
	SAMSW
	FVLSW
	1

	2026
	July
	SBCEBGR5
	421__A
	BCESW
	SNDSW
	1

	2026
	July
	XSNY89
	6690__E
	SNYDR
	SSFTP
	1

	2026
	July
	DBEANOR5
	6965__A
	LNGSW
	PRLSW
	1

	2026
	July
	DSLKNOR5
	6965__A
	LNGSW
	PRLSW
	1

	2026
	July
	SMARALM9
	ALMC_PAIS1_1
	ALMC
	PAIS
	1

	2026
	July
	SFTCGAR8
	BALLINGE_FMRL
	BALLINGE
	BALLINGE
	1

	2026
	July
	SBROALP9
	COCS_FTST1_1
	COCS
	FTST
	1

	2026
	July
	SMOOPEA8
	DILLY_PEARSA1_1
	DILLY
	PEARSAL1
	1

	2026
	July
	DCOTWR25
	FARMLAND_LONGD_1
	FARMLAND
	W_LD_345
	1

	2026
	July
	DBAKCED5
	FORTMA_YELWJC1_1
	FORTMA
	YELWJCKT
	1

	2026
	July
	DBIGSCH5
	FORTMA_YELWJC1_1
	YELWJCKT
	FORTMA
	1

	2026
	July
	DSGTSCH5
	HARGRO_TWINBU1_1
	TWINBU
	HARGROVE
	1

	2026
	July
	XHHG58
	HHGT_T2H
	HHGT
	HHGT
	1

	2026
	July
	SALIKIN8
	ORNGROV_69_1
	ORNGROV
	ORNGROV
	1

	2026
	July
	BASE CASE
	SN_STR26_A
	SN
	STR
	1

	2026
	July
	BASE CASE
	THOMASTN_PS1
	THOMASTN
	THOMASTN
	1

	2026
	July
	BASE CASE
	UVALDE
	n/a
	n/a
	1

	2026
	July
	SPRIHAR8
	WESLCO_HIDLBRG_1
	MV_HBRG4
	MV_WESL4
	1

	2026
	July
	DLONPK25
	12020__B
	BRTSW
	JUNPR
	1

	2026
	July
	SBLAWDB8
	1210__B
	HUBRD
	HAN1
	1

	2026
	July
	DPHRAL58
	138_ALV_NAL_1
	TNNALVIN
	ALVIN
	1

	2026
	July
	SPIGSOL8
	138_FTS_LNC_1
	FTST
	LEONCRK
	1

	2026
	July
	SHELBUL5
	235__A
	SGRSW
	JEWET
	1

	2026
	July
	SPACVLS5
	403__A
	PRSSW
	VLYSO
	1

	2026
	July
	SSUNRGR8
	6240__C
	SACRC
	DPCRK
	1

	2026
	July
	SRAIMAD8
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	1

	2026
	July
	SILLFTL8
	CTHR_TINSLE1_1
	TINSLEY
	CTHR
	1

	2026
	July
	DVICEDN8
	FURHMAN_VANDB_1
	FURHMAN
	VANBLTSS
	1

	2026
	July
	SBRAPIN8
	HAMILT_MAVERI1_1
	HAMILTON
	MAVERICK
	1

	2026
	July
	SCISPUT8
	LENSW_PUTN2_1
	LENSW
	PUTN
	1

	2026
	July
	SCOMHA38
	MAXWEL_WHITIN1_1
	MAXWELL
	WHITING
	1

	2026
	July
	SALVTNN8
	138_FWP_MNL_1
	FRWYPARK
	MAINLAND
	1

	2026
	July
	SPRAWAL8
	155T217_1
	BELLSO
	PT
	1

	2026
	July
	DWTRWLV5
	3170__B
	SMPST
	BNTDR
	1

	2026
	July
	MBULSAM5
	35045__A
	SAMSW
	FVLSW
	1

	2026
	July
	MBULNAV5
	505__B
	FBRSW
	THSES
	1

	2026
	July
	DBRHLIG8
	6405__C
	HLSES
	RMTPW
	1

	2026
	July
	SCLCGTN8
	6635__G
	MRVLY
	ESTLD
	1

	2026
	July
	SFLTLNG8
	6635__G
	MRVLY
	ESTLD
	1

	2026
	July
	SDAFDES8
	CKT_1027_1
	DUNLAP
	DECKER
	1

	2026
	July
	SCRDJON5
	HOOD_DECRDVA_1
	DCDAM
	HOD
	1

	2026
	July
	SN_SLON5
	KINGSV_KLEBER1_1
	KLEBERG
	KINGSVIL
	1

	2026
	July
	SMOOPEA8
	PALDRO_DILLEY_1
	PALODURO
	DILLEYSW
	1

	2026
	July
	DRAZSA89
	READIN_UVALDE1_1
	UVALDE
	READING
	1

	2026
	July
	SMV_PAR8
	RIOHND_ERIOHND_1
	MV_RIOHO
	RIOHONDO
	1

	2026
	July
	DBAKCED5
	SCHNDR_BIGHIL2_2
	SCHNDR
	BIGHIL
	1

	2026
	July
	SZENTH35
	THWZEN71_A
	ZEN
	THW
	1

	2026
	July
	SREAUVA8
	UVLD_DOWI_1
	DOWNIES
	UVLDES
	1

	2026
	July
	DSALKLN5
	1270__F
	KFHSW
	KLNFH
	1

	2026
	July
	SSALTMP5
	1270__F
	KFHSW
	KLNFH
	1

	2026
	July
	SMYPHLS9
	2270__B
	MEXTP
	ITALY
	1
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IRR Output / Total ERCOT Load

Monthly Max/Min/Avg Wind, Solar, IRR Output as a Percentage of Total ERCOT Load
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Wind, Solar, IRR penetration during hour of Peak Load
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Minimum Wind, Solar, IRR Output during the peak load hour as percentage of daily peak Load in
July, 2026
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