July 2026 ERCOT Monthly Operations Report

Reliability and Operations Subcommittee Meeting

October 1, 2026

Table of Contents

1.	Report Highlights	2

2.	Frequency Control	3

2.1.	Frequency Events	3

2.2.	Automatic/Manual Load Resource Deployments	5

3.	Reliability Unit Commitment	6

4.	IRR, Wind, and Solar Generation as a Percent of Load	9

5.	Largest Net-Load Ramps	10

6.	Congestion Analysis	12

6.1.	Notable Constraints	12

6.2.	Generic Transmission Constraint Congestion	32

6.3.	Manual Overrides	32

6.4.	Congestion Costs for Calendar Year 2026	33

7.	System Events	34

7.1.	ERCOT Peak Load	34

7.2.	Load Shed Events	34

7.3.	Stability Events	34

7.4.	Notable PMU Events	35

7.5.	DC Tie Curtailment	35

7.6.	TRE/DOE Reportable Events	35

7.7.	New/Updated Constraint Management Plans	35

7.8.	New/Modified/Removed RAS	35

7.9.	New Procedures/Forms/Operating Bulletins	35

8.	Emergency Conditions	36

8.1.	OCNs	36

8.2.	Advisories	36

8.3.	Watches	36

8.4.	Emergency Notices	36

9.	Application Performance	36

9.1.	TSAT/VSAT Performance Issues	36

9.2.	Communication Issues	37

9.3.	Market System Issues	37

10.	Model Updates	37

Appendix A: Real-Time Constraints	40

# Report Highlights

The unofficial ERCOT peak load for July 2026 was 91,134 MW and occurred on 07/22/2026 during hour ending 18:00, this is 9,400 MW higher than the July 2025 peak demand of 81,734 MW on 07/30/2025.

On 15-minute settlement interval basis, maximum demand of 91,263 MW occurred on 7/22/2026 during interval ending 17:30 and minimum demand of 51,412 MW occurred on 7/15/2026 during interval ending 04:00.

There were 9 frequency events.

There were no events which required automatic/manual deployment of Load Resources that were controlled by an Under-Frequency Relays.

There were 0 OCNs

There was 1 Advisory issued for a geomagnetic disturbance of K7 until 0100 on 07/05/26.

There was 1 Watch issued due to HRUC not completing for HE18 due to timeline deviation.

There were 0 Emergency Notices.

There were 62 RUC commitments.

A PVGR Generation Record of 35,427 MW was set on 07/30/2026 at 13:33.

The following GTCs saw congestion in July:

| GTC | Days Congestion |
| --- | --- |
| East Texas | 31 |
| Nelson Sharpe - Rio Hondo | 29 |
| North Edinburg - Lobo | 28 |
| South Texas Export Pawnee - Spruce | 25 |
| South Texas Export Pawnee - Tango | 24 |
| West Texas | 12 |
| McCamey | 11 |
| Panhandle | 9 |
| North - Houston | 8 |
| South Texas Import Katoen - Lonhill | 2 |
| Uvalde | 1 |
| Williamson - Burnet | 1 |
| Zapata Starr | 1 |
| Culberson | 1 |

# Frequency Control

## Frequency Events

The ERCOT Interconnection experienced 9 frequency events.

A summary of the frequency events is provided below. The reported frequency events meet one of the following criteria: Delta Frequency is 60 mHz or greater; the MW loss is 350 MW or greater; resource trip event triggered ECRS deployment. Frequency events that have been identified as Frequency Measurable Events (FME) for purposes of BAL-001-TRE-2 analysis are highlighted in blue. When analyzing frequency events, ERCOT evaluates PMU data according to industry standards. Events with an oscillating frequency of less than 1 Hz are inter-area, while higher frequencies indicate local events. Industry standards specify that damping ratio for inter-area oscillations should be 3.0% or greater. For the frequency event listed below, the ERCOT system met these standards and transitioned well after the disturbance. In the case of negative delta frequency, the MW Loss column could refer to load loss.

| Date and Time | Delta Frequency | Max/Min Frequency | Duration of Event | PMU Data |  | MW Loss | Load | IRR | Inertia |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | (Hz) | (Hz) |  | Oscillation Mode (Hz) | Damping Ratio |  | (MW) | % | (MW-s) |
| 7/3/2026 14:04:33 | 0.020 | 59.957 | 00:04:33 | 0.54 | 13% | 502 | 80,042 | 50% | 303,616 |
| 7/7/2026 19:35:49 | 0.026 | 59.960 | 00:03:53 | 0.49 | 16% | 658 | 79,529 | 26% | 329,009 |
| 7/21/2026 11:35:35 | 0.034 | 59.961 | 00:05:19 | 0.41 | 12% | 503 | 75,241 | 48% | 331,000 |
| 7/21/2026 15:48:02 | 0.040 | 59.968 | 00:05:25 | 0.34 | 9% | 515 | 86,432 | 41% | 347,319 |
| 7/22/2026 13:43:32 | 0.035 | 59.963 | 00:05:59 | 0.51 | 13% | 615 | 87,798 | 39% | 351,561 |
| 7/22/2026 16:33:58 | 0.025 | 59.960 | 00:03:42 | 0.37 | 10% | 606 | 90,865 | 37% | 365,941 |
| 7/29/2026 14:41:34 | 0.017 | 59.966 | 00:03:19 | 0.59 | 15% | 522 | 86,994 | 46% | 327,452 |
| 7/30/2026 14:15:07 | 0.017 | 59.964 | 00:07:39 | 0.44 | 11% | 467 | 87,119 | 53% | 327,026 |
| 7/30/2026 22:40:25 | 0.037 | 59.974 | 00:06:10 | 0.57 | 14% | 312 | 75,265 | 28% | 343,896 |

(Note: All data on this graph encompasses frequency event analysis based on BAL-001-TRE-2.)

## Automatic/Manual Load Resource Deployments

There were no events which required automatic/manual deployment of Load Resources that were controlled by an Under-Frequency Relays.

# Reliability Unit Commitment

ERCOT reports on Reliability Unit Commitments (RUC) monthly. Commitments are reported grouped by operating day and weather zone. The total number of hours committed is the sum of the hours for all the units in the specified region. Additional information on RUC commitments can be found on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

There were 62 RUC commitments.

| Resource Location | # of Resources | Operating Day | Total # of Hours Committed | Total MWhs | Reason for Commitment |
| --- | --- | --- | --- | --- | --- |
| NORTH_CENTRAL | 1 | July 2, 2026 | 4 | 1,580.0 | E_PASP |
| NORTH_CENTRAL | 1 | July 3, 2026 | 4 | 1,568.0 | Capacity |
| NORTH_CENTRAL | 5 | July 5, 2026 | 34 | 3,791.9 | Capacity, E_PASP |
| EAST, NORTH_CENTRAL | 8 | July 6, 2026 | 43 | 5,808.8 | Capacity |
| NORTH_CENTRAL | 2 | July 7, 2026 | 13 | 2,320.0 | Capacity, MWTRWLV5 |
| EAST | 2 | July 9, 2026 | 8 | 2,688.0 | DCDHTVW5 |
| COAST, NORTH, NORTH_CENTRAL | 10 | July 19, 2026 | 61 | 8,458.4 | Capacity |
| NORTH_CENTRAL | 4 | July 20, 2026 | 24 | 2,620.0 | Capacity |
| SOUTH_CENTRAL | 1 | July 22, 2026 | 5 | 2,000.0 | E_PASP |
| NORTH_CENTRAL | 1 | July 27, 2026 | 1 | 375.0 | Capacity |
| EAST, NORTH_CENTRAL | 9 | July 28, 2026 | 61 | 17,149.0 | Capacity, DCDHTVW5 |
| NORTH_CENTRAL, SOUTH_CENTRAL, SOUTHERN | 10 | July 29, 2026 | 82 | 17,340.7 | Capacity, Capacity AS, E_PASP |
| NORTH_CENTRAL | 3 | July 30, 2026 | 65 | 13,124.0 | Capacity AS |
| NORTH_CENTRAL, SOUTH_CENTRAL | 5 | July 31, 2026 | 32 | 4,238.8 | Capacity AS, E_PASP |

# IRR, Wind, and Solar Generation as a Percent of Load

The graph below shows the maximum, minimum and average aggregate solar, wind and IRR output as a percentage of total ERCOT load when evaluated as 10-minute averaged intervals, over the past 13 months. Current wind and solar generation and penetration records are listed in the footnote below. Maximum IRR penetration for July 2026 was 70.90% on 7/25/2026 interval ending 10:10 and minimum IRR penetration for July 2026 was 5.10% on 7/13/2026 interval ending 06:40.

During the hour of peak load for the month, hourly integrated wind generation was 4,653 MW and solar generation was 28,710 MW. The graph below shows the wind and solar penetration percentage during the hour of the peak load in the last 13 months.

Lastly, the graph below shows the minimum wind, solar, and IRR output during the peak load hour as a percentage of the daily peak load for every day in the month.

# Largest Net-Load Ramps

The net-load ramp is defined as the change in net-load (load minus wind and PVGR generation) during the defined time horizon. Such a variation in net-load needs to be accommodated in grid operations to ensure that the reliability of the grid is satisfactorily maintained. The largest net-load ramps over 5-minute, 10-minute, 15-minute, 30-minute, and 60-minute intervals in July 2026 were 1,706 MW, 2,873 MW, 3,822 MW, 6,941 MW, and 12,588 MW respectively. A comparison with historical values is provided in the table below.

| Month and Year | 5 min | 10 min | 15 min | 30 min | 60 min |
| --- | --- | --- | --- | --- | --- |
| 14-Jul | 674 MW | 1,169 MW | 1,589 MW | 2,854 MW | 5,201 MW |
| 15-Jul | 776 MW | 1,231 MW | 1,754 MW | 3,303 MW | 6,260 MW |
| 16-Jul | 834 MW | 1,350 MW | 1,881 MW | 3,230 MW | 6,319 MW |
| 17-Jul | 797 MW | 1,421 MW | 1,953 MW | 3,167 MW | 5,798 MW |
| 18-Jul | 1,333 MW | 1,854 MW | 2,780 MW | 3,205 MW | 6,604 MW |
| 19-Jul | 830 MW | 1,460 MW | 2,084 MW | 3,795 MW | 7,375 MW |
| 20-Jul | 954 MW | 1,536 MW | 2,221 MW | 4,101 MW | 7,690 MW |
| 21-Jul | 1,323 MW | 1,596 MW | 2,081 MW | 3,614 MW | 6,761 MW |
| 22-Jul | 977 MW | 1,837 MW | 2,664 MW | 4,529 MW | 7,716 MW |
| 23-Jul | 1,230 MW | 1,793 MW | 2,519 MW | 4,733 MW | 8,650 MW |
| 24-Jul | 1,128 MW | 2,011 MW | 2,837 MW | 4,671 MW | 7,772 MW |
| 25-Jul | 1,564 MW | 2,531 MW | 3,7678 MW | 7,116 MW | 12,438 MW |
| 26-Jul | 1,706 MW | 2,873 MW | 3,822 MW | 6,941 MW | 12,588 MW |
|  | 7/27/2026 | 7/6/2026 | 7/20/2026 | 7/30/2026 | 7/20/2026 |
|  | (IE 11:21) | (IE 19:08) | (IE 19:29) | (IE 19:18) | (IE 19:53) |
| All Months in 2014-2026 | 1,771 MW | 3,107 MW | 4,588 MW | 8,901 MW | 16,522 MW |
|  | 5/28/2024 | 1/29/2024 | 1/29/2024 | 1/29/2024 | 1/29/2024 |
|  | (IE 19:01) | (IE 17:05) | (IE 17:10) | (IE 17:11) | (IE 17:17) |

# Congestion Analysis

## Notable Constraints

Nodal protocol section 3.20 specifies that ERCOT shall identify transmission constraints that are binding in Real-Time three or more Operating Days within a calendar month. As part of this process, ERCOT reports congestion that meets this criterion to ROS. In addition, ERCOT also highlights notable constraints that have an estimated congestion rent exceeding $1,000,000 for a calendar month. These constraints are detailed in the table below, including approved transmission upgrades from TPIT that may provide some congestion relief based on ERCOT’s engineering judgement. Rows highlighted in blue indicate the congestion was affected by one or more outages. For a list of all constraints activated in SCED, please see Appendix A at the end of this report.

| Data Item | Contingency Name | Overloaded Element | Contingency Name | Overloaded Element | # of Days Constraint Binding | Congestion Rent | Transmission Project |
| --- | --- | --- | --- | --- | --- | --- | --- |
| STP_WAP_STPWAP39_1 | DWPWFWP5 | STPWAP39_1 | TWR(345) WAP-WLF64 & WAP-WLY72 | South Texas Project - Wa Parish 345kV | 25 | $22,566,078.45 |  |  |
| TMPSW_FRYSW_1715__B | DSALHUT5 | 1715__B | SALSW - HUTTO 345KV | Temple Switch - Fryers Creek 138kV | 17 | $10,105,097.03 | Temple Area Project (24RPG001). Note that Fryers Creek is named Boggy Creek in planning cases. |  |
| SEA_SEA_SEA_AAT1 | DFRYTM58 | SEA_AAT1 | DOUBLE FRYSW-TMPSW 138 & KNBSW-SALSW 345 | Seaton 138kV | 20 | $8,689,562.07 |  |  |
| TMPSW_TMPSE_610__B | DPPRTEC8 | 610__B | PEPPER CREEK SW TO TEMPLE ELM CREEK 138 KV DOUBLE | Temple Switch - Temple Southeast 138kV | 3 | $8,406,579.68 |  |  |
| MCNEIL__WELLBR_96T136_1 | DHUTGEA8 | 96T136_1 | HUTTO TO RNDRK 138 AND HUTTO TO GEORSO 138 DBLCKT | Wells Branch - Mcneil 138kV | 2 | $8,070,717.33 |  |  |
| SAMSW_VENSW_35055__A | SVENFTS5 | 35055__A | FORT SMITH SWITCH to FORT SMITH SWITCH LIN _B | Sam Switch - Venus Switch 345kV | 20 | $7,639,766.34 | Venus Switch to Sam Switch 345-kV Line Project (24RPG017) |  |
| MGSES_CATSW_6945__A | SRGRMGS5 | 6945__A | MORGAN CREEK SES to RANGER CAMP SWITCH LIN _A | Morgan Creek Ses - Cattleman Switch 345kV | 14 | $4,949,105.91 | West Texas 345-kV Infrastructure Rebuild Project (23RPG034) |  |
| n/a_n/a_WESTEX | BASE CASE | WESTEX | Basecase | WESTEX GTC | 7 | $4,537,911.14 | Permian Basin Relibility Plan (765-kV import paths) (The PUCT approved ,helps improve, but not fully exit, the GTC yet.) |  |
| NLARSW_PILONCIL_NLARSW_PILONC1_1 | DFOAVLO5 | NLARSW_PILONC1_1 | FOWLERTON to LOBO & AVANZADA | North Laredo Switch - Piloncillo 138kV | 17 | $3,174,440.05 |  |  |
| MDO_PHR_MDOPHR99_A | DWAP_OB5 | MDOPHR99_A | TWR (345) OB-WAP98 & OB-WAP99 | Meadow - Ph Robinson 345kV | 16 | $2,806,532.52 | CNP_28TPIT103344_PH_Robinson_to_WA_Parish_Hardening (MOD 103344 Phase 103435, 25RPG028) |  |
| TYPRK_PLYAM_6200__F | DCDHTVW5 | 6200__F | TVWSW TO CDHSW 345 AND CDHSW TO VENSW 345 DBLCKT | Poly-America - Tyre Park Sub 138kV | 14 | $2,770,555.27 |  |  |
| PALOUSE_WOLFCAMP_PALOUS_WOLFCA1_1 | DBIGSCH5 | PALOUS_WOLFCA1_1 | Big Hill - Schneeman Draw & Big Hill - Schneeman Draw 2 | Palouse - Wolfcamp 138kV | 21 | $2,686,618.72 |  |  |
| n/a_n/a_NELRIO | BASE CASE | NELRIO | Basecase | NELRIO GTC | 29 | $2,598,104.98 | The Lower Rio Grande Valley (LRGV) System Enhancement Project (21RPG017) |  |
| JN_BI_BI_JN_64_A | DWAP_BI5 | BI_JN_64_A | TWR (345) WAP-BI50 & SMITHERS-BI98 | Bellaire - Jeanetta 345kV | 18 | $2,518,527.11 |  |  |
| LPLMK_LPLNE_LPLMK_LPLNE_1 | SBWDDBM5 | LPLMK_LPLNE_1 | BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1 | Mackenzie Substation - Northeast Substation 115kV | 8 | $2,512,965.18 |  |  |
| SMITHERS_BI_BI_SMR98_A | DWAP_JN5 | BI_SMR98_A | TWR (345) JN-WAP64 & JN-WAP72 | Bellaire - Smithers 345kV | 2 | $2,354,060.48 |  |  |
| WAP_OB_OB_WAP98_A | SOBWAP5 | OB_WAP98_A | WA PARISH to OBRIEN LIN A | Wa Parish - Obrien 345kV | 11 | $2,336,304.50 |  |  |
| n/a_n/a_NE_LOB | BASE CASE | NE_LOB | Basecase | NE_LOB GTC | 20 | $2,279,186.03 | San Antonio South Reliability I Project (22RPG048) LRGV Transmission Improvement Project (21RPG017) San Antonio South Reliability II Project (23RPG032) |  |
| SEA_SEA_SEA_AAT1 | DFRYBC58 | SEA_AAT1 | DOUBLE KNBSW-SALSW 345 & FRYSW-BELCNTY 138 | Seaton 138kV | 3 | $2,098,744.93 |  |  |
| n/a_n/a_EASTEX | BASE CASE | EASTEX | Basecase | EASTEX GTC | 28 | $2,054,622.70 |  |  |
| COLLEGE_JUPITER_COLLE_JUPIT_1 | SWALNAA8 | COLLE_JUPIT_1 | NAAMAN to NAAMAN LIN 1 | College - Jupiter 138kV | 3 | $2,031,522.28 | GPL_TPIT_110751_WylieSW_LCP_Upgrades_Jupiter_College_Line (MOD 110751) |  |
| MEXTP_ITALY_2270__B | SBLURDH8 | 2270__B | BLUM to RED HILL SWITCH LIN _G | Milford Exxon Tap - Italy 69kV | 20 | $1,620,574.42 |  |  |
| MV_HBRG4_MV_WESL4_WESLCO_HIDLBRG_1 | MHARNED5 | WESLCO_HIDLBRG_1 | Manual dbl ckt for NEDIN-BONILLA 345kV & RIOH-PRIM138kV | Heidelburg Sub - Weslaco Sub 138kV | 20 | $1,614,159.44 | STEC_71928_Heidelberg_AEPWeslaco_Upgrade (MOD 71928) |  |
| BALLINGE_BALLINGE_BALLINGE_FMRL | SCOLBAL8 | BALLINGE_FMRL | BALLINGER to COLEMAN LAKE IVIE TAP LIN 1 | Ballinger 69kV | 5 | $1,361,943.12 |  |  |
| LPLNW_LPLMD_LPLNW_LPLMD_1 | SBWDDBM5 | LPLNW_LPLMD_1 | BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1 | Northwest Substation - Mcdonald Substation 115kV | 3 | $1,303,618.88 |  |  |
| ZEN_THW_THWZEN98_A | DRNS_TB5 | THWZEN98_A | Rns-Rtw & Sng-Tb 345kV | Th Wharton - Zenith 345kV | 9 | $1,278,093.25 |  |  |
| LONG_LIPAN_MIL_LIPAN_1 | SGRSMNW8 | MIL_LIPAN_1 | GRINDSTONE SWITCH to MILLER LIN _C | Lipan - Long 138kV | 5 | $1,238,096.46 |  |  |
| TREADWEL_YELWJCKT_TREADW_YELWJC1_1 | DBIGKEN5 | TREADW_YELWJC1_1 | Bighil-Kendal 345kV | Yellow Jacket - Treadwell 138kV | 15 | $1,235,839.94 |  |  |
| NEWMAN_WALNUT1_NEWM_WAL_1 | SOAKSHI8 | NEWM_WAL_1 | OAKLAND SUBSTATION to SHILOH LIN 1 | Newman - Walnut 138kV | 6 | $1,139,066.46 |  |  |
| HLSES_RMTPW_6405__C | DHLSLIG8 | 6405__C | HLSES TO EVRSW 138 AND HLSES TO LIGSW 138 DBLCKT | Handley Ses - Randol Mill Tap West 138kV | 3 | $1,072,991.73 |  |  |
| PGTP1_PDSES_3610__G | MWTRWLV5 | 3610__G | MANUAL WTRML-WLVEE&WTRML-SARRD 345 DBLCKT | Parkdale Switch - Pleasant Grove Tap 1 138kV | 3 | $1,044,638.06 |  |  |
| SOLSTICE_SOLSTICE_SOLSTICE_PST1 | DBAKSOL5 | SOLSTICE_PST1 | Bakersfield - Solstice line 1 and 2 | Solstice 138kV | 13 | $1,001,186.66 | Fort Stockton Switch: Expand 345 kV Station (MOD 93226) |  |
| VICTORIA_MAGRUDER_MAGRUD_VICTOR2_1 | XVIC89 | MAGRUD_VICTOR2_1 | VICTORIA TRX 69A2 138/69 | Magruder - Victoria 138kV | 6 | $822,146.08 |  |  |
| MARSW_DEVIT_6293__C | DEVRHLS8 | 6293__C | EVRSW TO HLSES 138 DBLCKT | Marrs Switch - Devitt Sub 138kV | 4 | $808,339.74 |  |  |
| n/a_n/a_PNHNDL | BASE CASE | PNHNDL | Basecase | PNHNDL GTC | 5 | $803,246.92 |  |  |
| HOWARD_LEON_CRK_D5_S1_1 | SP5CAG8 | D5_S1_1 | CAGNON to CAGNON LIN 1 | Leon Creek - Howard 138kV | 15 | $802,742.20 |  |  |
| FLTSW_PRSSW_1545__A | SPRSPAR8 | 1545__A | PARIS SWITCH to PARIS LIN _A | Paris Switch - Flying Tiger Switch 138kV | 21 | $781,103.29 |  |  |
| CRDSW_OLNEY_6830__B | DGRMGRS8 | 6830__B | FIREROCK TO BRNWD 138 AND FIREROCK TO BANGS 69 DBLCKT | Cottonwood Road Switch - Olney Pod 69kV | 12 | $726,946.31 |  |  |
| WAP_OB_OB_WAP99_A | SOBWA2P5 | OB_WAP99_A | WA PARISH to OBRIEN LIN A | Wa Parish - Obrien 345kV | 4 | $662,416.03 |  |  |
| PALOUSE_WOLFCAMP_PALOUS_WOLFCA1_1 | DBIGKEN5 | PALOUS_WOLFCA1_1 | Bighil-Kendal 345kV | Palouse - Wolfcamp 138kV | 11 | $590,279.86 |  |  |
| BRUNI_BRUNI_BRUNI_69_1 | DFOAVLO5 | BRUNI_69_1 | FOWLERTON to LOBO & AVANZADA | Bruni Sub 138kV | 7 | $580,200.81 |  |  |
| SCRCV_KNAPP_6437__F | DMTSCOS5 | 6437__F | DMTSW TO SCOSW 345 DBLCKT | Knapp - Scurry Chevron 138kV | 7 | $542,470.14 |  |  |
| HECKER_RESNIK_HECKER_RESNIK1_1 | DMCDUPS8 | HECKER_RESNIK1_1 | MCCAMPBE - RESNIK & I_DUPSW 138kV | Hecker - Resnik 138kV | 11 | $523,418.33 |  |  |
| SALDS_SONTERRA_1710__A | DSALHUT5 | 1710__A | SALSW - HUTTO 345KV | Salado South - Sonterra 138kV | 6 | $470,143.60 |  |  |
| CMNSW_CMNTP_651__B | SCMNCPS5 | 651__B | COMANCHE SWITCH (Oncor) to COMANCHE PEAK SES LIN _A | Comanche Tap - Comanche Switch (Oncor) 138kV | 8 | $464,403.32 |  |  |
| CMNSW_CMNTP_651__B | DMBDRKC5 | 651__B | MBDSW-CMBSW & MBDSW-RKCRK 345_DBLCKT | Comanche Tap - Comanche Switch (Oncor) 138kV | 8 | $454,297.99 |  |  |
| n/a_n/a_E_PASP | BASE CASE | E_PASP | Basecase | E_PASP GTC | 18 | $454,103.73 |  |  |
| NUECES_B_WHITE_PT_NUECES_WHITE_2_1 | SMAYWHI8 | NUECES_WHITE_2_1 | GILA to MAYO LIN 1 | Nueces Bay - Whitepoint 138kV | 11 | $428,414.57 |  |  |
| PAWNEE_CALAVERS_PAWNEE_SPRUCE_1 | DELMSAN5 | PAWNEE_SPRUCE_1 | Elmcreek-Sanmigl 345kV | Pawnee Switching Station - Calaveras 345kV | 10 | $416,961.38 |  |  |
| NORTMC_CROSSOVE_CROSSO_NORTMC1_1 | DBIGSCH5 | CROSSO_NORTMC1_1 | Big Hill - Schneeman Draw & Big Hill - Schneeman Draw 2 | North Mccamey - Crossover 138kV | 9 | $374,266.42 |  |  |
| VICTORIA_MAGRUDER_MAGRUD_VICTOR2_1 | DELMSAN5 | MAGRUD_VICTOR2_1 | Elmcreek-Sanmigl 345kV | Magruder - Victoria 138kV | 8 | $359,774.24 |  |  |
| WLY_WAP_WAPWLY72_A | DOASSEB5 | WAPWLY72_A | TWR(345) DOW-OAS 18 & OAS-SEB 27 | Wa Parish - Whaley 345kV | 4 | $322,057.67 |  |  |
| CATARINA_ASHERTON_ASHERT_CATARI1_1 | DFOAVLO5 | ASHERT_CATARI1_1 | FOWLERTON to LOBO & AVANZADA | Asherton - Catarina 138kV | 10 | $301,467.46 |  |  |
| n/a_n/a_MCCAMY | BASE CASE | MCCAMY | Basecase | MCCAMY GTC | 8 | $298,592.02 |  |  |
| ESCONDID_GANSO_ESCOND_GANSO1_1 | SBRAHAM8 | ESCOND_GANSO1_1 | BRACKETTVILLE to HAMILTON ROAD LIN 1 | Escondido - Ganso 138kV | 7 | $287,348.42 |  |  |
| TNNALVIN_ALVIN_138_ALV_NAL_1 | SMDOPHR5 | 138_ALV_NAL_1 | MEADOW to PH ROBINSON LIN A | North Alvin Tnp - Alvin Tnp 138kV | 11 | $284,310.82 |  |  |
| SNDSW_SNDSW_SNDSW_MR1H | MSNDWCR5 | SNDSW_MR1H | MANUAL SANDOW SW TO WALLEYE CREEK SW | Sandow Switch 345kV | 3 | $278,404.22 |  |  |
| WLY_WAP_WAPWLY72_A | DBLW2JC5 | WAPWLY72_A | TWR (345) JCK-WAT62 & BLY-JCK57 | Wa Parish - Whaley 345kV | 9 | $269,816.04 |  |  |
| SAMSW_FVLSW_35045__A | MBULNAV5 | 35045__A | Mnaual single contingency BULLOCK-NAVARRO 345kV | Sam Switch - Files Valley Switch 345kV | 7 | $260,491.74 |  |  |
| RS_FB_FB_RS_60_A | SWAATH8 | FB_RS_60_A | Athena to WALLIS LIN A | Fort Bend - Rosenberg 138kV | 7 | $230,753.90 |  |  |
| BCESW_SNDSW_421__A | SSNDBGR5 | 421__A | SANDOW SWITCH to BADGER SWITCH LIN _A | Sandow Switch - Bell County East Switch 345kV | 8 | $230,446.68 |  |  |
| STP_WAP_STPWAP39_1 | DBLBYWF5 | STPWAP39_1 | TWR (345) BLU-BLY72 & HLJ-WLF64 | South Texas Project - Wa Parish 345kV | 4 | $221,068.61 |  |  |
| ENWSW_TMPTN_940__A | SPEBTRU8 | 940__A | GAMMA to GAMMA LIN _D | Ennis West Switch - Templeton 138kV | 12 | $210,947.50 |  |  |
| GN_PZ_GN_PZ_08_A | SMDOOAS5 | GN_PZ_08_A | MEADOW to OASIS LIN A | Grant - Plaza 138kV | 3 | $209,868.46 |  |  |
| FRONTERA_S_MISSIN_BENTS_FRTER_1B_1 | SSHAFRO8 | BENTS_FRTER_1B_1 | FRONTERA to SHARYLAND LIN 1 | Frontera - South Mission 138kV | 10 | $206,668.07 |  |  |
| ASHERTON_CATARINA_ASHERT_CATARI1_1 | DLOFOAV5 | ASHERT_CATARI1_1 | Double LOBO - FOWLERTON & AVANZADA | Asherton - Catarina 138kV | 4 | $189,994.64 |  |  |
| PEARSALL_POTEETS_POT_PEAR_1 | SMOOPEA8 | POT_PEAR_1 | MOORE SWITCHING STATION to MOORE SWITCHING STATION LIN 1 | Poteet Sub - Pearsall Switching Station 69kV | 5 | $186,111.73 |  |  |
| FORTMA_YELWJCKT_FORTMA_YELWJC1_1 | DBIGKEN5 | FORTMA_YELWJC1_1 | Bighil-Kendal 345kV | Yellow Jacket - Fort Mason 138kV | 10 | $185,310.90 |  |  |
| MEXTP_ITALY_2270__B | SBLAWDB8 | 2270__B | BLANTON to WOODBURY SWITCH LIN _C | Milford Exxon Tap - Italy 69kV | 13 | $172,825.64 |  |  |
| CRDSW_OLNEY_6830__B | SGRMGRS8 | 6830__B | GRAHAM EAST to GRAHAM EAST LIN _A | Cottonwood Road Switch - Olney Pod 69kV | 4 | $155,695.59 |  |  |
| RS_FB_FB_RS_60_A | SEBATH8 | FB_RS_60_A | Athena to EAST BERNARD LIN A | Fort Bend - Rosenberg 138kV | 4 | $155,134.28 |  |  |
| REVEILLE_COTULLA_COTULL_REVEIL1_1 | DFOWSMG5 | COTULL_REVEIL1_1 | FOWLRTON TO SAN MIGUEL DOUBLE CIRCUIT CONTINGENCY | Cotulla - Reveille 138kV | 8 | $146,785.25 |  |  |
| SOLSTICE_SOLSTICE_SOLSTICE_PST1 | STARLEO8 | SOLSTICE_PST1 | LEON CREEK TNP to TARBUSH TNP LIN 1 | Solstice 138kV | 7 | $139,178.65 |  |  |
| BERGHE_BERGHE_BERGHE_AT1H | DZORHAY5 | BERGHE_AT1H | ZORN - HAYSEN 345KV | Bergheim 345kV | 6 | $136,345.69 |  |  |
| CMNSW_CMNTP_651__B | DBUCRGP5 | 651__B | MANUAL DOUBLE RGPSW - KLNSW 345 KV & BUCSW - KLNSW 345 KV | Comanche Tap - Comanche Switch (Oncor) 138kV | 4 | $135,664.12 |  |  |
| BGRSW_SNDSW_455__A | SBCESN35 | 455__A | BELL COUNTY EAST SWITCH to BELL COUNTY EAST SWITCH LIN _A | Badger Switch - Sandow Switch 345kV | 9 | $133,356.67 |  |  |
| BRUNI_BRUNI_BRUNI_69_1 | SLAQLOB8 | BRUNI_69_1 | LAQUINTA to LOBO LIN 1 | Bruni Sub 138kV | 16 | $131,593.78 |  |  |
| DPREA_RCSES_1561__A | DVLSPAC5 | 1561__A | VLSES-PACSW 345&PRSSW-VLYSO 345 DBLCKT | Rivercrest Ses - Deport Rea 138kV | 4 | $113,554.98 |  |  |
| NVKSW_ANARN_6840__B | DMGSRIC8 | 6840__B | DBL_CKT_GRSES-RICSW_138 kV and GRSES-SGRAS_138 kV | Anarene - Navy Kickapoo Switch 69kV | 7 | $106,618.34 |  |  |
| n/a_n/a_E_PATA | BASE CASE | E_PATA | Basecase | E_PATA GTC | 7 | $98,518.19 |  |  |
| HONDOCK_DEVINESW_HON_DEVI_1 | SHONF38 | HON_DEVI_1 | HONDO to HONDO CREEK SWITCHING STATION LIN 1 | Hondo Creek Switching Station - Devine Switch 69kV | 6 | $70,565.33 |  |  |
| TWINBU_HARGROVE_HARGRO_TWINBU1_1 | DBAKCED5 | HARGRO_TWINBU1_1 | BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Hargrove - Twin Buttes 138kV | 3 | $65,810.45 |  |  |
| ESCONDID_GANSO_ESCOND_GANSO1_1 | SBRAPIN8 | ESCOND_GANSO1_1 | BRACKETTVILLE to BRACKETTVILLE LIN 1 | Escondido - Ganso 138kV | 5 | $62,197.20 |  |  |
| ENWSW_SHKSW_943__B | SENSENW8 | 943__B | ENNIS SOUTH to ENNIS SOUTH LIN _C | Shankle Switch - Ennis West Switch 138kV | 7 | $59,397.74 |  |  |
| DILLEYSW_DILLEYSW_DILLEYSW_XF1H | DDILCOT8 | DILLEYSW_XF1H | Dilleysw-Sanmgsw&Cotulas 138kV | Dilley Switch Aep 138kV | 3 | $57,185.70 |  |  |
| BLESSING_PAVLOV_BLESSI_PAVLOV1_1 | SSTPESP8 | BLESSI_PAVLOV1_1 | STP SWITCH to Esperanza LIN 1 | Blessing - Pavlov 138kV | 4 | $54,058.19 |  |  |
| YELWJCKT_FORTMA_FORTMA_YELWJC1_1 | DBIGKEN5 | FORTMA_YELWJC1_1 | Bighil-Kendal 345kV | Yellow Jacket - Fort Mason 138kV | 10 | $49,832.84 |  |  |
| SONR_ATSO_ATSO_SONR1_1 | SCARFRI8 | ATSO_SONR1_1 | Carver to Carver LIN 1 | Atlantic Sonora - Sonora 69kV | 3 | $48,239.63 |  |  |
| MADDUX_TREADWEL_MADDUX_TREADW1_1 | DBIGKEN5 | MADDUX_TREADW1_1 | Bighil-Kendal 345kV | Maddux - Treadwell 138kV | 6 | $44,826.02 |  |  |
| FTST_SOLSTICE_FTST_SOLSTI1_1 | BASE CASE | FTST_SOLSTI1_1 | Basecase | Fort Stockton Plant - Solstice 138kV | 3 | $41,255.73 |  |  |
| PALOUSE_CROSSOVE_CROSSO_PALOUS1_1 | SWOLPAL8 | CROSSO_PALOUS1_1 | PALOUSE to Wolfcamp LIN 1 | Crossover - Palouse 138kV | 4 | $29,011.08 |  |  |
| SN_STR_SN_STR26_A | SVLGLO8 | SN_STR26_A | VELASCO to GLOBAL LIN A | Sintek - Stratt 138kV | 3 | $22,932.31 |  |  |
| DOWNIES_DOWNIES_DOWNIES_AX1H | DRAZSA89 | DOWNIES_AX1H | Double Circuit RAZORBAC to DRYFRIO 138 kV & UVALDE to SABINAL 69 kV | Downie Switching Station 138kV | 3 | $22,641.78 |  |  |
| FRONTERA_S_MISSIN_BENTS_FRTER_1B_1 | SBENS_M8 | BENTS_FRTER_1B_1 | SOUTH MCALLEN to BENTSEN LIN 1 | Frontera - South Mission 138kV | 14 | $22,482.01 |  |  |
| FTST_LEONCRK_138_FTS_LNC_1 | BASE CASE | 138_FTS_LNC_1 | Basecase | Leon Creek Tnp - Fort Stockton Plant 138kV | 13 | $21,032.28 |  |  |
| FURHMAN_MOURSUND_MOURSUND_FUR_1 | SFURVAN8 | MOURSUND_FUR_1 | FURHMAN to VANDERBILT SWITCHING STATION LIN 1 | Moursund - Furhman 138kV | 17 | $20,403.70 |  |  |
| LEONCRK_FTST_138_FTS_LNC_1 | STARLEO8 | 138_FTS_LNC_1 | LEON CREEK TNP to TARBUSH TNP LIN 1 | Leon Creek Tnp - Fort Stockton Plant 138kV | 5 | $19,605.99 |  |  |
| WLVSW_GAILS_6217__A | SVEAW_L5 | 6217__A | wett_long_draw to VEALMOOR - Sharyland Utilities LIN 1 | Willow Valley Switch - Gail Sub 138kV | 3 | $12,133.39 |  |  |
| IH20_TNCOLIET_138_IH2_COT_1 | SSTAWIC8 | 138_IH2_COT_1 | STAGHORN TNP to WICKETT TNP LIN 1 | Ih 20 Tnp - Collie Field Tap Tnp 138kV | 17 | $11,824.04 |  |  |
| LA_PALMA_HAINE_DR_HAINE__LA_PAL1_1 | SRAYRI38 | HAINE__LA_PAL1_1 | LAS PULGAS to RAYMONDVILLE 2 LIN 1 | Haine Drive - La Palma 138kV | 4 | $10,885.01 |  |  |
| WC_WCOLMAIN__WC_WCO_1 | SWCOW2C8 | _WC_WCO_1 | WEST COLUMBIA MAIN TNP to WEST COLUMBIA LIN 1 | West Columbia Main Tnp - West Columbia 138kV | 9 | $9,621.89 |  |  |
| DOWNIES_DOWNIES_DOWNIES_AX1H | SREAUVA8 | DOWNIES_AX1H | Reading to Reading LIN 1 | Downie Switching Station 138kV | 5 | $8,159.29 |  |  |
| ANGLETON_WCOLLOCL_G138_15_1 | SWCOWCO8 | G138_15_1 | WEST COLUMBIA MAIN TNP to ANGLETON TNP LIN 1 | West Columbia Local Tnp - Angleton Tnp 138kV | 19 | $7,185.89 |  |  |
| YELWJCKT_HEXT_HEXT_YELWJC1_1 | SJUNYEL9 | HEXT_YELWJC1_1 | MENARD PHILLIPS TAP to MENARD PHILLIPS TAP LIN 1 | Yellow Jacket - Hext Lcra 69kV | 7 | $5,560.31 |  |  |
| YELWJCKT_HEXT_HEXT_YELWJC1_1 | DYETRJU8 | HEXT_YELWJC1_1 | Double for YellowJacket - Treadwell & Junction | Yellow Jacket - Hext Lcra 69kV | 10 | $5,377.78 |  |  |
| LON_HILL_CLARK_WD_CLARK__LON_HI1_1 | SCITWEI8 | CLARK__LON_HI1_1 | CHAMPLIN to CHAMPLIN LIN 1 | Clarkwood - Lon Hill 138kV | 7 | $5,360.76 |  |  |
| FTST_LEONCRK_138_FTS_LNC_1 | DTNFBCA8 | 138_FTS_LNC_1 | TNFXTAIL TO TARBUSH to BCATOKA 138KV | Leon Creek Tnp - Fort Stockton Plant 138kV | 5 | $5,182.14 |  |  |
| GANSO_ESCONDID_ESCOND_GANSO1_1 | SBRAPIN8 | ESCOND_GANSO1_1 | BRACKETTVILLE to BRACKETTVILLE LIN 1 | Escondido - Ganso 138kV | 5 | $5,075.45 |  |  |
| FRONTERA_S_MISSIN_BENTS_FRTER_1B_1 | SPALFRO8 | BENTS_FRTER_1B_1 | FRONTERA to KEY SWITCH LIN 1 | Frontera - South Mission 138kV | 4 | $4,488.93 |  |  |
| FTST_LEONCRK_138_FTS_LNC_1 | SSOAHOL8 | 138_FTS_LNC_1 | SOAPTREE TNP to HOLIDAY SUB TNP LIN 1 | Leon Creek Tnp - Fort Stockton Plant 138kV | 4 | $2,091.02 |  |  |
| WLVSW_GAILS_6217__A | SBUZHMP8 | 6217__A | BUZZARD DRAW SWITCH to HARDY MORGAN POI LIN _B | Willow Valley Switch - Gail Sub 138kV | 4 | $1,857.71 |  |  |

## Generic Transmission Constraint Congestion

| GTC | Days Congestion |
| --- | --- |
| East Texas | 31 |
| Nelson Sharpe - Rio Hondo | 29 |
| North Edinburg - Lobo | 28 |
| South Texas Export Pawnee - Spruce | 25 |
| South Texas Export Pawnee - Tango | 24 |
| West Texas | 12 |
| McCamey | 11 |
| Panhandle | 9 |
| North - Houston | 8 |
| South Texas Import Katoen - Lonhill | 2 |
| Uvalde | 1 |
| Williamson - Burnet | 1 |
| Zapata Starr | 1 |
| Culberson | 1 |

- There was no activity on the remaining GTCs during the month.

Note: This is how many times a constraint has been activated to avoid exceeding a GTC limit, it does not imply an exceedance of the GTC occurred or that the GTC was binding.

## Manual Overrides

- None

## Congestion Costs for Calendar Year 2026

The following table represents the top twenty active constraints for the calendar year based on the estimated congestion rent attributed to the congestion. ERCOT updates this list on a monthly basis.

| Contingency | Overloaded Element | # of 5-min SCED | Estimated | Transmission |
| --- | --- | --- | --- | --- |
| Basecase | WESTEX GTC | 16,629 | 97,011,822.87 | Permian Basin Relibility Plan (765-kV import paths) (The PUCT approved ,helps improve, but not fully exit, the GTC yet.) |
| MANUAL HCKSW-RAMSW 345 kV_2 | Hicks Switch 138kV | 1,363 | 51,703,803.38 |  |
| BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Longshore Switch - Prairieland Switch 345kV | 13,078 | 50,084,697.46 | Oncor_FW_81268_Longshore – Consavvy 345 kV Double-Circuit Line Rebuild (MOD 81268) |
| TWR(345) WAP-WLF64 & WAP-WLY72 | South Texas Project - Wa Parish 345kV | 6,500 | 37,872,522.05 |  |
| Basecase | EASTEX GTC | 8,733 | 35,476,046.68 |  |
| MANUAL RNKSW TO DHMSW 345&KRWSW TO DHMSW 345 DBLCKT | Argyle - Highlands Tnp 138kV | 6,658 | 34,162,852.87 |  |
| SALSW TO KLNSW 345 DBLCKT | Killeen Switch - Stagecoach 138kV | 2,796 | 31,304,486.27 | ONCOR_SE_87703_Belton_Killeen_138 kV Line (via Nolanville) (MOD 87703, 24RPG001) |
| BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1 | Mackenzie Substation - Northeast Substation 115kV | 7,908 | 28,970,921.60 |  |
| DOUBLE NVARO-LEG & NVARO-OUTSW 345 KV | Big Brown Ses - Jewett 345kV | 504 | 26,063,843.65 | ONCOR_SE_99622_PIN_OAK_SWITCH (MOD 99622, 25RPG004) |
| MORGAN CREEK SES to RANGER CAMP SWITCH LIN _A | Morgan Creek Ses - Cattleman Switch 345kV | 4,253 | 24,313,709.09 | West Texas 345-kV Infrastructure Rebuild Project (23RPG034) |
| BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Hargrove - Twin Buttes 138kV | 4,915 | 23,123,991.35 |  |
| Basecase | Omega - Horse Hollow Generation Tie 345kV | 9,100 | 21,147,903.99 |  |
| DMTSW TO SCOSW 345 DBLCKT | Knapp - Scurry Chevron 138kV | 11,350 | 21,126,587.99 | Oncor_FW_102849_Union 138 kV Switch (MOD 102849) |
| Basecase | NE_LOB GTC | 20,101 | 20,723,375.13 | San Antonio South Reliability I Project (22RPG048) LRGV Transmission Improvement Project (21RPG017) San Antonio South Reliability II Project (23RPG032) |
| FORT SMITH SWITCH to FORT SMITH SWITCH LIN _B | Sam Switch - Venus Switch 345kV | 3,657 | 20,598,006.36 | Venus Switch to Sam Switch 345-kV Line Project (24RPG017) |
| Basecase | E_PASP GTC | 9,798 | 20,461,803.10 | San Antonio South Reliability I Project (22RPG048) LRGV Transmission Improvement Project (21RPG017) San Antonio South Reliability II Project (23RPG032) |
| SALSW TO KLNSW 345 DBLCKT | Harker Heights South - Killeen Switch 138kV | 3,820 | 17,819,511.40 | ONCOR_SE_87699_Belton - Killeen 138 kV_Line (MOD 87699, 24RPG001) |
| STP-Elmcreek&WAP 345kV | #N/A | 355 | 15,959,909.51 |  |
| MANUAL SINGLE SANDOW SWITCH to BADGER SWITCH 345 | Sandow Switch - Bell County East Switch 345kV | 2,202 | 15,471,465.60 |  |
| FOWLERTON to LOBO & AVANZADA | Lobo - Laredo Vft North 138kV | 5,426 | 15,369,961.62 |  |

# System Events

## ERCOT Peak Load

The unofficial ERCOT peak load for July 2026 was 91,134 MW and occurred on 07/22/2026 during hour ending 18:00, this is 9,400 MW greater than the July 2025 demand of 81,734 MW on 07/30/2025 during hour ending 18:00. Instantaneous peak for July 2026 was 91,412 MW. Actual instantaneous peak for the same month last year was 82,627 MW.

## Load Shed Events

- None.

## Stability Events

- None.

## Notable PMU Events

ERCOT analyzes PMU data for any significant system disturbances that do not fall into the Frequency Events category reported in section 2.1. The results are summarized in this section once the analysis has been completed.

There were no PMU events outside of those reported in section 2.1.

## DC Tie Curtailment

None.

## TRE/DOE Reportable Events

- CPS Submitted a DOE-417 for 07/04/2026 for complete loss of monitoring or control capability at its staffed Bulk Electric System control center for 30 continuous minutes or more.

- BPUB Submitted a DOE-417 for 07/09/2026 for Physical threat to its Facility excluding weather or

- natural disaster related threats

- CNP Submitted a DOE-417 for 07/18/2026 for Unexpected Transmission loss within its area, contrary to design, of three or more Bulk Electric System Facilities caused by a common disturbance.

## New/Updated Constraint Management Plans

- MOD: MP_2011_08 REV38, MP_2012_07_REV 14, MP_2012_08 REV13, MP_2016_12 REV12, MP_2022_01 REV6, MP_2022_08 REV6, MP_2022_17 REV12, MP_2024_12 REV5, MP_2025_09 REV2, MP_2026_07 REV2

## New/Modified/Removed RAS

- None

## New Procedures/Forms/Operating Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 7/28/2026 | Reliability Unit Commitment V2 Rev 4 | 2033 |

# Emergency Conditions

## OCNs

- None

## Advisories

| Date and Time | Message |
| --- | --- |
| July 4, 2026 00:40 | Advisory issued for a geomagnetic disturbance of K7 until 0100 on 07/05/26. |

## Watches

| Date and Time | Message |
| --- | --- |
| July 9, 2026 16:50 | At 16:50, ERCOT is issuing a Watch due to HRUC not completing for HE18 due to timeline deviation. |

## Emergency Notices

- None

# Application Performance

## TSAT/VSAT Performance Issues

- None.

## Communication Issues

- None.

## Market System Issues

- None.

# Model Updates

The Downstream Production Change (DPC) process allows ERCOT to make changes in the one-line Network Operations Model without loading a completely new model.  The purpose of this process is to allow for reliable grid operations as system conditions change between designated Network Operations Model database loads.  The DPC process is limited in scope to just those items listed below, with equipment ratings updates being the most common.  ERCOT has seen a rise in the use of the DPC process to make on-line updates to the Network Operations Model in recent years, instead of through the standard Network Operations Model Change Request process.

- Static Line ratings (Interim Update)

- Dynamic Line ratings (non-Interim Update)

- Autotransformer ratings (non-Interim Update)

- Breaker and Switch Normal status (Interim Update)

- Contingency Definitions (Interim Update)

- RAP and RAS changes or additions (Interim Update)

- Net Dependable and Reactive Capability (NDCRC) values (Interim Update)

- Impedance Updates (non-Interim)

A total of 34 DPCs were implemented in July 2026. 310 DPCs have been implemented year to date. DPCs submitted by TDSPs are mainly updates to transmission element ratings. DPCs submitted by ERCOT are mainly updates to manual contingency definitions.

| Transmission Operator | Number of DPCs |
| --- | --- |
| AEP TEXAS COMPANY (TDSP) | 6 |
| BRAZOS ELECTRIC POWER CO OP INC (TDSP) | 0 |
| BROWNSVILLE PUBLIC UTILITIES BOARD (TDSP) | 0 |
| BRYAN TEXAS UTILITIES (TDSP) | 0 |
| CENTERPOINT ENERGY HOUSTON ELECTRIC LLC (TDSP) | 3 |
| CITY OF AUSTIN DBA AUSTIN ENERGY (TDSP) | 1 |
| CITY OF COLLEGE STATION (TDSP) | 0 |
| CITY OF GARLAND (TDSP) | 0 |
| CPS ENERGY (TDSP) | 0 |
| CROSS TEXAS TRANSMISSION LLC (TSP)) | 0 |
| DENTON MUNICIPAL ELECTRIC (TDSP) | 0 |
| ELECTRIC TRANSMISSION TEXAS LLC (TDSP) | 0 |
| ERCOT | 1 |
| LCRA TRANSMISSION SERVICES CORPORATION (TDSP) | 12 |
| LONE STAR TRANSMISSION LLC (TSP) | 0 |
| ONCOR ELECTRIC DELIVERY COMPANY LLC (TDSP) | 8 |
| PEDERNALES ELECTRIC CO OP INC (TDSP) | 0 |
| RAYBURN COUNTRY CO OP DBA RAYBURN ELECTRIC (TDSP) | 0 |
| SHARYLAND UTILITIES LP (TDSP) | 0 |
| SOUTH TEXAS ELECTRIC CO OP INC (TDSP) | 3 |
| TEXAS MUNICIPAL POWER AGENCY (TDSP) | 0 |
| TEXAS-NEW MEXICO POWER CO (TDSP) | 0 |
| WIND ENERGY TRANSMISSION TEXAS LLC (TSP) | 0 |

# Appendix A: Real-Time Constraints

The following is a complete list of constraints activated in SCED. Full contingency descriptions can be found in the Standard Contingencies List located on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

| Year | Month | Contingency Name | Overloaded Element | From Station | To Station | Count of Days |
| --- | --- | --- | --- | --- | --- | --- |
| 2026 | July | BASE CASE | EASTEX | n/a | n/a | 31 |
| 2026 | July | BASE CASE | NELRIO | n/a | n/a | 29 |
| 2026 | July | BASE CASE | NE_LOB | n/a | n/a | 28 |
| 2026 | July | SFURVAN8 | MOURSUND_FUR_1 | FURHMAN | MOURSUND | 28 |
| 2026 | July | DWPWFWP5 | STPWAP39_1 | STP | WAP | 26 |
| 2026 | July | BASE CASE | E_PASP | n/a | n/a | 25 |
| 2026 | July | BASE CASE | E_PATA | n/a | n/a | 24 |
| 2026 | July | SLAQLOB8 | BRUNI_69_1 | BRUNI | BRUNI | 21 |
| 2026 | July | DBIGSCH5 | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 21 |
| 2026 | July | DFRYTM58 | SEA_AAT1 | SEA | SEA | 21 |
| 2026 | July | SPRSPAR8 | 1545__A | FLTSW | PRSSW | 21 |
| 2026 | July | SVENFTS5 | 35055__A | SAMSW | VENSW | 21 |
| 2026 | July | SBLURDH8 | 2270__B | MEXTP | ITALY | 21 |
| 2026 | July | MHARNED5 | WESLCO_HIDLBRG_1 | MV_HBRG4 | MV_WESL4 | 21 |
| 2026 | July | DWAP_BI5 | BI_JN_64_A | JN | BI | 21 |
| 2026 | July | SWCOWCO8 | G138_15_1 | ANGLETON | WCOLLOCL | 20 |
| 2026 | July | SSTAWIC8 | 138_IH2_COT_1 | IH20 | TNCOLIET | 20 |
| 2026 | July | SWCOWCO8 | G138_15_1 | WCOLLOCL | ANGLETON | 20 |
| 2026 | July | SP5CAG8 | D5_S1_1 | HOWARD | LEON_CRK | 19 |
| 2026 | July | DFOAVLO5 | NLARSW_PILONC1_1 | NLARSW | PILONCIL | 19 |
| 2026 | July | DWAP_OB5 | MDOPHR99_A | MDO | PHR | 19 |
| 2026 | July | DSALHUT5 | 1715__B | TMPSW | FRYSW | 18 |
| 2026 | July | SMAYWHI8 | NUECES_WHITE_2_1 | NUECES_B | WHITE_PT | 18 |
| 2026 | July | SRGRMGS5 | 6945__A | MGSES | CATSW | 17 |
| 2026 | July | BASE CASE | 138_FTS_LNC_1 | LEONCRK | FTST | 15 |
| 2026 | July | DCDHTVW5 | 6200__F | TYPRK | PLYAM | 15 |
| 2026 | July | DBIGKEN5 | TREADW_YELWJC1_1 | TREADWEL | YELWJCKT | 15 |
| 2026 | July | BASE CASE | 138_FTS_LNC_1 | FTST | LEONCRK | 15 |
| 2026 | July | SBENS_M8 | BENTS_FRTER_1B_1 | FRONTERA | S_MISSIN | 14 |
| 2026 | July | SBENS_M8 | BENTS_FRTER_1B_1 | S_MISSIN | FRONTERA | 14 |
| 2026 | July | DMCDUPS8 | HECKER_RESNIK1_1 | HECKER | RESNIK | 14 |
| 2026 | July | DELMSAN5 | PAWNEE_SPRUCE_1 | PAWNEE | CALAVERS | 14 |
| 2026 | July | DGRMGRS8 | 6830__B | CRDSW | OLNEY | 14 |
| 2026 | July | SPEBTRU8 | 940__A | ENWSW | TMPTN | 14 |
| 2026 | July | SMDOPHR5 | 138_ALV_NAL_1 | TNNALVIN | ALVIN | 14 |
| 2026 | July | SWCOW2C8 | _WC_WCO_1 | WC | WCOLMAIN | 13 |
| 2026 | July | DYETRJU8 | HEXT_YELWJC1_1 | YELWJCKT | HEXT | 13 |
| 2026 | July | SOBWAP5 | OB_WAP98_A | WAP | OB | 13 |
| 2026 | July | DBLW2JC5 | WAPWLY72_A | WLY | WAP | 13 |
| 2026 | July | SBWDDBM5 | LPLMK_LPLNE_1 | LPLMK | LPLNE | 13 |
| 2026 | July | DBAKSOL5 | SOLSTICE_PST1 | SOLSTICE | SOLSTICE | 13 |
| 2026 | July | DFOAVLO5 | ASHERT_CATARI1_1 | CATARINA | ASHERTON | 13 |
| 2026 | July | SBLAWDB8 | 2270__B | MEXTP | ITALY | 13 |
| 2026 | July | SSHAFRO8 | BENTS_FRTER_1B_1 | FRONTERA | S_MISSIN | 12 |
| 2026 | July | DBIGKEN5 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 12 |
| 2026 | July | DFOAVLO5 | BRUNI_69_1 | BRUNI | BRUNI | 12 |
| 2026 | July | DBIGKEN5 | FORTMA_YELWJC1_1 | FORTMA | YELWJCKT | 12 |
| 2026 | July | DFOWSMG5 | COTULL_REVEIL1_1 | REVEILLE | COTULLA | 12 |
| 2026 | July | SBCESN35 | 455__A | BGRSW | SNDSW | 12 |
| 2026 | July | BASE CASE | WESTEX | n/a | n/a | 12 |
| 2026 | July | DRNS_TB5 | THWZEN98_A | ZEN | THW | 11 |
| 2026 | July | DBIGKEN5 | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 11 |
| 2026 | July | BASE CASE | MCCAMY | n/a | n/a | 11 |
| 2026 | July | DBIGSCH5 | CROSSO_NORTMC1_1 | NORTMC | CROSSOVE | 11 |
| 2026 | July | SOAKSHI8 | NEWM_WAL_1 | NEWMAN | WALNUT1 | 10 |
| 2026 | July | SSNDBGR5 | 421__A | BCESW | SNDSW | 10 |
| 2026 | July | XVIC89 | MAGRUD_VICTOR2_1 | VICTORIA | MAGRUDER | 10 |
| 2026 | July | SHONF38 | HON_DEVI_1 | HONDOCK | DEVINESW | 9 |
| 2026 | July | DMGSRIC8 | 6840__B | NVKSW | ANARN | 9 |
| 2026 | July | STARLEO8 | SOLSTICE_PST1 | SOLSTICE | SOLSTICE | 9 |
| 2026 | July | SCITWEI8 | CLARK__LON_HI1_1 | LON_HILL | CLARK_WD | 9 |
| 2026 | July | BASE CASE | PNHNDL | n/a | n/a | 9 |
| 2026 | July | DELMSAN5 | MAGRUD_VICTOR2_1 | VICTORIA | MAGRUDER | 9 |
| 2026 | July | DMTSCOS5 | 6437__F | SCRCV | KNAPP | 8 |
| 2026 | July | SCMNCPS5 | 651__B | CMNSW | CMNTP | 8 |
| 2026 | July | SBRAHAM8 | ESCOND_GANSO1_1 | ESCONDID | GANSO | 8 |
| 2026 | July | BASE CASE | N_TO_H | n/a | n/a | 8 |
| 2026 | July | SENSENW8 | 943__B | ENWSW | SHKSW | 8 |
| 2026 | July | SWAATH8 | FB_RS_60_A | RS | FB | 8 |
| 2026 | July | DSALHUT5 | 1710__A | SALDS | SONTERRA | 8 |
| 2026 | July | DMBDRKC5 | 651__B | CMNSW | CMNTP | 8 |
| 2026 | July | DTNFBCA8 | 138_FTS_LNC_1 | LEONCRK | FTST | 7 |
| 2026 | July | MBULNAV5 | 35045__A | SAMSW | FVLSW | 7 |
| 2026 | July | SJUNYEL9 | HEXT_YELWJC1_1 | YELWJCKT | HEXT | 7 |
| 2026 | July | SJUNYEL9 | HEXT_YELWJC1_1 | HEXT | YELWJCKT | 7 |
| 2026 | July | BASE CASE | FTST_SOLSTI1_1 | FTST | SOLSTICE | 7 |
| 2026 | July | DTNFBCA8 | 138_FTS_LNC_1 | FTST | LEONCRK | 7 |
| 2026 | July | DVLSPAC5 | 1561__A | DPREA | RCSES | 6 |
| 2026 | July | SBRAPIN8 | ESCOND_GANSO1_1 | GANSO | ESCONDID | 6 |
| 2026 | July | DZORHAY5 | BERGHE_AT1H | BERGHE | BERGHE | 6 |
| 2026 | July | SSTPESP8 | BLESSI_PAVLOV1_1 | BLESSING | PAVLOV | 6 |
| 2026 | July | SGRSMNW8 | MIL_LIPAN_1 | LONG | LIPAN | 6 |
| 2026 | July | MSNDWCR5 | SNDSW_MR1H | SNDSW | SNDSW | 6 |
| 2026 | July | DOASSEB5 | WAPWLY72_A | WLY | WAP | 6 |
| 2026 | July | SBUZHMP8 | 6217__A | WLVSW | GAILS | 6 |
| 2026 | July | DBIGKEN5 | MADDUX_TREADW1_1 | MADDUX | TREADWEL | 6 |
| 2026 | July | SBRAPIN8 | ESCOND_GANSO1_1 | ESCONDID | GANSO | 6 |
| 2026 | July | SMOOPEA8 | POT_PEAR_1 | PEARSALL | POTEETS | 5 |
| 2026 | July | DBUCRGP5 | 651__B | CMNSW | CMNTP | 5 |
| 2026 | July | SOBWA2P5 | OB_WAP99_A | WAP | OB | 5 |
| 2026 | July | SCARFRI8 | ATSO_SONR1_1 | SONR | ATSO | 5 |
| 2026 | July | SSOAHOL8 | 138_FTS_LNC_1 | FTST | LEONCRK | 5 |
| 2026 | July | DEVRHLS8 | 6293__C | MARSW | DEVIT | 5 |
| 2026 | July | SCOLBAL8 | BALLINGE_FMRL | BALLINGE | BALLINGE | 5 |
| 2026 | July | SREAUVA8 | DOWNIES_AX1H | DOWNIES | DOWNIES | 5 |
| 2026 | July | STARLEO8 | 138_FTS_LNC_1 | LEONCRK | FTST | 5 |
| 2026 | July | SENWSHK8 | 941__C | ENWSW | ENSSO | 5 |
| 2026 | July | SEBATH8 | FB_RS_60_A | RS | FB | 5 |
| 2026 | July | SRAYRI38 | HAINE__LA_PAL1_1 | LA_PALMA | HAINE_DR | 4 |
| 2026 | July | DFOWSMG5 | GEO_SIG_1 | GEOWEST | SIGMOR | 4 |
| 2026 | July | SBLURDH8 | 1210__B | HUBRD | HAN1 | 4 |
| 2026 | July | DLONPK25 | 6375__A | GRSES | GRMES | 4 |
| 2026 | July | SBLURDH8 | 1275__A | WDBSW | HLSBR | 4 |
| 2026 | July | DLOFOAV5 | ASHERT_CATARI1_1 | ASHERTON | CATARINA | 4 |
| 2026 | July | SPALFRO8 | BENTS_FRTER_1B_1 | FRONTERA | S_MISSIN | 4 |
| 2026 | July | SWOLPAL8 | CROSSO_PALOUS1_1 | PALOUSE | CROSSOVE | 4 |
| 2026 | July | BASE CASE | SOLSTICE_PST1 | SOLSTICE | SOLSTICE | 4 |
| 2026 | July | DBLBYWF5 | STPWAP39_1 | STP | WAP | 4 |
| 2026 | July | SGRMGRS8 | 6830__B | CRDSW | OLNEY | 4 |
| 2026 | July | SABSBLU8 | ABNTHW_SERDEV1_1 | ABNTHWST | ABNTHWST | 3 |
| 2026 | July | DFRYBC58 | SEA_AAT1 | SEA | SEA | 3 |
| 2026 | July | DPPRTEC8 | 610__B | TMPSW | TMPSE | 3 |
| 2026 | July | XBAL89 | CONCHO_VRBS1_1 | CONCHO | VRBS | 3 |
| 2026 | July | DDILCOT8 | DILLEYSW_XF1H | DILLEYSW | DILLEYSW | 3 |
| 2026 | July | SBWDDBM5 | LPLNW_LPLMD_1 | LPLNW | LPLMD | 3 |
| 2026 | July | SVLGLO8 | SN_STR26_A | SN | STR | 3 |
| 2026 | July | SMDOOAS5 | GN_PZ_08_A | GN | PZ | 3 |
| 2026 | July | SMA2SAP8 | MADDUX_SAPOWE1_1 | MADDUX | SAPOWER | 3 |
| 2026 | July | SMA2SAP8 | MADDUX_SAPOWE1_1 | SAPOWER | MADDUX | 3 |
| 2026 | July | DBAKCED5 | HARGRO_TWINBU1_1 | TWINBU | HARGROVE | 3 |
| 2026 | July | DFOWSMG5 | FWLRTN_TILDEN_1 | FOWLRTON | TILDEN | 3 |
| 2026 | July | DWPWFCK5 | STPWAP39_1 | STP | WAP | 3 |
| 2026 | July | SMOOPEA8 | UVALDE_W_BATE1_1 | W_BATESV | UVALDE | 3 |
| 2026 | July | SSAMTCR5 | 505__B | FBRSW | THSES | 3 |
| 2026 | July | SWALNAA8 | COLLE_JUPIT_1 | COLLEGE | JUPITER | 3 |
| 2026 | July | DRAZSA89 | DOWNIES_AX1H | DOWNIES | DOWNIES | 3 |
| 2026 | July | DELMWWE8 | 1035__A | MCLSW | WCOLO | 3 |
| 2026 | July | SVEAW_L5 | 6217__A | WLVSW | GAILS | 3 |
| 2026 | July | DCC1DUKE | WESLCO_HIDLBRG_1 | MV_HBRG4 | MV_WESL4 | 3 |
| 2026 | July | SFMRRYS5 | 400__A | FMRVL | RYSSW | 3 |
| 2026 | July | DHLSLIG8 | 6405__C | HLSES | RMTPW | 3 |
| 2026 | July | MWTRWLV5 | 3610__G | PGTP1 | PDSES | 3 |
| 2026 | July | DSNDBGR5 | 36040__A | KNBSW | SALSW | 2 |
| 2026 | July | DWAP_JN5 | BI_WAP50_A | WAP | BI | 2 |
| 2026 | July | XVE2N58 | 945__B | GLNHT | STERT | 2 |
| 2026 | July | SACSARE8 | ACSSW_AX1H | ACSSW | ACSSW | 2 |
| 2026 | July | SHONMOO8 | BIG_FO_PLEASA1_1 | BIG_FOOT | PLEASANT | 2 |
| 2026 | July | SCOLBAL8 | SANA_FMR1 | SANA | SANA | 2 |
| 2026 | July | SALIKIN8 | SND_ORAN_1 | ORNGROV | SNDIEGS | 2 |
| 2026 | July | DVLSPAC5 | 389__A | WDDSW | MNSES | 2 |
| 2026 | July | DSTPSTA5 | BLESSING_1382 | BLESSING | BLESSING | 2 |
| 2026 | July | SI_2RES8 | I_DUPS_RESNIK3_3 | I_DUPSW | RESNIK | 2 |
| 2026 | July | SN_SLON5 | N_SHARPE_PS3 | N_SHARPE | N_SHARPE | 2 |
| 2026 | July | DCDHTVW5 | 6200__E | PRKRW | TYPRK | 2 |
| 2026 | July | DCPSES12 | 810__G | RDHSW | BLUMS | 2 |
| 2026 | July | DBLUBUF8 | ABNTHW_SERDEV1_1 | ABNTHWST | ABNTHWST | 2 |
| 2026 | July | XFTS89 | ALPINE_BRONCO1_1 | BRONCO | ALPINE | 2 |
| 2026 | July | MATHEB_8 | FB_RS_60_A | RS | FB | 2 |
| 2026 | July | DWPWFWP5 | 155T217_1 | BELLSO | PT | 2 |
| 2026 | July | SEBHUG8 | DA_WC_89_A | WC | DA | 2 |
| 2026 | July | BASE CASE | I_KALO | n/a | n/a | 2 |
| 2026 | July | SWCOWC8 | _WC_WCO2_1 | WC | WCOLMAIN | 2 |
| 2026 | July | DRAZSA89 | 2585_1 | DOWNIES | MOORE | 2 |
| 2026 | July | DCDHMCS8 | 3160__A | CDCSW | OKCLS | 2 |
| 2026 | July | SW_LVLT5 | 6217__A | WLVSW | GAILS | 2 |
| 2026 | July | XPEA89 | DILLEYSW_XF1H | DILLEYSW | DILLEYSW | 2 |
| 2026 | July | MHARNED5 | HAINE__LA_PAL1_1 | LA_PALMA | HAINE_DR | 2 |
| 2026 | July | SBGLTWI8 | LAKENA_SAMATH1_1 | LAKENASW | SAMATHIS | 2 |
| 2026 | July | DTPCTHS5 | 235__A | SGRSW | JEWET | 2 |
| 2026 | July | MGTNHTN5 | 235__A | SGRSW | JEWET | 2 |
| 2026 | July | SHLSWDB8 | 810__G | RDHSW | BLUMS | 2 |
| 2026 | July | XASH89 | CARIZOSPG_BEVO_1 | BEVO | CARIZOS | 2 |
| 2026 | July | DCAGMED8 | D5_S1_1 | HOWARD | LEON_CRK | 2 |
| 2026 | July | SBRABND8 | FAI_COLL_1 | FAIRDALE | COLLEGE | 2 |
| 2026 | July | DPHRCTR5 | MDOPHR99_A | MDO | PHR | 2 |
| 2026 | July | SHAYZO25 | 6T227_1 | HAYSEN | ZORN | 2 |
| 2026 | July | DHUTGEA8 | 96T136_1 | MCNEIL_ | WELLBR | 2 |
| 2026 | July | SPETSNU8 | AE_STR26_A | AE | STR | 2 |
| 2026 | July | DWAP_JN5 | BI_SMR98_A | SMITHERS | BI | 2 |
| 2026 | July | DBIGKEN5 | HAMILT_MAXWEL1_1 | MAXWELL | HAMILTON | 2 |
| 2026 | July | DBAKCED5 | MADDUX_TREADW1_1 | TREADWEL | MADDUX | 2 |
| 2026 | July | SSNYCGR8 | SNYDR_FMR1 | SNYDR | SNYDR | 2 |
| 2026 | July | XPRS58 | 1561__A | DPREA | RCSES | 2 |
| 2026 | July | SFMRRY25 | 381__A | FMRVL | RYSSW | 2 |
| 2026 | July | DSCOTKW5 | 6215__A | BCKSW | CGRSW | 2 |
| 2026 | July | MTRYBRO8 | 6217__A | WLVSW | GAILS | 1 |
| 2026 | July | MGARHIC8 | CKT_1027_1 | DUNLAP | DECKER | 1 |
| 2026 | July | SSOLALM8 | COCS_FTST1_1 | FTST | COCS | 1 |
| 2026 | July | DBIGKEN5 | CROSSO_NORTMC1_1 | NORTMC | CROSSOVE | 1 |
| 2026 | July | BASE CASE | CULBSN | n/a | n/a | 1 |
| 2026 | July | DCAGHOW5 | D5_S1_1 | HOWARD | LEON_CRK | 1 |
| 2026 | July | MDBHRSA5 | 12020__B | BRTSW | JUNPR | 1 |
| 2026 | July | STNFTAR8 | 138_FTS_LNC_1 | FTST | LEONCRK | 1 |
| 2026 | July | DTHSFBR5 | 35045__A | SAMSW | FVLSW | 1 |
| 2026 | July | SFTSFVL5 | 35055__A | SAMSW | VENSW | 1 |
| 2026 | July | DLOFOAV5 | BRUNI_69_1 | BRUNI | BRUNI | 1 |
| 2026 | July | SLARLAS8 | DEL_MA_LAREDO1_1 | LAREDO | DEL_MAR | 1 |
| 2026 | July | DELMSAN5 | FURHMAN_VANDB_1 | FURHMAN | VANBLTSS | 1 |
| 2026 | July | STREMAD8 | KATEMC_MASN1_1 | MASN | KATEMCY | 1 |
| 2026 | July | DSGTSCH5 | LAKENA_SAMATH1_1 | LAKENASW | SAMATHIS | 1 |
| 2026 | July | SCARLVO8 | LAKENA_SAMATH1_1 | LAKENASW | SAMATHIS | 1 |
| 2026 | July | SLGDSAP8 | LAKENA_SAMATH1_1 | LAKENASW | SAMATHIS | 1 |
| 2026 | July | XASH89 | LAPRYO_UVALDE1_1 | UVALDE | LAPRYOR | 1 |
| 2026 | July | DRNS_TB5 | NB_THW97_A | THW | NB | 1 |
| 2026 | July | SOAKMCC8 | NEWM_WAL_1 | NEWMAN | WALNUT1 | 1 |
| 2026 | July | SWHILON5 | NUECES_WHITE_2_1 | NUECES_B | WHITE_PT | 1 |
| 2026 | July | DELMSAN5 | POT_OAKS_1 | POTEETS | OAKS9 | 1 |
| 2026 | July | SFORRAY8 | RAY_L_46_1 | RAYBURN | L_463S | 1 |
| 2026 | July | SWALWLN8 | SABIN_NEVAD_1 | NEVADA | SABNCRKT | 1 |
| 2026 | July | MKNGSTE5 | WESLCO_HIDLBRG_1 | MV_HBRG4 | MV_WESL4 | 1 |
| 2026 | July | SWDDMNS5 | 1561__A | DPREA | RCSES | 1 |
| 2026 | July | DELMWWE8 | 1880__E | WCOLO | MRYAV | 1 |
| 2026 | July | SODETES5 | 6052__C | QALSW | TESSW | 1 |
| 2026 | July | XSNY89 | 6690__E | SSFTP | SNYDR | 1 |
| 2026 | July | SSNYCGR8 | 6695__B | SNYDR | AMOTP | 1 |
| 2026 | July | DFRIILL8 | ATSO_SONR1_1 | SONR | ATSO | 1 |
| 2026 | July | DRYSALN5 | COLLE_JUPIT_1 | COLLEGE | JUPITER | 1 |
| 2026 | July | BASE CASE | FURHMAN_VANDB_1 | FURHMAN | VANBLTSS | 1 |
| 2026 | July | SHASTNN8 | G138_8A_1 | PHR | HDNLAKES | 1 |
| 2026 | July | SBRAESC8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 1 |
| 2026 | July | BASE CASE | HHGTOM_1 | HHGT | OMEGA | 1 |
| 2026 | July | DBIGKEN5 | NEVILL_NORTMC_1 | NEVILLSW | NORTMC | 1 |
| 2026 | July | DLOFOAV5 | NLARSW_PILONC1_1 | PILONCIL | NLARSW | 1 |
| 2026 | July | DTWLCED5 | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 1 |
| 2026 | July | DDSNGBY8 | TWGWF_66_A | WF | TWG | 1 |
| 2026 | July | BASE CASE | 138_ALV_NAL_1 | TNNALVIN | ALVIN | 1 |
| 2026 | July | SWORBRD8 | 138_WIC_STG_1 | WICKETT | STAGHORN | 1 |
| 2026 | July | DSALHUT5 | 1710__B | SONTERRA | JREST | 1 |
| 2026 | July | STMPTMP5 | 300__A | TMPSW | TMPCR | 1 |
| 2026 | July | DMTSCOS5 | 6240__C | SACRC | DPCRK | 1 |
| 2026 | July | DMBDRKC5 | 651__C | CMNTP | SHILO | 1 |
| 2026 | July | SANACN25 | 835__G | GTRSW | EPPOI | 1 |
| 2026 | July | DHUTGEA8 | 921T163_1 | HWRDTP | MCNEIL_ | 1 |
| 2026 | July | ULOPUNI1 | BENTS_FRTER_1B_1 | FRONTERA | S_MISSIN | 1 |
| 2026 | July | DSTOGAR8 | CKT_1027_1 | DUNLAP | DECKER | 1 |
| 2026 | July | MGARSTO8 | CKT_1027_1 | DUNLAP | DECKER | 1 |
| 2026 | July | DELMSAN5 | F2_11_1 | KENEDSW | F2 | 1 |
| 2026 | July | DFOAVLO5 | FREER_LOBO1_1 | LOBO | FREER | 1 |
| 2026 | July | SCRTIOL8 | IOLA_KEITHSW_1 | IOLA | KEITHSW | 1 |
| 2026 | July | STRECFL8 | KATEMC_MASN1_1 | MASN | KATEMCY | 1 |
| 2026 | July | SSTPESP8 | LAN_CT_PAVLOV1_1 | PAVLOV | LAN_CTY | 1 |
| 2026 | July | SFTLMES8 | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 1 |
| 2026 | July | SKINODE5 | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 1 |
| 2026 | July | SFURVAN8 | RAYBURN_69_2 | RAYBURN | RAYBURN | 1 |
| 2026 | July | SFURVAN8 | RAY_MOURSUND_1 | MOURSUND | RAYBURN | 1 |
| 2026 | July | SBE2ASH8 | WCR_CARI_1 | WCRYSTS | CARIZOS | 1 |
| 2026 | July | BASE CASE | WILBRN | n/a | n/a | 1 |
| 2026 | July | BASE CASE | ZAPSTR | n/a | n/a | 1 |
| 2026 | July | DWTRWLV5 | 3610__G | PGTP1 | PDSES | 1 |
| 2026 | July | DCPSST58 | 651__B | CMNSW | CMNTP | 1 |
| 2026 | July | DVENFTS5 | 810__G | RDHSW | BLUMS | 1 |
| 2026 | July | DBAKCED5 | LAKENA_SAMATH1_1 | LAKENASW | SAMATHIS | 1 |
| 2026 | July | XMDO58 | MDO_AT1 | MDO | MDO | 1 |
| 2026 | July | SMCEABS8 | MKLT_TRNT1_1 | TRNT | MKLT | 1 |
| 2026 | July | DBIGSCH5 | SANTAR_WOLFCA1_1 | WOLFCAMP | SANTARIT | 1 |
| 2026 | July | BASE CASE | SWEETWN2_XF21 | SWEETWN2 | SWEETWN2 | 1 |
| 2026 | July | SDIMBEV8 | UVALDE_W_BATE1_1 | W_BATESV | UVALDE | 1 |
| 2026 | July | MCYPHKB8 | 1160__A | HKBRY | VLYRN | 1 |
| 2026 | July | DALASOA8 | 138_FTS_LNC_1 | FTST | LEONCRK | 1 |
| 2026 | July | SSTAWIC8 | 138_WOR_HRT_1 | HARPOONT | WORSHAM | 1 |
| 2026 | July | SHELBUL5 | 35045__A | SAMSW | FVLSW | 1 |
| 2026 | July | SBCEBGR5 | 421__A | BCESW | SNDSW | 1 |
| 2026 | July | XSNY89 | 6690__E | SNYDR | SSFTP | 1 |
| 2026 | July | DBEANOR5 | 6965__A | LNGSW | PRLSW | 1 |
| 2026 | July | DSLKNOR5 | 6965__A | LNGSW | PRLSW | 1 |
| 2026 | July | SMARALM9 | ALMC_PAIS1_1 | ALMC | PAIS | 1 |
| 2026 | July | SFTCGAR8 | BALLINGE_FMRL | BALLINGE | BALLINGE | 1 |
| 2026 | July | SBROALP9 | COCS_FTST1_1 | COCS | FTST | 1 |
| 2026 | July | SMOOPEA8 | DILLY_PEARSA1_1 | DILLY | PEARSAL1 | 1 |
| 2026 | July | DCOTWR25 | FARMLAND_LONGD_1 | FARMLAND | W_LD_345 | 1 |
| 2026 | July | DBAKCED5 | FORTMA_YELWJC1_1 | FORTMA | YELWJCKT | 1 |
| 2026 | July | DBIGSCH5 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 1 |
| 2026 | July | DSGTSCH5 | HARGRO_TWINBU1_1 | TWINBU | HARGROVE | 1 |
| 2026 | July | XHHG58 | HHGT_T2H | HHGT | HHGT | 1 |
| 2026 | July | SALIKIN8 | ORNGROV_69_1 | ORNGROV | ORNGROV | 1 |
| 2026 | July | BASE CASE | SN_STR26_A | SN | STR | 1 |
| 2026 | July | BASE CASE | THOMASTN_PS1 | THOMASTN | THOMASTN | 1 |
| 2026 | July | BASE CASE | UVALDE | n/a | n/a | 1 |
| 2026 | July | SPRIHAR8 | WESLCO_HIDLBRG_1 | MV_HBRG4 | MV_WESL4 | 1 |
| 2026 | July | DLONPK25 | 12020__B | BRTSW | JUNPR | 1 |
| 2026 | July | SBLAWDB8 | 1210__B | HUBRD | HAN1 | 1 |
| 2026 | July | DPHRAL58 | 138_ALV_NAL_1 | TNNALVIN | ALVIN | 1 |
| 2026 | July | SPIGSOL8 | 138_FTS_LNC_1 | FTST | LEONCRK | 1 |
| 2026 | July | SHELBUL5 | 235__A | SGRSW | JEWET | 1 |
| 2026 | July | SPACVLS5 | 403__A | PRSSW | VLYSO | 1 |
| 2026 | July | SSUNRGR8 | 6240__C | SACRC | DPCRK | 1 |
| 2026 | July | SRAIMAD8 | BENTS_FRTER_1B_1 | FRONTERA | S_MISSIN | 1 |
| 2026 | July | SILLFTL8 | CTHR_TINSLE1_1 | TINSLEY | CTHR | 1 |
| 2026 | July | DVICEDN8 | FURHMAN_VANDB_1 | FURHMAN | VANBLTSS | 1 |
| 2026 | July | SBRAPIN8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 1 |
| 2026 | July | SCISPUT8 | LENSW_PUTN2_1 | LENSW | PUTN | 1 |
| 2026 | July | SCOMHA38 | MAXWEL_WHITIN1_1 | MAXWELL | WHITING | 1 |
| 2026 | July | SALVTNN8 | 138_FWP_MNL_1 | FRWYPARK | MAINLAND | 1 |
| 2026 | July | SPRAWAL8 | 155T217_1 | BELLSO | PT | 1 |
| 2026 | July | DWTRWLV5 | 3170__B | SMPST | BNTDR | 1 |
| 2026 | July | MBULSAM5 | 35045__A | SAMSW | FVLSW | 1 |
| 2026 | July | MBULNAV5 | 505__B | FBRSW | THSES | 1 |
| 2026 | July | DBRHLIG8 | 6405__C | HLSES | RMTPW | 1 |
| 2026 | July | SCLCGTN8 | 6635__G | MRVLY | ESTLD | 1 |
| 2026 | July | SFLTLNG8 | 6635__G | MRVLY | ESTLD | 1 |
| 2026 | July | SDAFDES8 | CKT_1027_1 | DUNLAP | DECKER | 1 |
| 2026 | July | SCRDJON5 | HOOD_DECRDVA_1 | DCDAM | HOD | 1 |
| 2026 | July | SN_SLON5 | KINGSV_KLEBER1_1 | KLEBERG | KINGSVIL | 1 |
| 2026 | July | SMOOPEA8 | PALDRO_DILLEY_1 | PALODURO | DILLEYSW | 1 |
| 2026 | July | DRAZSA89 | READIN_UVALDE1_1 | UVALDE | READING | 1 |
| 2026 | July | SMV_PAR8 | RIOHND_ERIOHND_1 | MV_RIOHO | RIOHONDO | 1 |
| 2026 | July | DBAKCED5 | SCHNDR_BIGHIL2_2 | SCHNDR | BIGHIL | 1 |
| 2026 | July | SZENTH35 | THWZEN71_A | ZEN | THW | 1 |
| 2026 | July | SREAUVA8 | UVLD_DOWI_1 | DOWNIES | UVLDES | 1 |
| 2026 | July | DSALKLN5 | 1270__F | KFHSW | KLNFH | 1 |
| 2026 | July | SSALTMP5 | 1270__F | KFHSW | KLNFH | 1 |
| 2026 | July | SMYPHLS9 | 2270__B | MEXTP | ITALY | 1 |

Current Wind Generation Record: 29,031 MW on 06/29/2026 at 02:00 | Current Wind Penetration Record: 69.15% on 04/10/2022 at 01:43

Current Solar Generation Record: 35,427 MW on 07/30/2026 at 13:33 | Current Solar Penetration Record: 72.74% on 05/02/2026 at 11:28