## Slide 1
ERCOT 2026 UFLS Survey Results Shane Herrera
Outline:
Background
2026 UFLS Survey Activity Timeline
2026 Survey Results – Standard UFLS Stages
2026 Survey Results – Anti-Stall Stages

## Slide 2: Background on the ERCOT UFLS Survey and Requirements​
ERCOT coordinated and conducted the 2026 survey with ERCOT Transmission Operators (TOs.) The survey serves to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event. ​
The table below is taken from the ERCOT Nodal Operating Guides, Section 2.6.1 (1), Requirements for Under-Frequency Load Shedding, and lists the required load shed amounts:​
ERCOT Nodal Operating Guides, Section 2.6.1 (2) ​
ERCOT will, prior to the peak each year, survey each TO’s compliance with the automatic Load shedding requirements described in paragraph (1) above, and report its findings to the Technical Advisory Committee (TAC). For purposes of determining a TO’s compliance with this annual survey requirement, TO Load will be the total amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, at the specified time of the survey.​
Frequency Threshold | Load Relief
59.3 Hz ​ | At least 5% of the TO Load​
59.1 Hz​ | A total of at least 5% of the TO Load​
58.9 Hz ​ | A total of at least 15% of the TO Load​
58.7 Hz​ | A total of at least 15% of the TO Load​
58.5 Hz ​ | A total of at least 25% of the TO Load​

## Slide 3: 2026 UFLS Survey Activity Timeline​
Below is the timeline reflecting the survey dates and activities:​
Date​ | Activity​
March 24 | Announcement of survey timeline to OWG​
April 6 | Market Notice sent to Authorized TO Representatives​
May 6 @ 11:00 AM​ | Date and time of survey​
July 7 | Survey results due to ERCOT​
August 25 | Results reported to OWG
October 1 | Results reported to ROS

## Slide 4: Standard UFLS Stages - 2026 Survey Results​
The overall results of the 2026 UFLS survey are reflected in the table below:​
Frequency Threshold​ | Minimum Requirement​ | 2026 Survey ​ Measurement​
59.3 Hz​ | At least 5% of the TO Load​ | 6.92%​
59.1 Hz​ | A total of at least 5% of the TO Load​ | 10.02%​
58.9 Hz ​ | A total of at least 15% of the TO Load​ | 19.22%​
58.7 Hz​ | A total of at least 15% of the TO Load​ | 22.34%​
58.5 Hz​ | A total of at least 25% of the TO Load​ | 31.20%​
TOs successfully met the UFLS requirements for all five thresholds.​
​
The ERCOT load at the time of the survey was 52,790 MW.​

## Slide 5: Standard UFLS Stages, NOGRR247​
NOGRR247 (approved on 10/12/2023 and effective no earlier than October 1, 2026) will modify the ERCOT automatic UFLS program by increasing the number of Load shed stages from three to five and changing the TO Load relief amounts to uniformly increment by 5% for each stage. The NOGRR also adds a UFLS minimum time delay of six cycles (0.1 seconds). ​
Frequency Threshold​ | Minimum Requirement​ | Delay to Trip​
59.3 Hz​ | At least 5% of the TO Load​ | At least six cycles but no more than 30 cycles​
59.1 Hz ​ | A total of at least 10% of the TO Load​ | At least six cycles but no more than 30 cycles​
58.9 Hz​ | A total of at least 15% of the TO Load​ ​ | At least six cycles but no more than 30 cycles​ ​
58.7 Hz​ | A total of at least 20% of the TO Load​ ​ | At least six cycles but no more than 30 cycles​ ​
58.5 Hz​ | A total of at least 25% of the TO Load​ ​ | At least six cycles but no more than 30 cycles​ ​
All ERCOT TOs have started implementation of the additional UFLS stages. Six TOs have completed implementation and provided responses and data confirming full implementation.
Reference: ERCOT Nodal Operating Guides Section 2: System Operations and Control Requirements​

## Slide 6: Previous Year Comparison of Standard UFLS Stages​
​The overall results of the 2025 and 2026 UFLS surveys are reflected in the table below:​
Frequency Threshold​ | Minimum Requirement​ | 2025 Survey ​ Measurement​ | 2026 Survey ​ Measurement​
59.3 Hz​ | At least 5% of the TO Load​ | 6.66%​​ | 6.92%​
59.1 Hz​ | A total of at least 5% of the TO Load​ | 8.47%​​ | 10.02%​
58.9 Hz ​ | A total of at least 15% of the TO Load​ | 18.26%​​ | 19.22%​
58.7 Hz​ | A total of at least 15% of the TO Load​ | 20.16%​​ | 22.34%​
58.5 Hz​ | A total of at least 25% of the TO Load​ | 30.66%​​ | 31.20%​
The ERCOT load at the time of the survey was 52,790 MW. In comparison, the 2025 ERCOT load was 54,343 MW.​
​

## Slide 7: Supplemental/Anti-Stall UFLS Stages​
​ERCOT Nodal Operating Guides 2.6.1 (1)​ ​
“TOs may, but are not required to, provide supplemental anti-stall under-frequency Load relief in the amounts described in Table 2, Supplemental Anti-Stall UFLS Stages, below. If the TOs provide supplemental anti-stall under-frequency Load relief, the under-frequency relays shall be set to use the frequency thresholds and time delays described in Table 2. For the purposes of this paragraph, the TO Load will be the amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, when the ERCOT frequency drops to the 59.5 Hz threshold.”
Frequency Threshold​ | Minimum Requirement​ | Delay to Trip​
59.5 Hz​ | At least 1.5% of the TO Load​ | 90 seconds​
59.5 Hz ​ | A total of at least 3.0% of the TO Load ​ | 120 seconds​
59.5 Hz​ | A total of at least 4.5% of the TO Load​ | 150 seconds​
Reference: ERCOT Nodal Operating Guides Section 2: System Operations and Control Requirements​

## Slide 8: Annual UFLS Survey – Anti-Stall UFLS Stages​
​The overall results of the 2026 UFLS survey are reflected in the table below:​
Frequency Threshold / Delay to Trip​ | Minimum Requirement​ | 2026 Survey ​ Measurement​
59.5 Hz / 90s​ | At least 1.5% of the TO Load​ | 1.34%​
59.5 Hz / 120s​ | A total of at least 3.0% of the TO Load ​ | 2.36%​
59.5 Hz / 150s​ | A total of at least 4.5% of the TO Load​ | 3.14%​

## Slide 9: Supplemental/Anti-Stall UFLS Stages, NOGRR226​
NOGRR226 (approved on 1/26/2023 and effective no earlier than October 1, 2026) will modify ERCOT Nodal Operating Guides 2.6.1 (1)​
​
“In the event of an under-frequency event, each Transmission Operator (TO) shall provide Load relief by shedding the required percentage of its Distribution Service Provider (DSP)-connected Load and transmission-level Customer Load using automatic under-frequency relays, as specified in Table 1, Standard UFLS Stages, and Table 2, Supplemental/Anti-Stall UFLS Stages, below. For the purposes of this paragraph, the TO Load will be the amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, when the ERCOT frequency drops to the 59.5 Hz threshold.”​
​
Eight ERCOT TOs have started implementation of the Supplemental/Anti-Stall UFLS Stages. Four TOs have completed implementation and provided responses and data confirming full implementation.

## Slide 10: Previous Year Comparison of Anti-Stall UFLS Stages​
Frequency Threshold / Delay to Trip​ | Minimum Requirement​ | 2025 Survey ​ Measurement​ | 2026 Survey ​ Measurement​
59.5 Hz / 90s​ | At least 1.5% of the TO Load​ | .31%​ | 1.34%​
59.5 Hz / 120s​ | A total of at least 3.0% of the TO Load ​ | .53%​ | 2.36%​
59.5 Hz / 150s​ | A total of at least 4.5% of the TO Load​ | .73%​ | 3.14%​
The ERCOT load at the time of the survey was 52,790 MW. In comparison, the 2025 ERCOT load was 54,343 MW.​
​
​The overall results of the 2025 and 2026 UFLS survey are reflected in the table below:​

## Slide 11: Questions/Comments?
ERCOT Compliance appreciates all entities participation in the 2026 UFLS Survey. ​
Conclusion ​