## Slide 1: Operations Working Group Meeting Notes
Chair- Rickey Floyd
Vice-Chair- Tyler Springer
8/25/2026

## Slide 2: ERCOT Updates and System Operation Report
July unofficial peak load on July 22th HE18 at 91,134 MW. This is a new all time demand record surpassing the previous record of 85,508 MW on Aug 10, 2023. Roughly a 5,600 MW increase.
Solar generation record of 35,427 MW on July 30 with a penetration of 41.62%

## Slide 3: Texas Reliability Entity Report
Talk with Texas Podcast - 8/25 Defenders Guide to AI and Machine Learning.
Talk with Texas Podcast – 10/8 Operational Technology
Board of Directors meeting on 9/16

## Slide 4: HITE List Review
Reviewed requests for removals of each requesting TO.
  LCRA recommended 1 addition based on recent congestion.
    Wells Branch – Howard Lane Tap LN 138 26/07 DCKT Hutto to Round Rock 138kV and Hutto to Georgetown South 138kV McNeil-Wells Branch, McNeil-Howard Lane Tap RT Planned WELLBR HWRDTP 378T378 DHUTGEA9
OWG endorses proposed removals / additions to MTE list.

## Slide 5: 2026 UFLS Survey Results
TO’s successfully met the UFLS results for all 5 thresholds. The ERCOT load at the time of the survey was 52,790 MW.
  59.3 Hz – 6.92%
  59.1 Hz – 10.02%
  58.9 Hz – 19.22%
  58.7 Hz – 22.34%
  58.5 Hz – 31.20%
Supplemental / Anti-Stall UFLS Stages (Currently Voluntary)
  59.5 Hz 90s – 1.34% (1.5% requirement)
  59.5 Hz 120s – 2.36% (3.0% requirement)
  59.5 Hz 150s – 3.14% (4.5% requirement)
  8 TO’s have started implementation
  4 TO’s have completed implementation

## Slide 6: Operations Analysis Discussion on Implementation of NOGRR266 (Fabian Yepo)
  ERCOT is requesting TO’s that have not fully implemented to send Operations Analysis an email explaining why they have not implemented the requirements yet.
    Send notification to the same UFLS email chain, or directly to Fabian at fabian.yepo@ercot.com
  Please notify the expected date when it will be implemented.
  Internal discussion ongoing at ERCOT on projected implementation date for NOGRR266, ERCOT will present results of discussion at next OWG.

## Slide 7: NPRR 1340 Dispatchable Reliability Reserve Service Ancillary Service with Energy Storage Resource Participation
  Overview of NPRR, no discussion from OWG.

## Slide 8: NOGRR 288 Related to NPRR1340, Dispatchable Reliability Reserve Service Ancillary Service with Energy Storage Resource Participation
  Overview of NOGRR, no discussion from OWG.

## Slide 9: ERCOT SWD Reporting and 2026 Update
  Severe weather drill is for a winter storm this year.
  The 2026 SWD is scheduled for October 14th. Market notice to come out in September.

## Slide 10: Other Business
  None