## Slide 1: Batch 1+
October 15, 2026
Stakeholder workshop #3

## Slide 2
1. Antitrust admonition
2. PUCT 58481 Discussion
3. Pre-Batch Portal Process Discussion (LIOO)
4. Other Batch details
5. Batch Large Load Reporting/Transparency
6. BYOG/PCLR Enhancement Discussion
7. Adjourn
2
On the agenda
PUBLIC

## Slide 3
1. Antitrust admonition
2. PUCT 58481 Discussion
3. Pre-Batch Portal Process Discussion (LIOO)
4. Other Batch details
5. Batch Large Load Reporting/Transparency
6. BYOG/PCLR Enhancement Discussion
7. Adjourn
3
On the agenda
PUBLIC

## Slide 4: PUCT Project 58481: Process flow
Default process flow in 16 TAC §25.194
ILLE sends request to TSP / DSP
ILLE and TSP / DSP enters into intermediate agreement*
Interconnecting TSP / DSP submit to ERCOT to initiate interconnection study
ERCOT initiates interconnection study
ERCOT provides updates on interconnection study
60 days
Inform ILLE
5 working days
Inform ILLE
5 working days
Inform ILLE
5 working days / update
Interconnecting TSP / DSP, or ERCOT provides timely notification of transmission capacity allocated to the ILLE
Execute and fund the SLLIA1 (including disclosure updates)
Post security, pay CIAC in cash, and agree to pay large load minimum billing demand
*Intermediate agreement requirements:
TSP/DSP study fee ($100K)
ERCOT study fee (TBD)
Financial security for system upgrades ($50K/MW)
Disclosures, including site control, similar interconnection requests, site progress, phased energization schedules, water usage, state and local regulatory approvals, backup generation / onsite facilities, controllability, plans for power supply
ERCOT Batch study
60 days
Other major topics
This rule standardizes interconnection requests for all load types
If an ILLE does not hit milestones (e.g., energizing within time period), they will lose allocated capacity; refund terms have also been changed
All curtailment is outside of this rule
Competitively sensitive information is treated as protected
Every process step is subject to audit and verification
Interconnection study

## Slide 5
1. Antitrust admonition
2. PUCT 58481 Discussion
3. Pre-Batch Portal Process Discussion (LIOO)
4. Other Batch details
5. Batch Large Load Reporting/Transparency
6. BYOG/PCLR Enhancement Discussion
7. Adjourn
5
On the agenda
PUBLIC

## Slide 6
PUBLIC
Load Integration & Ongoing Operations (LIOO) Overview
LIOO is ERCOT's centralized application and data repository for Large Loads
A single location to request, collect, and maintain Large Load information
Supports the Large Load lifecycle from interconnection through ongoing operations
Improved visibility into interconnection status
ERCOT is still working to develop process sequence and hand-offs within the overall process1
1. Will be discussed in later workshop

## Slide 7
Anticipated Release: December 2026
PUBLIC
Centralized Large Load Data: Centralized repository for Large Load project information
Project Visibility: External Participants can view applicable project status through dashboards
Read-Only Access: External Participants will initially have read-only access
ERCOT Data Management: For the initial release, ERCOT will enter and maintain Large Load data
Initial Release – What to Expect

## Slide 8: External Participant Dashboard (1/2)
Sample data generated for demonstration purposes only
The initial LIOO release will include an External Participant dashboard showing projects associated with the logged-in user
NOTE: This is a preliminary version. Field names and labels are subject to change as the design is further refined

## Slide 9: External Participant Dashboard (2/2)
Sample data generated for demonstration purposes only
Users will have the ability to drill down into a project to see additional details
NOTE: This is a preliminary version. Field names and labels are subject to change as the design is further refined

## Slide 10: What Comes Next?
Future Enhancements
Capabilities continue to evolve with Large Load processes and requirements
Pre-Batch 1 Release
TSPs and ILLEs will be able to enter and manage information directly in LIOO
Initial Release
(Dec 2026)
Data entered and maintained by ERCOT
External Participants have read-only access

## Slide 11
1. Antitrust admonition
2. PUCT 58481 Discussion
3. Pre-Batch Portal Process Discussion (LIOO)
4. Other Batch details
5. Batch Large Load Reporting/Transparency
6. BYOG/PCLR Enhancement Discussion
7. Adjourn
11
On the agenda
PUBLIC

## Slide 12: Batch processes: Batch re-study proposals
Q6: ILLEs with unfulfilled ramp: ERCOT is proposing that ILLEs with unfulfilled ramp may request re-study under their original Large Load Batch (LLB) tracking number
Q7: Uncommitted large loads: ERCOT is proposing for large load projects that did not commit in prior Batch, that they may request inclusion in subsequent Batch studies, provided they (i) formally request it and (ii) pay a new study fee. The ILLE’s financial security, intermediate agreement, LL tracking number, and all portal information would carry forward to the new Batch study
Q8: Large loads excluded from Batch Zero: ERCOT is proposing to allow large loads that received a tracking number, but were excluded from Batch Zero, to request inclusion in Batch One. ERCOT will waive the subsequent Batch fee if the interconnecting TSP/DSP attests that the ILLE has already paid at least $100k in study fees for the project. The ILLE must meet all other Batch One study requirements
Q6-8: Do you agree with ERCOT’s proposed approach [to the following issues]? % of respondents
PUBLIC
Source: CTP TSP survey, fielded 09/15–09/21 (n = 74 respondents; 15 blank responses)
Chart: 
 | 66.6667 | 81.8182 | 76 | 87.5 | 76.2712
 | 13.3333 | 9.0909 | 8 | 12.5 | 10.1695
 | 20 | 9.0909 | 16 | 0 | 13.5593
TSP
ILLE
Generators
Others
Total
Yes
No
No Opinion
Chart: 
 | 86.6667 | 54.5455 | 72 | 75 | 72.8814
 | 0 | 36.3636 | 8 | 25 | 13.5593
 | 13.3333 | 9.0909 | 20 | 13.5593
TSP
ILLE
Generators
Others
Total
# of respondents
xx
15
11
25
8
Chart: 
 | 73.3333 | 63.6364 | 76 | 100 | 76.2712
 | 6.6667 | 18.1818 | 24 | 0 | 5.0847
 | 20 | 18.1818 | 18.6441
TSP
ILLE
Generators
Others
5%
Total
59
15
11
25
8
59
15
11
25
8
59
Majority of respondents (73-76%) agree with ERCOT’s three proposed approaches to improve the Batch process
ERCOT considers stakeholder conceptual review substantially complete for these items. ERCOT will begin incorporating them into Revision Requests.

## Slide 13: Potential changes to large loads (1/2)
For ILLE changes to batch projects: ILLE must submit change request in the portal, with the following rules
Preliminary
Treatment / restudy rule1
Potential change
In-service date (forward or backward)
1
Project MWs (increase or decrease)
2
Change LCP (ramp)
3
  Administrative change
Change ownership
4
  Restudy in next Batch, unless ERCOT determines the new POI is electrically equivalent
Change POI
5
  See "Change load characteristics (dynamics)"
Change type of load
6
1. Restudy detailed on slide 24
  If earlier date, subject to restudy, while maintaining keep base load status for prior commitments.
  If later date, no restudy and will be reflected in next Batch / CTP study
  If increase in size, subject to restudy, while maintaining base load status for prior commitments
  If decrease, no restudy
  If increase and/or earlier LCP ramp amount, subject to restudy, while maintaining base load status for prior commitments
  If decrease and/or later LCP ramp amount, no restudy but will be reflected in next Batch / CTP study
ERCOT considers stakeholder conceptual review substantially complete for these items. ERCOT will begin incorporating them into Revision Requests.

## Slide 14: Potential changes to large loads (2/2)
1. Restudy detailed on slide 18
2. Including reactive consumption
For ILLE changes to batch projects: ILLE must submit change request in the portal, with the following rules
Preliminary
Treatment / restudy rule1
Potential change
  See next slide
Change load characteristics (dynamics)2
7
  Administrative change
Change DSP
8
  Administrative change if no POI change; otherwise see “Change POI”
Change TSP
9
  No restudy if electrically similar; otherwise restudy in next Batch
Split the project into multiple projects
10
  Administrative change
Change disclosure info
11
  No restudy if electrically similar; otherwise restudy in next Batch
Change co-location status
12
  Can cancel and be removed at any time, but there will be a deadline for reflecting that change in the current Batch / CTP study
Cancel
13
ERCOT considers stakeholder conceptual review substantially complete for these items. ERCOT will begin incorporating them into Revision Requests.

## Slide 15: Evaluation of Changing Load Characteristics (dynamics)
Evaluation Principle and Guidelines
  If the changes negatively impact dynamic performance, a restudy is needed
  If the changes are equal or better from a dynamic performance perspective, an assessment is needed without affecting the allocation
Load does not need to be restudied in a subsequent batch, but it does need to be assessed in the next batch stability study, which does not affect its allocation but could impact its Initial Energization date
No
No
Yes
Yes
1. VRT/FRT Impact Check
Load must be restudied in a subsequent batch
ERCOT checks the dynamic model to determine if there's an adverse impact on VRT or FRT performance
2. Dynamics Impact Check
Is there an adverse impact on VRT or FRT performance?
Is there a material impact to the dynamics?
No restudy is needed
ERCOT checks the dynamic model to determine if there’s a material impact to the dynamics
Start
VRT = Voltage Ride Through
FRT = Frequency Ride Through
Preliminary
ERCOT considers stakeholder conceptual review substantially complete for these items. ERCOT will begin incorporating them into Revision Requests.

## Slide 16: What does “Restudy in the next Batch” mean?
Unless otherwise noted, a restudy means:
The Large Load will forfeit any previously allocated MWs
The Large Load will enter the next Batch as a “studied load”
The Large Load must pay the Batch study fee and meet all other prerequisites for the Batch study, including any relevant deadlines
Preliminary
ERCOT considers stakeholder conceptual review substantially complete for these items. ERCOT will begin incorporating them into Revision Requests.

## Slide 17
1. Antitrust admonition
2. PUCT 58481 Discussion
3. Pre-Batch Portal Process Discussion (LIOO)
4. Other Batch details
5. Batch Large Load Reporting/Transparency
6. BYOG/PCLR Enhancement Discussion
7. Adjourn
17
On the agenda
PUBLIC

## Slide 18: Batch reporting/transparency: Overview
NPRR 1267 as a starting point for Large Load transparency (approved June 2025, not implemented)
3.2.7 Large Load Interconnection Status Report
(1) For purposes of this section, a Large Load is inclusive of one or more Facilities at a single site with an aggregate peak Demand greater than or equal to 75 MW behind one or more common Points of Interconnection (POIs) or Service Delivery Points that is seeking interconnection on or after March 25, 2022. ERCOT may expand the criteria for including a Load as a Large Load, provided the defining criteria are clearly stated in the applicable report.
(2) ERCOT must publish a Large Load Interconnection status report each month to the ERCOT website that aggregates Large Load Interconnection requests across multiple dimensions with as much specificity as possible while maintaining the confidentiality of Customer data, including:
(a) Load Zone;
(b) TSP;
(c) Load type (as provided to the TSP, such as refinery, steel mill, data center, etc...);
(d) Calendar quarter and year in which the interconnecting TSP submitted the project to ERCOT;
(e) Requested energization quarter and year;
(f) Size range;
(g) Interconnection status (as defined by ERCOT to differentiate between operational, approved, under study, etc.);
(h) Co-location status.
Preliminary

## Slide 19: Batch reporting/transparency: Overview
NPRR 1267 as a starting point for Large Load transparency (approved June 2025, not implemented)
3.2.7 Large Load Interconnection Status Report
(3) ERCOT shall take actions such as providing ranges of interconnection MW sizes, aggregate loads, and other similar actions to protect, anonymize, and otherwise safeguard confidential and competitively-sensitive Customer data from public disclosure. When aggregating Customer data, ERCOT should ensure that at least five Customers exist in a particular Load type subcategory prior to aggregation, to protect against accidental disclosure. ERCOT may leave a certain category blank or aggregated with other Load types to avoid disclosure.
ERCOT shall report to TAC or its designated subcommittee its methodology for developing the report defined in paragraph (2) above whenever that methodology changes, but at least every two years.
Preliminary

## Slide 20: Batch reporting/transparency: Survey results
PUBLIC
Source: CTP TSP survey, fielded 09/15–09/21 (n = 74 respondents; 41 blank responses).
Preliminary
Q34: NPRR1267 establishes a monthly aggregated Large Load report to improve transparency. The report includes the data elements listed below, with protections to prevent disclosure of confidential information when aggregation levels are not adequate to maintain anonymity. Please list any reporting elements you would like added or modified.
Data elements: Load zone, TSP, load type (as provided to the TSP), TSP submission to ERCOT quarter, requested energization quarter and year size range, interconnection status, co-location status
Data element
Example data element details
Ramp & energization performance detail (11)
  Requested ramp by quarter
  Actual MW energized vs. approved ramp schedule
  Energized MW vs. requested MW
  Average timeline from application to energization
Locational detail (9)
  County and/or city, including geographic coordinates
  Proposed or actual POI
Batch/study & agreement status detail (8)
  Batch or study cohort
  Intermediate Agreement and financial security status
  Commitment status following Batch study
  Standardized readiness milestones (e.g., site control, permits, construction status)
Data-center load-type sub-categorization (2)
  Data center type (e.g., AI training, AI inference, cloud, enterprise, crypto)
Project configuration / technology classification (11)
  BYOG/WLPUN/PCLR election or designation
  Back up generation type (e.g., islanded generation, backup generation, WLPUN/BYOG)
  Generation resource type for co-located projects (solar, wind, BESS, gas)
  Respondents flagged the need to protect confidentiality: Concerns include the ability to identify customers from broad data, lack of appropriate aggregation thresholds, and clarity on data that will not be published

## Slide 21: Existing GIS report provides a starting point to define Large Load reporting attributes
# | GIS attribute | Include in Large Load report?
Project attributes |  | 
1 | INR | 🟡 Conditional
2 | Project Name | ❌ No
3 | GIM Study Phase | ✅ Yes
4 | Interconnecting Entity | ❌ No
5 | POI Location | 🟡 Conditional
6 | County | 🟡 Conditional
7 | CDR Reporting Zone | ✅ Yes
8 | Projected COD | ✅ Yes
9 | Fuel | 🟡 Conditional
10 | Technology | 🟡 Conditional
11 | Capacity (MW) | ✅ Yes
12 | Changes from Last Report | ✅ Yes
Project milestone dates |  | 
13 | Approval Date for Submission of Proof of Site Control | 🟡 Conditional
14 | Screening Study Started | 🟡 Conditional
15 | Screening Study Complete | 🟡 Conditional
16 | FIS Requested | 🟡 Conditional
17 | FIS Approved | ✅ Yes
18 | Economic Study Required | ❌ No
19 | IA Signed | ✅ Yes
20 | Financial Security and Notice to Proceed Provided | 🟡 Conditional
21 | Air Permit | 🟡 Conditional
22 | GHG Permit | 🟡 Conditional
23 | Water Availability | 🟡 Conditional
24 | Meets Planning Guide Section 6.9(1) Requirements for Inclusion in Planning Models | 🟡 Conditional
25 | Meets All Planning Guide Section 6.9 Requirements for Inclusion in Planning Models | 🟡 Conditional
26 | Meets Planning Guide QSA (Section 5.9) Prerequisites | ✅ Yes
27 | Construction Start | 🟡 Conditional
28 | Construction End | 🟡 Conditional
29 | Approved for Energization | ✅ Yes
30 | Approved for Synchronization | ❌ No
31 | Comment | ❌ No
GIS report attribute
Include equivalent in LL report?
GIS report attribute
Include in LL report?
3
GIM Study Phase
2
Project Name
1
INR
4
Interconnecting Entity
5
POI Location
6
County
7
CDR Reporting Zone
8
Projected COD
9
Fuel
10
Technology
11
Capacity (MW)
13
Approval Date for Submission of Proof of Site Control
12
Changes from Last Report
14
Screening Study Started
15
Screening Study Complete
16
FIS Requested
17
FIS Approved
18
Economic Study Required
19
IA Signed
20
Financial Security and Notice to Proceed Provided
21
Air Permit
22
GHG Permit
23
Water Availability
24
Meets Planning Guide Section 6.9(1) Requirements for Inclusion in Planning Models
25
Meets All Planning Guide Section 6.9 Requirements for Inclusion in Planning Models
26
Meets Planning Guide QSA (Section 5.9) Prerequisites
29
Approved for Energization
27
Construction Start
28
Construction End
30
Approved for Synchronization
No
Yes
Conditional
Do we need any other attributes to add to the Large Load report?
Source: ERCOT Generator Interconnection Status (GIS) Report, “Project Details – Large Gen” tab

## Slide 22
1. Antitrust admonition
2. PUCT 58481 Discussion
3. Pre-Batch Portal Process Discussion (LIOO)
4. Other Batch details
5. Batch Large Load Reporting/Transparency
6. BYOG/PCLR Enhancement Discussion
7. Adjourn
22
On the agenda
PUBLIC

## Slide 23: BYOG/PCLR enhancements: Under evaluation (1/2)
Category
Enhancement
Description
WLPUN registration and lifecycle
WLPUN opt-out option during Commitment
Allow a Large Load with WLPUN to elect to be a standalone Large Load if the batch study results in full withdrawal capability for the load; i.e., cancel the GINR project without losing the load allocation
1
WLPUN exit plan
Define how a WLPUN can transition to different registration upon completion of energization of planned facilities (load, generation, and transmission upgrades as applicable)
2
WLPUN generation additions
Define how to add more generation to an existing/planned WLPUN site.
3
WLPUN on-ramp for existing Large Load
Define how to add generation to an existing/planned standalone Large Load so that it becomes a WLPUN
4
WLPUN enhancements
WLPUN Dynamic Limits
Define how WLPUN withdrawal limits could change from static to dynamic values in real-time
5
Large load self-supply outside of Batch
Allow a Large Load with generation to connect before going through the batch if the load ensures that it will not consume from the grid until after it goes through a batch process, i.e., use the GINR process
6
WLPUN with Settlement Only Generation
Allow a WLPUN to use Settlement Only generation
7
Alternative BYOG enhancements
Large Load island transition to grid-connected
Define process for islanded configurations to become grid-connected
8
BYOG at different location
Develop BYOG option for generation at a different location from the Large Load (if selected, provide comment on extent of "different location", such as one station away, or beyond)
9
Define/allow Self-Limiting Facility (SLF) Private Use Networks (PUN)
Combine SLF and PUN concepts
10
Pursue BYOG option of Netted Network
Consider in the planning process how Netted Network concept discussed at Aug 21 LLWG would impact allocations if adopted in Operations.
11
Source: 1-ERCOT-CTP-stakeholder-workshop-2_09242026_v2
ERCOT is continuing to triage BYOG and PCLR enhancements, assessing technical feasibility and implementation complexity, and will share priorities as the evaluation progresses

## Slide 24: BYOG enhancements: Items under evaluation (2/2)
Category
Enhancement
Description
Alternative BYOG enhancements (continued)
Battery enhancements
Allow Multiple POIs and/or Customer-owned Substations
n/a
12
Allow mix of resources at PUN
Allow a mix of different resource registration categories at a PUN, i.e., Generation Resources AND Settlement Only
13
Allow temporary generation
Allow temporary generation until the transmission is built to reliably serve the Large Load. Generation is planned from the beginning to be temporary without having to go through the RMR process
14
Define operational battery registration
Define battery registration for batteries that are only used for meeting operational requirements, e.g., voltage ride-through
15
Develop rules for market-operating operational batteries
Define rules for batteries that are added for operational requirements, and want to participate in the market
16
Rules for using an interconnected battery as part of PCLR
17
n/a
Other stakeholders’ ideas
Alternative PCLR interconnection pathways1
Explore alternative pathways for PCLRs to interconnect and operate independently of Batch timelines while maintaining ERCOT reliability requirements
18
Alternative technologies to enable Large Load interconnection2
Evaluate the use of distributed energy resources and other alternative technologies to alleviate transmission constraints and enable additional Large Load capacity
19
Alternative approaches to transmission capacity allocation3
20
Explore alternative mechanisms for allocating transmission capacity to Large Loads, including market-based approaches and financial commitments
Enhanced coordination of generation and flexible loads4
21
Explore mechanisms to coordinate separately metered generation and flexible load operations, including operational netting arrangements that maintain ERCOT visibility and dispatchability
Source: 1-ERCOT-CTP-stakeholder-workshop-2_09242026_v2
1. Agentic Infrastructure — PCLR Market Design Initiatives | 2. PIQ Energy – Flexibility without Curtailment: Aggregate DER Dispatch to Support Additional Firm Large Load Service | 3. Vistra - An Open Season Batch Integration for Large Load Interconnection | 4. Global Capacity Alliance – FRONT-OF-THE-METER (FTM) NETTING
ERCOT is continuing to triage BYOG and PCLR enhancements, assessing technical feasibility and implementation complexity, and will share priorities as the evaluation progresses
Detailed next

## Slide 25: ERCOT is evaluating three BESS configurations to clarify interconn., modeling, and registration req's for Large Computational Loads
UPS (Ride-Through Only)
Parallel BESS w/o grid exports
Market-participating ESR
Configuration
BESS installed electrically between grid and Large Computational Load
BESS connected in parallel with the Large Computational Load
BESS connected in parallel with the Large Computational Load
Primary purpose
Provide ride-through during grid disturbances
Provide ride-through, demand response, or both
Provide ride-through while participating in ERCOT markets
Grid exports
Not permitted
Not permitted
Subject to ESR operating requirements
Interconnection study process
Batch
Batch and Generation Interconnection or Modification (GIM)
Batch and GIM as an ESR3
ERCOT modeling
Part of the Load
generator
ESR3
Registration
No additional registration
NSG1 (when implemented4) or SOTSG2
ESR3
1
2
3
1. Non-Settled Generation | 2. Settlement Only Transmission Self-Generator | 3. Energy Storage Resource | 4. NPRR1317 and PGRR140

## Slide 26: Deep-dive: UPS (Ride-Through Only)
1
BESS operating exclusively as UPS is modeled as part of the Large Load, without separate registration
1. Network Operations Model
Description and electrical configuration
The BESS is installed electrically between the grid and the Large Computational Load, providing electrical decoupling and acting as an energy buffer
The configuration is designed to:
Protect the Large Computational Load from grid disturbances and support ride-through requirements
Maintain stable load behavior at the POI
Operate exclusively as a UPS, without exporting power to the grid
Interconnection study process
Batch process
Dynamic model
Model accurately representing the Large Load's dynamic characteristics at the POI, including the UPS/BESS. The applicable modeling and performance requirements are described in Planning Guide Section 6.2 and Nodal Operating Guide Sections 2.6 and 2.15 (e.g., LCL Ride-Through Requirements)
Stability studies
Stability study performed using the Large Load dynamic model
Planning studies
Studied as a Large Computational Load; Subsynchronous Oscillation (SSO) study required if applicable
NOM1
BESS modeled as part of the Large Computational Load
Registration
No additional registration is required
Proposed ERCOT requirements

## Slide 27: Deep-dive: Parallel BESS w/o grid exports
2
Description and electrical configuration
The BESS is connected in parallel with the Large Computational Load behind the same POI. The configuration supports two applications:
Ride-through: The battery supports the Large Computational Load during grid disturbances
Demand Response: The battery supplies energy to the co-located Large Computational Load, reducing net grid consumption when appropriate
The BESS is not designed to inject active power into the ERCOT grid
1. Network Operations Model | 2. Subsynchronous Oscillation
BESS connected in parallel with a Large Computational Load requires separate generation modeling and registration, even without grid exports
Interconnection study process
Batch (for Load) + Generation Interconnection or Modification (GIM) process, as Non-Settled Generation (NSG) when approved or Settlement Only Transmission Self-Generator (SOTSG)
Dynamic model
Dynamic models and data for the Large Load and BESS are separately needed and should accurately represent their dynamic characteristics at the POI. The applicable modeling/performance requirements are described in Planning Guide Section 6.2 and Nodal Operating Guide Sections 2.6, 2.14, and 2.15 (e.g., AGS-ESR Capability, LCL Ride-Through Requirements)
Stability studies
Stability study using both Large Load and BESS dynamic models, including associated control systems
Planning studies
SSO2 study required, if applicable
NOM1
BESS modeled as a generator
Registration
NSG when implemented or SOTSG; SOTSG registration is not available if a Generation Resource is co-located behind the same POI
Proposed ERCOT requirements

## Slide 28: Deep-dive: Market-participating ESR
3
Proposed ERCOT requirements
Interconnection study process
Batch (for Load) + Generation Interconnection or Modification (GIM) process as an ESR
Dynamic model
Dynamic data for the Large Computational Load and ESR are needed. The model should accurately represent their dynamic characteristics at the POI. The applicable modeling and performance requirements are described in Planning Guide Section 6.2 and Nodal Operating Guide Sections 2.6, 2.14, and 2.15
Stability studies
Stability study using both Large Load and ESR dynamic models, including associated control systems
Planning studies
Studied as a co-located ESR
NOM1
BESS modeled as an ESR
Registration
ESR registration required; ESR cannot receive Wholesale Storage Load (WSL) treatment within a Private Use Network (PUN); market-available MW and SOC capability must be derated
Description and electrical configuration
The BESS is connected in parallel with the Large Computational Load and registered as an Energy Storage Resource (ESR).The configuration is designed to support both:
Ride-through: The battery provides support to the Large Computational Load during grid disturbances
Market participation: The battery participates in ERCOT markets as a registered ESR
The MW and State of Charge (SOC) capability made available to ERCOT markets must be derated
1. Network Operations Model
The battery operates alongside the Large Computational Load while participating in ERCOT markets, subject to applicable modeling, ride-through, and available-capacity requirements

## Slide 29
1. Antitrust admonition
2. PUCT 58481 Discussion
3. Pre-Batch Portal Process Discussion (LIOO)
4. Other Batch details
5. Batch Large Load Reporting/Transparency
6. BYOG/PCLR Enhancement Discussion
7. Adjourn
29
On the agenda
PUBLIC

## Slide 30: Thank you