| PGRR Number | 122 | PGRR Title | Reliability Performance for Loss of Load |
| --- | --- | --- | --- |

| Date | October 22, 2026 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | John Russ Hubbard |
| E-mail Address | jhubbard@omm.com |
| Company | Texas Industrial Energy Consumers (TIEC) |
| Phone Number | 737-261-8631 |
| Cell Number |  |
| Market Segment | Consumers |

Comments

Texas Industrial Energy Consumers (TIEC) files these comments ahead of the November Reliability and Operations Subcommittee (ROS) meeting to address the treatment of Critical Load under Planning Guide Revision Request (PGRR) 122.  As discussed during the October 1, 2026 ROS meeting, TIEC’s proposed revision adds the phrase “other than Load designated as a Critical Load Industrial Customer pursuant to P.U.C. Subst. R. 25.497” to paragraph (7) of Section 4.1.1.9 to ensure that a Critical Load Industrial Customer is not subject to curtailment under the operational mechanisms ERCOT uses to mitigate an exceedance of the maximum Load loss threshold.

TIEC does not oppose ERCOT’s efforts to maintain total Load loss within an established limit.  However, as currently drafted, PGRR122 does not properly prioritize Loads whose continued service is essential to public health and safety.  While ERCOT does not anticipate that any non-computational loads would contribute to the maximum Load loss threshold, ERCOT clarified that in the future it could identify an issue with traditional loads, including Critical Load Industrial Customers.  This would make those Loads subject to curtailment under the operational mechanisms contemplated in Section 4.1.1.9(7).  Critical Load Industrial Customers have been designated as critical because an interruption of service creates safety, environmental, or public health risks.  They may be subject to curtailment in other contexts, but their service should not be interrupted as a part of the operational mechanics meant to mitigate the risk in planning studies and system operations.

To be clear, TIEC’s proposed language is meant to preserve ERCOT’s ability to protect the system.  The exclusion would not apply in other contexts where ERCOT determines that curtailment of a Critical Load Industrial Customer is necessary to prevent or respond to an imminent risk of cascading outages, uncontrolled Islanding, or frequency instability, and only after all other reasonably available measures have been exhausted.  TIEC’s language is merely meant to ensure that service to Critical Load Industrial Customers can be maintained to the extent possible to ensure the safety of the system.

Revised Cover Page Language

| Planning Guide Sections Requiring Revision | 4.1.1.2, Reliability Performance Criteria 4.1.1.9, Maximum Load Loss Criteria |
| --- | --- |

Market Rules Notes

Please note the baseline Planning Guide language in the following section(s) has been updated to reflect the incorporation of the following PGRR(s) into the Planning Guide:

- PGRR115 – Related to NPRR1234, Interconnection Requirements for Large Loads and Modeling Standards for Loads 25 MW or Greater (unboxed 12/15/25)

  - Section 4.1.1.2

Please note that the following PGRR(s) also propose revisions to Section 4.1.1.2:

- PGRR147, Allowable Non-Consequential Load Loss Alignment

Revised Proposed Guide Language

#### 4.1.1.2	Reliability Performance Criteria

(1)	The following reliability performance criteria (summarized in Table 1: ERCOT-specific Reliability Performance Criteria, below) shall be applicable to planning analyses in the ERCOT Region:

(a)	With all Facilities in their normal state, following a common tower outage with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss;

(b)	With all Facilities in their normal state, following an outage of a DC Tie Resource or DC Tie Load with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss;

(c)	With all Facilities in their normal state, following an outage of a Large Load with or without a three-phase fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss;

(d)	With any single generating unit unavailable, followed by Manual System Adjustments, followed by a common tower outage, the opening of a line section without a fault, or outage of a DC Tie Resource or DC Tie Load with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss;

(e)	With any single transformer, with the high voltage winding operated at 300 kV or above and low voltage winding operated at 100 kV or above unavailable, followed by Manual System Adjustments, followed by a common tower outage, the opening of a line section without a fault, or the contingency loss of a single generating unit, transmission circuit, transformer, shunt device, FACTS device, or DC Tie Resource or DC Tie Load with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.  An operational solution may be planned on a permanent basis to resolve a performance deficiency under this condition;  and

(f)	With any single DC Tie Resource or DC Tie Load unavailable, followed by Manual System Adjustments, followed by a common tower outage, the opening of a line section without a fault, or the contingency loss of a single generating unit, transmission circuit, transformer, shunt device, FACTS device, or DC Tie Resource or DC Tie Load, with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.  An operational solution may be planned on a permanent basis to resolve a performance deficiency under this condition.

| Initial Condition |  | Event | Facilities within Applicable Ratings and System Stable with No Cascading or Uncontrolled Outages | Non-consequential Load Loss Allowed |
| --- | --- | --- | --- | --- |
| 1 | Normal System | Common tower outage, DC Tie Resource outage, DC Tie Load outage, or the outage of a Large Load | Yes | No |
| 2 | Unavailability of a generating unit, followed by Manual System Adjustments | Common tower outage, DC Tie Resource outage, DC Tie Load outage, or opening of a line section without a fault | Yes | No |
| 3 | Unavailability of a transformer with the high voltage winding operated at 300 kV or above and low voltage winding operated at 100 kV or above, followed by Manual System Adjustments | Common tower outage; opening of a line section without a fault; or Contingency loss of one of the following: 1. Generating unit; 2. Transmission circuit; 3. Transformer; 4. Shunt device; 5. FACTS device; or 6. DC Tie Resource or DC Tie Load | Yes | No |
| 4 | Unavailability of a DC Tie Resource or DC Tie Load, followed by Manual System Adjustments | Common tower outage; opening of a line section without a fault; or Contingency loss of one of the following: 1. Generating unit; 2. Transmission circuit; 3. Transformer; 4. Shunt device; 5. FACTS device; or 6. DC Tie Resource or DC Tie Load | Yes | No |

Table 1: ERCOT-specific Reliability Performance Criteria

(2)	ERCOT and the TSPs shall endeavor to resolve any performance deficiencies as appropriate.  If a Transmission Facility improvement is required to meet the criteria in this Section 4.1.1.2, but the improvement cannot be implemented in time to resolve the performance deficiency, an interim solution may be used to resolve the deficiency until the improvement has been implemented.

(a)	A Remedial Action Scheme (RAS) shall not be planned to resolve a planning criteria performance deficiency unless it is expected that system conditions will change such that the RAS will no longer be needed within the next five years.

[PGRR113: Replace item (a) above with the following upon system implementation of NPRR1198:] (a) A Remedial Action Scheme (RAS) or Constraint Management Plan (CMP) shall not be planned to resolve a planning criteria performance deficiency unless it is expected that system conditions will change such that the RAS or CMP will no longer be needed within the next five years.

4.1.1.9	Maximum Load Loss Criteria

(1)	For the purpose of this section, the maximum Load loss threshold is 3,200 MW and shall be evaluated in at least one off-peak system condition occurring outside of the Peak Load Season for assessment.

(2)	ERCOT shall review the maximum Load loss threshold at least once every two years, or more frequently if warranted by material changes in ERCOT System conditions.

(3)	The total Load loss for a contingency event is the aggregate of all Load not served as a result of the event, including consequential Load loss, Load reduction due to voltage excursion, and Load that is disconnected from the ERCOT System by end-user equipment.

(a)	The total Load loss should reflect Load that remains disconnected or not served following the event and should not include momentary Load reductions or disconnections.

(4)	With all Facilities in their normal state, for any contingency event in category P1, P2, P4, P5, or P7 of the NERC Reliability Standard addressing Transmission System Planning Performance Requirements, or following a common tower outage, the total Load loss shall be less than the maximum Load loss threshold .

(5)	With any of the following Facilities unavailable, followed by Manual System Adjustments, followed by a common tower outage or the contingency loss of a transmission circuit, transformer, shunt device, or FACTS device, the total Load loss shall be less than the maximum Load loss threshold.  The total Load loss does not include the total Load loss resulting from the unavailability of any Facility and Manual System Adjustment.

(a)	Any transmission circuit, transformer, shunt device, or FACTS device;

(b)	Any double-circuit transmission line consisting of two circuits sharing a tower of 0.5 miles or greater; or

(c)	Any single generating unit.

(6)	If ERCOT identifies an exceedance of the maximum Load loss threshold in a Large Load interconnection study, ERCOT may limit the amount of Large Load allocated in the study for each studied Large Load that contributes to the total Load loss.

(7)	If ERCOT identifies the performance deficiency in the course of performing any system analysis other than a Large Load interconnection study , ERCOT shall use operational mechanisms to mitigate the risk in planning studies and in system operations.  Operational mechanisms may include, but are not limited to, curtailment of any of the Large  Load contributing to the total Load loss, other than Load designated as a Critical Load Industrial Customer pursuant to P.U.C. Subst. R. 25.497.

See GridMonitor, ROS Meeting at 02:09:49-02:10:26 (October 1, 2026) (available at: https://dash2.gridmonitor.com/sharing/?token=26e98023-c688-4f50-927c-c0942238d02a).