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[bookmark: _Toc242710749]Report Highlights 
The unofficial ERCOT peak load for September 2026 was 86,647 MW and occurred on 9/12/2026 during hour ending 17:00, this is 6,698 MW higher than the September 2025 peak demand of 79,949 MW on 9/4/2025.
On 15-minute settlement interval basis, maximum demand of 86,782 MW occurred on 9/12/2026 during interval ending 16:45 and minimum demand of 51,330 MW occurred on 9/26/2026 during interval ending 05:00. 
There were 2 frequency events.
There were no events which required automatic/manual deployment of Load Resources that were controlled by an Under-Frequency Relays.
There were 0 DC Tie Curtailment Notices.
There were 0 OCNs.
There were 3 Advisories: ERCOT postponed the deadline for posting of the DAM solution due to long run time on 9/15/2026, 9/28/2026, and 9/29/2026.
There were 0 Watches.
There were 0 Emergency Notices.
There were 43 RUC commitments.
The following GTCs saw congestion in September: 
	GTC
	Days Congestion

	East Texas
	23

	Nelson Sharpe - Rio Hondo
	22

	South Texas Export Pawnee - Spruce
	21

	South Texas Export Pawnee - Tango
	20

	North Edinburg - Lobo
	17

	North - Houston
	10

	Panhandle
	8

	West Texas
	7

	South Texas Import Katoen - Lonhill
	4

	Zapata Starr
	4

	South Texas Import Pawnee - Spruce
	1




[bookmark: _Toc242710750]Frequency Control
[bookmark: _Toc242710751]Frequency Events
The ERCOT Interconnection experienced 2 frequency events.
A summary of the frequency events is provided below. The reported frequency events meet one of the following criteria: Delta Frequency is 60 mHz or greater; the MW loss is 350 MW or greater; resource trip event triggered ECRS deployment. Frequency events that have been identified as Frequency Measurable Events (FME) for purposes of BAL-001-TRE-2 analysis are highlighted in blue. When analyzing frequency events, ERCOT evaluates PMU data according to industry standards. Events with an oscillating frequency of less than 1 Hz are inter-area, while higher frequencies indicate local events. Industry standards specify that damping ratio for inter-area oscillations should be 3.0% or greater. For the frequency event listed below, the ERCOT system met these standards and transitioned well after the disturbance. In the case of negative delta frequency, the MW Loss column could refer to load loss.

	Date and Time
	Delta Frequency
	Max/
Min Frequency
	[bookmark: RANGE!D1]Duration of Event
	[bookmark: RANGE!E1]PMU Data 
	MW Loss
	Load
	IRR
	Inertia

	
	[bookmark: RANGE!B2](Hz)
	(Hz)
	
	Oscillation Mode (Hz)
	Damping Ratio
	
	(MW)
	% 
	[bookmark: RANGE!J2](MW-s)

	9/6/2026 2:11:38
	0.047
	59.959
	00:03:11
	0.56
	14%
	664
	    60,172 
	20%
	  325,638 

	9/27/2026 1:27:27
	0.018
	59.967
	00:03:05
	0.6
	11%
	477
	    56,152 
	20%
	  321,061 
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[bookmark: _Toc90113254][bookmark: _Toc90367425](Note: All data on this graph encompasses frequency event analysis based on BAL-001-TRE-2.)

[bookmark: _Toc242710752]Automatic/Manual Load Resource Deployments
There were no events which required automatic/manual deployment of Load Resources that were controlled by an Under-Frequency Relays.

[bookmark: _Toc242710753]Reliability Unit Commitment
ERCOT reports on Reliability Unit Commitments (RUC) monthly. Commitments are reported grouped by operating day and weather zone. The total number of hours committed is the sum of the hours for all the units in the specified region. Additional information on RUC commitments can be found on the MIS secure site at Grid  Generation  Reliability Unit Commitment.
There were 43 RUC commitments.
	Resource Location
	# of Resources
	Operating Day
	Total # of Hours Committed
	 Total MWhs 
	Reason for Commitment

	 NORTH_CENTRAL 
	4
	September 1, 2026
	43
	            6,083.5 
	 Capacity AS 

	 EAST, NORTH_CENTRAL 
	4
	September 2, 2026
	26
	            2,718.8 
	 Capacity AS 

	 SOUTHERN 
	1
	September 6, 2026
	8
	            1,948.9 
	 Capacity AS 

	 NORTH_CENTRAL 
	2
	September 7, 2026
	16
	            1,167.2 
	 Capacity AS 

	 NORTH_CENTRAL 
	5
	September 8, 2026
	67
	          12,539.3 
	 Capacity AS 

	 NORTH_CENTRAL 
	2
	September 9, 2026
	12
	               366.4 
	 Capacity AS 

	 NORTH_CENTRAL, SOUTH_CENTRAL 
	2
	September 10, 2026
	16
	            3,265.7 
	 A/S Shortage, E_PASP 

	 NORTH_CENTRAL 
	1
	September 15, 2026
	4
	            1,739.6 
	 Capacity AS 

	 NORTH_CENTRAL 
	3
	September 16, 2026
	25
	            1,710.2 
	 DWCSRAM5 

	 NORTH_CENTRAL 
	2
	September 17, 2026
	12
	               407.7 
	 DWCSRAM5 

	 NORTH_CENTRAL 
	1
	September 18, 2026
	8
	               358.0 
	 Capacity AS 

	 NORTH, NORTH_CENTRAL, SOUTHERN 
	3
	September 20, 2026
	17
	            1,084.6 
	 Capacity AS, Capactity AS, DHILMAR5 

	 NORTH_CENTRAL, SOUTHERN 
	3
	September 21, 2026
	18
	            1,387.7 
	 Capacity AS, DHILMAR5 

	 NORTH_CENTRAL, SOUTHERN 
	2
	September 22, 2026
	11
	            1,049.0 
	 Capacity AS, DHILMAR5 

	 EAST, NORTH_CENTRAL 
	3
	September 24, 2026
	16
	            2,413.8 
	 DCMBCPS8, Energy Uncertainty 

	 NORTH_CENTRAL 
	2
	September 27, 2026
	16
	               678.5 
	 Capacity AS 

	 NORTH_CENTRAL 
	3
	September 28, 2026
	24
	            1,638.0 
	 Capacity AS 





[bookmark: _Toc242710754]IRR, Wind, and Solar Generation as a Percent of Load
[bookmark: _Hlk83634375]The graph below shows the maximum, minimum and average aggregate solar, wind and IRR output as a percentage of total ERCOT load when evaluated as 10-minute averaged intervals, over the past 13 months. Current wind and solar generation and penetration records are listed in the footnote below[footnoteRef:2]. Maximum IRR penetration for September 2026 was 71.94% on 9/15/2026 interval ending 09:40 and minimum IRR penetration for September 2026 was 6.41% on 9/6/2026 interval ending 07:10. [2:  Current Wind Generation Record: 29,031 MW on 06/29/2026 at 02:00 | Current Wind Penetration Record: 69.15% on 04/10/2022 at 01:43
  Current Solar Generation Record: 35,427 MW on 07/30/2026 at 13:33 | Current Solar Penetration Record: 72.74% on 05/02/2026 at 11:28] 

[image: ]
The following graph shows the maximum and average ESR charging and discharging as a percentage of total ERCOT load when evaluated as 10-minute averaged intervals, over the past 13 months.  Current ESR charging and discharging records are listed in the footnote below[footnoteRef:3].  Maximum ESR discharge generation for September 2026 was 12,627 MW on 9/1/2026 interval ending 20:00 and maximum ESR charge load for September 2026 was 12,123 MW on 9/10/2026 interval ending 09:30. [3:  Current ESR Discharge Record: 13,300 MW on 08/23/2026 at 19:45 | Current ESR Discharge Penetration Record: 20.61% on 03/13/2026 at 19:31
  Current ESR Charge Record: 12,392 MW on 09/10/2026 09:19 | Current ESR Charge Penetration Record: 18.91% on 09/10/2026 at 09:18] 

[image: ]
The graph below shows the wind, solar, IRR, and ESR penetration percentage during the hour of the peak load in the last 13 months.  Positive values for ESRs indicate discharging while negative values indicate charging.  During the hour of peak load for the month, hourly integrated wind generation was 7,405 MW and solar generation was 29,705 MW.  The ESR injection during the peak load hour was -539 MW.
[image: ]
The following graph shows the minimum wind, solar, and IRR output during the peak load hour as a percentage of the daily peak load for every day in the month.
[image: ]
Lastly, the chart below shows the total ESR charging/discharging and efficiency over the past 13 months.  Efficiency is defined as total discharging divided by total charging.  Total ESR charging and discharging for September 2026 were 1,001,673 MWh and 789,299 MWh, respectively, and efficiency was 78.80%.
[image: ]
[bookmark: _Toc241049170][bookmark: _Toc242710755]Energy Storage Resource (ESR) Output and State of Charge (SOC) Profile
The graph below shows how ESR SOC varies by Hour Ending (HE). The SOC is generally higher during the day and lower during night. During the month of September 2026, ESRs operated below 20% SOC for 15.62% of the time and below 10% SOC for 2.27% of the time. The minimum observed SOC was 6.24% on 9/22/2026 at interval ending 23:36, while the maximum was 95.47% on 9/8/2026 at interval ending 17:15.
[image: ]
The chart below shows the maximum ESR output as a percentage of the total ERCOT Net Load. ESR penetration reached a maximum of 19.68% on 9/12/2026 at interval ending 19:35. The net load reached a peak of about 71210 MW on 9/2/2026 at interval ending 19:35.
[image: ]
[bookmark: _Toc242710756][bookmark: _Hlk80277108][bookmark: _Hlk130892461]Largest Net-Load Ramps
The net-load ramp is defined as the change in net-load (load minus wind and PVGR generation) during the defined time horizon. Such a variation in net-load needs to be accommodated in grid operations to ensure that the reliability of the grid is satisfactorily maintained. The largest net-load ramps over 5-minute, 10-minute, 15-minute, 30-minute, and 60-minute intervals in August 2026 were 1,777 MW, 3,348 MW, 4,671 MW, 8,447 MW, and 15,338 MW respectively. A comparison with historical values is provided in the table below.
	Month and Year
	5 min
	10 min
	15 min
	30 min
	60 min

	14-Sep
	1,054 MW
	1,531 MW
	1,695 MW
	2,628 MW
	4,898 MW

	15-Sep
	993 MW
	1,457 MW
	1,779 MW
	2,952 MW
	5,659 MW

	16-Sep
	827 MW
	1,260 MW
	1,688 MW
	2,880 MW
	5,464 MW

	17-Sep
	730 MW
	1,251 MW
	1,758 MW
	3,298 MW
	5,716 MW

	18-Sep
	1,129 MW
	1,991 MW
	2,372 MW
	3,391 MW
	6,015 MW

	19-Sep
	867 MW
	1,207 MW
	1,643 MW
	3,134 MW
	5,716 MW

	20-Sep
	776 MW
	1,285 MW
	1,763 MW
	2,728 MW
	5,087 MW

	21-Sep
	1,251 MW
	1,655 MW
	1,972 MW
	3,519 MW
	6,629 MW

	22-Sep
	887 MW
	1,391 MW
	1,818 MW
	3,099 MW
	5,351 MW

	23-Sep
	1,018 MW
	1,642 MW
	2,416 MW
	4,129 MW
	7,947 MW

	24-Sep
	2,163 MW
	3,028 MW
	3,456 MW
	5,918 MW
	10,401 MW

	25-Sep
	1,637 MW
	2,824 MW
	3,944 MW
	6,492 MW
	12,268 MW

	
	1,918 MW
	3,326 MW
	4,661 MW
	8,092 MW
	14,234 MW

	26-Sep
	9/8/2026
	9/7/2026
	9/12/2026
	9/7/2026
	9/12/2026

	 
	(IE 18:21)
	(IE 18:38)
	(IE 18:29)
	(IE 18:47)
	(IE 19:07)

	All Months in 2014-2026
	3,797 MW
	3,562 MW
	4,671 MW
	8,901 MW
	16,522 MW

	
	5/28/2025
	5/28/2025
	8/27/2026
	1/29/2024
	1/29/2024

	
	(IE 10:27)
	(IE 10:27)
	(IE 18:56)
	(IE 17:11)
	(IE 17:17)



[bookmark: _Toc242710757]Congestion Analysis
[bookmark: _Toc242710758]Notable Constraints
[bookmark: _Hlk92804220]Nodal protocol section 3.20 specifies that ERCOT shall identify transmission constraints that are binding in Real-Time three or more Operating Days within a calendar month. As part of this process, ERCOT reports congestion that meets this criterion to ROS. In addition, ERCOT also highlights notable constraints that have an estimated congestion rent exceeding $1,000,000 for a calendar month. These constraints are detailed in the table below, including approved transmission upgrades from TPIT that may provide some congestion relief based on ERCOT’s engineering judgement. Rows highlighted in blue indicate the congestion was affected by one or more outages. For a list of all constraints activated in SCED, please see Appendix A at the end of this report.

	Element Key
	Contingency Name
	Overloaded Element
	Contingency Desc
	Overloaded Element Desc
	# of Days Constraint Binding
	Congestion Rent
	Transmission Project

	PKRSW_HCKSW_35100__A
	DWCSRAM5
	35100__A
	WCSWS TO RAMSW 345 DBLCKT TRPLCKT 3 of 3
	Parker Switch - Hicks Switch 345kV
	4
	$41,819,804.55
	Oncor Southern DFW Load Interconnection and General Grid Strengthening Project (25RPG004)

	FORSW_FORSW_FORSW_MR3H
	SCNRFOR5
	FORSW_MR3H
	CENTERVILLE ROAD SWITCH to FORNEY SWITCH LIN _A
	Forney Switch 345kV
	2
	$23,466,291.82
	Oncor Forney 345/138-kV Switch Rebuild Project (24RPG021)

	LA_PALMA_LA_PALMA_LA_PALMA_XF1A
	MKNGSTE5
	LA_PALMA_XF1A
	manual double NEDIN_KNG2 and NEDIN_STEWAR1 345KV line
	La Palma 345kV
	6
	$16,170,984.86
	 

	SCRCV_KNAPP_6437__F
	DMTSCOS5
	6437__F
	DMTSW TO SCOSW 345 DBLCKT
	Knapp - Scurry Chevron 138kV
	16
	$10,215,544.97
	Dermott Area 138 kV Like Upgrades (26RPG014)

	STP_WAP_STPWAP39_1
	DWPWFWP5
	STPWAP39_1
	TWR(345) WAP-WLF64 & WAP-WLY72
	South Texas Project - Wa Parish 345kV
	16
	$9,120,265.72
	 

	SMPST_BNTDR_3170__B
	DWTRWLV5
	3170__B
	WTRML TO WLVEE and TO SARRD 345KV
	Buntin Drive - Simpson Stuart 138kV
	4
	$8,124,352.92
	 

	JN_BI_BI_JN_64_A
	DWAP_BI5
	BI_JN_64_A
	TWR (345) WAP-BI50 & SMITHERS-BI98
	Bellaire - Jeanetta 345kV
	10
	$5,841,001.82
	TPIT#87479 upgrades this line Normal and emergency ratings of 1614 MVA and 1792 MVA

	MULBERRY_ABINDUST_ABINDU_MULBER1_1
	SABSBLU8
	ABINDU_MULBER1_1
	BLUFF CREEK to ABILENE SOUTH LIN 1
	Abilene Industrial Park - Abilene Mulberry Creek 138kV
	4
	$5,509,187.08
	 

	n/a_n/a_EASTEX
	BASE CASE
	EASTEX
	Basecase
	EASTEX GTC
	14
	$5,301,408.54
	 

	SEA_SEA_SEA_AAT1
	DFRYBC58
	SEA_AAT1
	DOUBLE KNBSW-SALSW 345 & FRYSW-BELCNTY 138
	Seaton 138kV
	16
	$5,208,416.82
	 

	LA_PALMA_LA_PALMA_LA_PALMA_XF1A
	BASE CASE
	LA_PALMA_XF1A
	Basecase
	La Palma 345kV
	1
	$5,051,448.17
	 

	SALDS_SONTERRA_1710__A
	DSALHUT5
	1710__A
	SALSW - HUTTO 345KV
	Salado South - Sonterra 138kV
	24
	$4,976,897.35
	Oncor & LCRA TSC Resubmission for Salado Switch to Hutto Switch 138-kV Line Project (25RPG006, TPIT #80546D)

	MV_HBRG4_MV_WESL4_WESLCO_HIDLBRG_1
	MHARNED5
	WESLCO_HIDLBRG_1
	Manual dbl ckt for NEDIN-BONILLA 345kV & RIOH-PRIM138kV
	Heidelburg Sub - Weslaco Sub 138kV
	15
	$4,821,291.48
	STEC_71928_Heidelberg_AEPWeslaco_Upgrade (MOD 71928)

	MESQE_OATES_1395__A
	DFORCN85
	1395__A
	FORNEY SWITCH  to LAKE HUBBARD SES  and Centerville Rd 345 and 138
	Oates - Mesquite East 138kV
	2
	$4,553,105.54
	 

	PAWNEE_CALAVERS_PAWNEE_SPRUCE_1
	DELMSAN5
	PAWNEE_SPRUCE_1
	Elmcreek-Sanmigl 345kV
	Pawnee Switching Station - Calaveras 345kV
	16
	$4,026,434.20
	San Antonio South Reliability II Project (23RPG032) : Project rebuilds the existing Pawnee to Spruce 345-kV line with normal and emergency rating of 1746MVA

	LAGOVI_NAMELE_228T333_1
	DROUCHI8
	228T333_1
	RNDRK-CHIEBR & SPANOA 138kV
	Lago Vista - Nameless 138kV
	2
	$3,610,609.22
	TPIT#72576A Lago Vista to Nameless Transmission Line Upgrade

	PK_DT_DT_PK_91_A
	DWO5_EU8
	DT_PK_91_A
	TWR (345/138) EU-SF09 & WO-JN72
	Downtown - Polk 138kV
	17
	$3,503,244.21
	 

	n/a_n/a_WESTEX
	BASE CASE
	WESTEX
	Basecase
	WESTEX GTC
	5
	$3,281,615.53
	Permian Basin Relibility Plan (765-kV import paths) (The PUCT approved ,helps improve, but not fully exit, the GTC yet.)

	MDO_PHR_MDOPHR99_A
	DWAP_OB5
	MDOPHR99_A
	TWR (345) OB-WAP98 & OB-WAP99
	Meadow - Ph Robinson 345kV
	17
	$3,139,134.38
	CNP_28TPIT103344_PH_Robinson_to_WA_Parish_Hardening (MOD 103344 Phase 103435, 25RPG028)

	WAP_OB_OB_WAP98_A
	SOBWAP5
	OB_WAP98_A
	WA PARISH to OBRIEN LIN A
	Wa Parish - Obrien 345kV
	12
	$3,075,274.99
	 

	KLNSW_KLNSW_KLNSW_MR1H
	DSALKLN5
	KLNSW_MR1H
	SALSW TO KLNSW 345 DBLCKT
	Killeen Switch 345kV
	5
	$2,550,205.83
	 

	MULBERRY_ABINDUST_ABINDU_MULBER1_1
	DBLUBUF8
	ABINDU_MULBER1_1
	BLUF_CRK - SOUTHABI & BUFF_GAP 138 KV
	Abilene Industrial Park - Abilene Mulberry Creek 138kV
	2
	$2,147,250.51
	 

	TMPSW_FRYSW_1715__B
	DSALHUT5
	1715__B
	SALSW - HUTTO 345KV
	Temple Switch - Fryers Creek 138kV
	18
	$2,130,006.99
	Temple Area Project (24RPG001). Note that Fryers Creek is named Boggy Creek in planning cases.

	BIGHIL_OERSTED_225T558_1
	DBAKCED5
	225T558_1
	BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV
	Big Hill - Orsted 345kV
	2
	$2,051,743.26
	 

	GN_PZ_GN_PZ_08_A
	SMDOOAS5
	GN_PZ_08_A
	MEADOW to OASIS LIN A
	Grant - Plaza 138kV
	16
	$2,028,924.62
	 

	MGSES_CATSW_6945__A
	SRGRMGS5
	6945__A
	MORGAN CREEK SES to RANGER CAMP SWITCH LIN _A
	Morgan Creek Ses - Cattleman Switch 345kV
	14
	$2,011,376.58
	West Texas 345-kV Infrastructure Rebuild Project (23RPG034)

	SNDSW_SNDSW_SNDSW_MR1H
	MSNDWCR5
	SNDSW_MR1H
	MANUAL SANDOW SW TO WALLEYE CREEK SW
	Sandow Switch 345kV
	11
	$1,963,202.46
	TPIT#109874 Rebuild Sandow 345 kV Switch

	TYPRK_PLYAM_6200__F
	DCDHTVW5
	6200__F
	TVWSW TO CDHSW 345 AND CDHSW TO VENSW 345 DBLCKT
	Poly-America - Tyre Park Sub 138kV
	7
	$1,961,868.18
	 

	ZEN_THW_THWZEN98_A
	SZENTHW5
	THWZEN98_A
	TH WHARTON to Zenith LIN A
	Th Wharton - Zenith 345kV
	7
	$1,852,495.91
	 

	PILONCIL_NLARSW_NLARSW_PILONC1_1
	MLOFOAV5
	NLARSW_PILONC1_1
	Manual Double LOBO - FOWLERTON & AVANZADA
	North Laredo Switch - Piloncillo 138kV
	12
	$1,806,928.88
	 

	PGTP1_PDSES_3610__G
	DWTRWLV5
	3610__G
	WTRML TO WLVEE and TO SARRD 345KV
	Parkdale Switch - Pleasant Grove Tap 1 138kV
	2
	$1,564,991.67
	 

	SARDIS_WXHNW_950__B
	XVE2N58
	950__B
	VENUS SWITCH TRX VENSW_3_3 345/138
	Sardis - Waxahachie Northwest 138kV
	7
	$1,459,827.15
	 

	SAMSW_VENSW_35055__A
	SVENFTS5
	35055__A
	FORT SMITH SWITCH to FORT SMITH SWITCH LIN _B
	Sam Switch - Venus Switch 345kV
	4
	$1,448,429.59
	Venus Switch to Sam Switch 345-kV Line Project (24RPG017)

	WEAVERRD_GREENLK_GREENL_WEAVER1_1
	SBIGV_D8
	GREENL_WEAVER1_1
	VICTORIA DUPONT SWITCH to BIG THREE LIN 1
	Greenlake - Weaver Road 69kV
	11
	$1,419,654.33
	 

	n/a_n/a_NELRIO
	BASE CASE
	NELRIO
	Basecase
	NELRIO GTC
	20
	$1,296,141.04
	The Lower Rio Grande Valley (LRGV) System Enhancement Project (21RPG017) 

	DUNLAP_DECKER_CKT_1027_1
	DSALHUT5
	CKT_1027_1
	SALSW - HUTTO 345KV
	Decker Power Plant - Aen Dunlap 138kV
	10
	$1,285,041.09
	 

	ZEN_THW_THWZEN98_A
	DRNS_TB5
	THWZEN98_A
	Rns-Rtw & Sng-Tb 345kV
	Th Wharton - Zenith 345kV
	8
	$1,111,487.03
	 

	LPLMK_LPLNE_LPLMK_LPLNE_1
	SBWDDBM5
	LPLMK_LPLNE_1
	BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1
	Mackenzie Substation - Northeast Substation 115kV
	13
	$1,050,950.82
	 

	LHM_LY_LHMLY_08_A
	DBCVPSA8
	LHMLY_08_A
	TWR (138) BCV-CV03 & GBY-PSA03
	Lyondell - Lychem 138kV
	3
	$1,015,839.38
	 

	BERGHE_BERGHE_BERGHE_AT1H
	DZORHAY5
	BERGHE_AT1H
	ZORN - HAYSEN 345KV
	Bergheim 345kV
	5
	$946,919.52
	 

	VERS_SANDROAD_SANDRO_VERS1_1
	SVEROK28
	SANDRO_VERS1_1
	OKLAUNION to OKLAUNION LIN 1
	Southwest Vernon - Sand Road 69kV
	4
	$941,344.77
	 

	ORNGROV_SNDIEGS_SND_ORAN_1
	SCALBAN9
	SND_ORAN_1
	BANQUETE to BANQUETE LIN 1
	San Diego Sub - Orange Grove Switching Station 69kV
	6
	$928,703.00
	 

	n/a_n/a_NE_LOB
	BASE CASE
	NE_LOB
	Basecase
	NE_LOB GTC
	9
	$829,764.30
	San Antonio South Reliability I Project (22RPG048)
LRGV Transmission Improvement Project (21RPG017)
San Antonio South Reliability II Project (23RPG032)

	MEXTP_ITALY_2270__B
	SBLURDH8
	2270__B
	BLUM to RED HILL SWITCH LIN _G
	Milford Exxon Tap - Italy 69kV
	14
	$792,286.43
	 

	FLTSW_PRSSW_1545__A
	SPRSPAR8
	1545__A
	PARIS SWITCH to PARIS LIN _A
	Paris Switch - Flying Tiger Switch 138kV
	25
	$785,926.61
	 

	PALOUSE_WOLFCAMP_PALOUS_WOLFCA1_1
	SFTLMES8
	PALOUS_WOLFCA1_1
	FORT LANCASTER to FORT LANCASTER LIN 1
	Palouse - Wolfcamp 138kV
	8
	$727,750.70
	 

	BALLINGE_BALLINGE_BALLINGE_FMRL
	SCOLBAL8
	BALLINGE_FMRL
	BALLINGER to COLEMAN LAKE IVIE TAP LIN 1
	Ballinger 69kV
	5
	$709,908.42
	 

	n/a_n/a_E_PASP
	BASE CASE
	E_PASP
	Basecase
	E_PASP GTC
	18
	$702,057.20
	San Antonio South Reliability I Project (22RPG048)
LRGV Transmission Improvement Project (21RPG017)
San Antonio South Reliability II Project (23RPG032)

	BLESSING_BLESSING_BLESSING_1382
	DSTPSTA5
	BLESSING_1382
	Double STP to HLJ & Static 345 KV
	Blessing 345kV
	8
	$698,120.32
	 

	WLY_WAP_WAPWLY72_A
	DBLW2JC5
	WAPWLY72_A
	TWR (345) JCK-WAT62 & BLY-JCK57
	Wa Parish - Whaley 345kV
	13
	$687,718.60
	 

	VICTORIA_MAGRUDER_MAGRUD_VICTOR2_1
	XVIC89
	MAGRUD_VICTOR2_1
	VICTORIA TRX 69A2 138/69
	Magruder - Victoria 138kV
	8
	$670,818.13
	 

	LENSW_PUTN_LENSW_PUTN2_1
	SCISPUT8
	LENSW_PUTN2_1
	CISCO to CISCO LIN 1
	Leon Switch - Putnam 138kV
	5
	$654,906.98
	 

	PALOUSE_WOLFCAMP_PALOUS_WOLFCA1_1
	DBIGSCH5
	PALOUS_WOLFCA1_1
	Big Hill - Schneeman Draw & Big Hill - Schneeman Draw 2
	Palouse - Wolfcamp 138kV
	6
	$609,067.79
	 

	DUNLAP_DECKER_CKT_1027_1
	SDAFAUS8
	CKT_1027_1
	AUSTROP to DAFFIN GIN LIN 1
	Decker Power Plant - Aen Dunlap 138kV
	8
	$551,420.35
	 

	NLARSW_PILONCIL_NLARSW_PILONC1_1
	DFOAVLO5
	NLARSW_PILONC1_1
	FOWLERTON to LOBO & AVANZADA
	North Laredo Switch - Piloncillo 138kV
	7
	$542,322.71
	 

	OAKC_PERSHING_OAKC_PERSHI1_1
	SABSBLU8
	OAKC_PERSHI1_1
	BLUFF CREEK to ABILENE SOUTH LIN 1
	Oak Creek Aep - Pershing Tap 138kV
	3
	$534,565.71
	 

	BRUNI_BRUNI_BRUNI_69_1
	DFOAVLO5
	BRUNI_69_1
	FOWLERTON to LOBO & AVANZADA
	Bruni Sub 138kV
	10
	$495,647.89
	 

	HIGH36_BRENNO_215T215_1
	SGIDLIN8
	215T215_1
	GIDDINGS to GIDDINGS LIN 1
	Highway 36 - Brenham North 138kV
	3
	$436,472.15
	 

	ELMOT_MCTYE_1020__A
	DELMWWE8
	1020__A
	ELMOT TO WWEST 138 AND ELMOT TO WEAST 69 DBLCKT
	Elm Mott - Mclennan County East 138kV
	9
	$432,239.46
	 

	ASHERTON_CATARINA_ASHERT_CATARI1_1
	MLOFOAV5
	ASHERT_CATARI1_1
	Manual Double LOBO - FOWLERTON & AVANZADA
	Asherton - Catarina 138kV
	14
	$380,252.99
	 

	BGRSW_SNDSW_455__A
	SBCESN35
	455__A
	BELL COUNTY EAST SWITCH to BELL COUNTY EAST SWITCH LIN _A
	Badger Switch - Sandow Switch 345kV
	9
	$375,578.50
	 

	ORNGROV_SNDIEGS_SND_ORAN_1
	MLOFOAV5
	SND_ORAN_1
	Manual Double LOBO - FOWLERTON & AVANZADA
	San Diego Sub - Orange Grove Switching Station 69kV
	5
	$360,619.08
	 

	VICTORIA_MAGRUDER_MAGRUD_VICTOR2_1
	SPAWCAL5
	MAGRUD_VICTOR2_1
	CALAVERAS to CALAVERAS LIN 1
	Magruder - Victoria 138kV
	3
	$342,123.23
	 

	FMRVL_RYSSW_400__A
	SFMRRYS5
	400__A
	Farmersville Switch to Farmersville Switch LIN _A
	Royse Switch - Farmersville Switch 345kV
	7
	$311,654.57
	 

	FRONTERA_S_MISSIN_BENTS_FRTER_1B_1
	SBENS_M8
	BENTS_FRTER_1B_1
	SOUTH MCALLEN to BENTSEN LIN 1
	Frontera - South Mission 138kV
	20
	$308,828.52
	 

	KNBSW_SALSW_36040__A
	DSNDBGR5
	36040__A
	DOUBLE SNDSW TO BCESW & BGRSW
	Salado Switch - Knob Creek Switch 345kV
	6
	$286,808.69
	 

	n/a_n/a_PNHNDL
	BASE CASE
	PNHNDL
	Basecase
	PNHNDL GTC
	3
	$283,519.64
	 

	SOLSTICE_SOLSTICE_SOLSTICE_PST1
	STARLEO8
	SOLSTICE_PST1
	LEON CREEK TNP to TARBUSH TNP LIN 1
	Solstice 138kV
	15
	$275,071.41
	Fort Stockton Switch: Expand 345 kV Station (MOD 93226)

	SEA_SEA_SEA_AAT1
	DFRYTM58
	SEA_AAT1
	DOUBLE FRYSW-TMPSW 138 & KNBSW-SALSW 345
	Seaton 138kV
	5
	$250,007.06
	 

	LA_PALMA_HAINE_DR_HAINE__LA_PAL1_1
	MHARNED5
	HAINE__LA_PAL1_1
	Manual dbl ckt for NEDIN-BONILLA 345kV & RIOH-PRIM138kV
	Haine Drive - La Palma 138kV
	11
	$236,075.96
	 

	NUECES_B_WHITE_PT_NUECES_WHITE_2_1
	SMAYWHI8
	NUECES_WHITE_2_1
	GILA to MAYO LIN 1
	Nueces Bay - Whitepoint 138kV
	7
	$234,105.03
	 

	CRDSW_OLNEY_6830__B
	DGRMGRS8
	6830__B
	FIREROCK TO BRNWD 138 AND FIREROCK TO BANGS 69 DBLCKT
	Cottonwood Road Switch - Olney Pod 69kV
	11
	$220,815.20
	 

	GIDEON_SETTLE_196T171_1
	DAUSLOS5
	196T171_1
	Lostpi-Austro&Dunlap 345kV
	Settlers - Sim Gideon 138kV
	7
	$218,675.13
	 

	HECKER_RESNIK_HECKER_RESNIK1_1
	DMCDUPS8
	HECKER_RESNIK1_1
	MCCAMPBE - RESNIK & I_DUPSW 138kV
	Hecker - Resnik 138kV
	7
	$216,597.63
	 

	BRUNI_BRUNI_BRUNI_69_1
	SLAQLOB8
	BRUNI_69_1
	LAQUINTA to LOBO LIN 1
	Bruni Sub 138kV
	15
	$211,503.46
	 

	SONR_ATSO_ATSO_SONR1_1
	SCARFRI8
	ATSO_SONR1_1
	Carver to Carver LIN 1
	Atlantic Sonora - Sonora 69kV
	12
	$202,780.30
	 

	FLTSW_PRSSW_1545__A
	DPRSHWK8
	1545__A
	PRSSW-HWKSW 138 DBLCKT
	Paris Switch - Flying Tiger Switch 138kV
	6
	$189,833.13
	 

	POTEETS_OAKS9_POT_OAKS_1
	DELMSAN5
	POT_OAKS_1
	Elmcreek-Sanmigl 345kV
	Poteet Sub - Oaks Sub 69kV
	10
	$183,836.41
	 

	NORTMC_CROSSOVE_CROSSO_NORTMC1_1
	SFTLMES8
	CROSSO_NORTMC1_1
	FORT LANCASTER to FORT LANCASTER LIN 1
	North Mccamey - Crossover 138kV
	3
	$176,957.29
	 

	HOWARD_LEON_CRK_D5_S1_1
	SP5CAG8
	D5_S1_1
	CAGNON to CAGNON LIN 1
	Leon Creek - Howard 138kV
	6
	$175,063.53
	 

	BCESW_SNDSW_421__A
	SSNDBGR5
	421__A
	SANDOW SWITCH to BADGER SWITCH LIN _A
	Sandow Switch - Bell County East Switch 345kV
	6
	$172,595.78
	 

	AE_STR_AE_STR26_A
	SPETSNU8
	AE_STR26_A
	PETSON to Snug LIN A
	Angleton - Stratt 138kV
	3
	$114,325.46
	 

	TMPSW_TMPSE_610__B
	DPPRTEC8
	610__B
	PEPPER CREEK SW TO TEMPLE ELM CREEK 138 KV DOUBLE
	Temple Switch - Temple Southeast 138kV
	3
	$110,382.49
	Temple Area Project (24RPG001). 

	ENWSW_TMPTN_940__A
	SPEBTRU8
	940__A
	GAMMA to GAMMA LIN _D
	Ennis West Switch - Templeton 138kV
	14
	$108,591.02
	 

	BEVO_CARIZOS_CARIZOSPG_BEVO_1
	XASH89
	CARIZOSPG_BEVO_1
	ASHERTON TRX 69A1 138/69
	Carrizo Springs Sub - Bevo 69kV
	12
	$100,703.31
	 

	RAYBURN_RAYBURN_RAYBURN_69_2
	SFURVAN8
	RAYBURN_69_2
	FURHMAN to VANDERBILT SWITCHING STATION LIN 1
	Sam Rayburn Switchyd 138kV
	7
	$89,838.86
	 

	BIG_FOOT_BIG_FOOT_BIG_FOOT_69A1
	SHONMOO8
	BIG_FOOT_69A1
	MOORE SWITCHING STATION to HONDO CREEK SWITCHING STATION LIN 1
	Big Foot 138kV
	3
	$88,868.99
	 

	POTEETS_OAKS9_POT_OAKS_1
	SMOOPEA8
	POT_OAKS_1
	MOORE SWITCHING STATION to MOORE SWITCHING STATION LIN 1
	Poteet Sub - Oaks Sub 69kV
	6
	$79,039.72
	 

	TREADWEL_YELWJCKT_TREADW_YELWJC1_1
	DBIGKEN5
	TREADW_YELWJC1_1
	Bighil-Kendal 345kV
	Yellow Jacket - Treadwell 138kV
	4
	$78,029.48
	 

	RDHSW_BLUMS_810__G
	DCPSES12
	810__G
	Comanche Peak 1 & 2
	Red Hill Switch - Blum 138kV
	7
	$70,492.17
	 

	CMNSW_CMNTP_651__B
	SCMNCPS5
	651__B
	COMANCHE PEAK SES to COMANCHE SWITCH (Oncor) LIN _A
	Comanche Tap - Comanche Switch (Oncor) 138kV
	3
	$69,760.74
	 

	NVKSW_ANARN_6840__B
	DMGSRIC8
	6840__B
	DBL_CKT_GRSES-RICSW_138 kV and GRSES-SGRAS_138 kV
	Anarene - Navy Kickapoo Switch 69kV
	5
	$65,331.15
	 

	PALOUSE_CROSSOVE_CROSSO_PALOUS1_1
	SWOLPAL8
	CROSSO_PALOUS1_1
	PALOUSE to Wolfcamp LIN 1
	Crossover - Palouse 138kV
	5
	$64,829.75
	 

	GABRIE_GABRIE_GABRIE_AT1
	DSALHUT5
	GABRIE_AT1
	SALSW - HUTTO 345KV
	Gabriel 138kV
	5
	$60,817.82
	 

	ORNGROV_ORNGROV_ORNGROV_69_1
	SGEOORN8
	ORNGROV_69_1
	GEORGE WEST to GEORGE WEST LIN 1
	Orange Grove Switching Station 138kV
	3
	$58,669.30
	 

	TNNALVIN_ALVIN_138_ALV_NAL_1
	SMDOPHR5
	138_ALV_NAL_1
	MEADOW to PH ROBINSON LIN A
	North Alvin Tnp - Alvin Tnp 138kV
	21
	$50,291.76
	 

	LAKENASW_SAMATHIS_LAKENA_SAMATH1_1
	SWOLPAL8
	LAKENA_SAMATH1_1
	PALOUSE to Wolfcamp LIN 1
	Lake Nasworthy - San Angelo Mathis Field 69kV
	4
	$47,211.67
	 

	n/a_n/a_E_PATA
	BASE CASE
	E_PATA
	Basecase
	E_PATA GTC
	7
	$43,132.36
	 

	REVEILLE_COTULLA_COTULL_REVEIL1_1
	DFOWSMG5
	COTULL_REVEIL1_1
	FOWLRTON TO SAN MIGUEL DOUBLE CIRCUIT CONTINGENCY
	Cotulla - Reveille 138kV
	4
	$34,098.48
	 

	FTST_LEONCRK_138_FTS_LNC_1
	BASE CASE
	138_FTS_LNC_1
	Basecase
	Leon Creek Tnp - Fort Stockton Plant 138kV
	7
	$32,774.90
	 

	LEONCRK_FTST_138_FTS_LNC_1
	STARLEO8
	138_FTS_LNC_1
	LEON CREEK TNP to TARBUSH TNP LIN 1
	Leon Creek Tnp - Fort Stockton Plant 138kV
	3
	$27,134.37
	 

	RS_FB_FB_RS_60_A
	SEBATH8
	FB_RS_60_A
	Athena to EAST BERNARD LIN A
	Fort Bend - Rosenberg 138kV
	6
	$23,460.64
	 

	LEON_CRK_V4_TAP_D5_V4TP_1
	DLEOPEA8
	D5_V4TP_1
	Medinabs-Quintana&Leon_Crk-Pearsal 138KV
	Leon Creek - Palo Alto Tap 138kV
	6
	$22,447.48
	 

	CRDSW_OLNEY_6830__B
	SGRMGRS8
	6830__B
	GRAHAM EAST to GRAHAM EAST LIN _A
	Cottonwood Road Switch - Olney Pod 69kV
	3
	$20,667.94
	 

	FTST_LEONCRK_138_FTS_LNC_1
	DTNFBCA8
	138_FTS_LNC_1
	TNFXTAIL TO TARBUSH to BCATOKA 138KV
	Leon Creek Tnp - Fort Stockton Plant 138kV
	11
	$20,026.09
	 

	FRONTERA_S_MISSIN_BENTS_FRTER_1B_1
	SSHAFRO8
	BENTS_FRTER_1B_1
	FRONTERA to SHARYLAND LIN 1
	Frontera - South Mission 138kV
	10
	$19,073.14
	 

	V4_B4_B4_V4_1
	BASE CASE
	B4_V4_1
	Basecase
	Chavanea - Palo Alto 138kV
	4
	$18,127.32
	 

	V_DUPSW_BIGTRE_BIGTRE_V_DUPS1_1
	DVICDUP8
	BIGTRE_V_DUPS1_1
	VICTORIA DUPONT SWITCH TO VICTORIA DOUBLE CKT 138KV
	Big Three - Victoria Dupont Switch 138kV
	4
	$17,231.78
	 

	FURHMAN_MOURSUND_MOURSUND_FUR_1
	SFURVAN8
	MOURSUND_FUR_1
	FURHMAN to VANDERBILT SWITCHING STATION LIN 1
	Moursund - Furhman 138kV
	5
	$13,456.03
	 

	WDBSW_HLSBR_1275__A
	SBLURDH8
	1275__A
	BLUM to RED HILL SWITCH LIN _G
	Hillsboro - Woodbury Switch 138kV
	10
	$12,728.06
	 

	RAYBURN_RAYBURN_RAYBURN_69_2
	SL_4RAY8
	RAYBURN_69_2
	LOOP 463 SUB to LOOP 463 SUB LIN 1
	Sam Rayburn Switchyd 138kV
	4
	$12,505.03
	 

	CRD_CRD_CRD_CRD2
	XCMB58
	CRD_CRD2
	CARMICHAEL BEND SWITCH TRX CMBSW_3_1 345/138
	Concord 345kV
	3
	$11,399.60
	 

	YELWJCKT_HEXT_HEXT_YELWJC1_1
	SJUNYEL9
	HEXT_YELWJC1_1
	MENARD PHILLIPS TAP to MENARD PHILLIPS TAP LIN 1
	Yellow Jacket - Hext Lcra 69kV
	5
	$10,755.10
	 

	MRVLY_ESTLD_6635__G
	SCLCGTN8
	6635__G
	COLONY CREEK to GHOST TOWN SWITCH LIN _A
	Morton Valley (Oncor) - Eastland 69kV
	3
	$10,062.56
	 

	IH20_TNCOLIET_138_IH2_COT_1
	SSTAWIC8
	138_IH2_COT_1
	STAGHORN TNP to WICKETT TNP LIN 1
	Ih 20 Tnp - Collie Field Tap Tnp 138kV
	8
	$10,060.02
	 

	LA_PALMA_HAINE_DR_HAINE__LA_PAL1_1
	SRAYRI38
	HAINE__LA_PAL1_1
	LAS PULGAS to RAYMONDVILLE 2 LIN 1
	Haine Drive - La Palma 138kV
	5
	$9,595.61
	 

	FTST_LEONCRK_138_FTS_LNC_1
	DALASOA8
	138_FTS_LNC_1
	Manual From ALAMO_ST To SOAPTREE  138kV
	Leon Creek Tnp - Fort Stockton Plant 138kV
	8
	$7,002.88
	 

	FRONTERA_S_MISSIN_BENTS_FRTER_1B_1
	SPALFRO8
	BENTS_FRTER_1B_1
	FRONTERA to KEY SWITCH LIN 1
	Frontera - South Mission 138kV
	5
	$6,308.56
	 

	SN_STR_SN_STR26_A
	SVLGLO8
	SN_STR26_A
	VELASCO to GLOBAL LIN A
	Sintek - Stratt 138kV
	3
	$6,036.78
	 

	HUBRD_HAN1_1210__B
	SBLURDH8
	1210__B
	BLUM to RED HILL SWITCH LIN _G
	Hubbard - Haney Bepc 138kV
	3
	$5,254.38
	 

	GANSO_ESCONDID_ESCOND_GANSO1_1
	SBRAPIN8
	ESCOND_GANSO1_1
	BRACKETTVILLE to BRACKETTVILLE LIN 1
	Escondido - Ganso 138kV
	3
	$4,911.29
	 

	VICTORIA_OCONNOR_REFUG_VICTO_1C_1
	SGRIRAP5
	REFUG_VICTO_1C_1
	Grissom to RAPTOR LIN 1
	Oconnor - Victoria 69kV
	3
	$4,757.61
	 

	ESCONDID_GANSO_ESCOND_GANSO1_1
	SBRAHAM8
	ESCOND_GANSO1_1
	BRACKETTVILLE to HAMILTON ROAD LIN 1
	Escondido - Ganso 138kV
	6
	$4,482.82
	 

	FRWYPARK_MAINLAND_138_FWP_MNL_1
	SALVTNN8
	138_FWP_MNL_1
	ALVIN TNP to ALVIN TNP LIN 1
	Mainland Tnp - Freeway Park Tnp 138kV
	3
	$4,226.64
	 

	NLARSW_UNITEC_NLARSW_UNITEC1_1
	SDELLAR8
	NLARSW_UNITEC1_1
	DEL MAR to DEL MAR LIN 1
	Unitec - North Laredo Switch 138kV
	4
	$3,218.55
	 

	ANGLETON_WCOLLOCL_G138_15_1
	SWCOWCO8
	G138_15_1
	WEST COLUMBIA MAIN TNP to ANGLETON TNP LIN 1
	West Columbia Local Tnp - Angleton Tnp 138kV
	15
	$2,793.52
	 

	MPPOI_KEYSB_6217__B
	SBUZHMP8
	6217__B
	BUZZARD DRAW SWITCH to HARDY MORGAN POI LIN _B
	Mushaway Peak Poi - Key Sub 138kV
	3
	$2,012.22
	 

	HEXT_MASONSW_HEXT_MASONS1_1
	SJUNYEL9
	HEXT_MASONS1_1
	MENARD PHILLIPS TAP to MENARD PHILLIPS TAP LIN 1
	Mason Switching Station - Hext Lcra 69kV
	6
	$1,386.83
	 

	HEXT_MASONSW_HEXT_MASONS1_1
	DYETRJU8
	HEXT_MASONS1_1
	Double for YellowJacket - Treadwell & Junction
	Mason Switching Station - Hext Lcra 69kV
	3
	$192.68
	 

	PILONCIL_NLARSW_NLARSW_PILONC1_1
	DFOAVLO5
	NLARSW_PILONC1_1
	FOWLERTON to LOBO & AVANZADA
	North Laredo Switch - Piloncillo 138kV
	7
	$187.01
	 

	YELWJCKT_HEXT_HEXT_YELWJC1_1
	DYETRJU8
	HEXT_YELWJC1_1
	Double for YellowJacket - Treadwell & Junction
	Yellow Jacket - Hext Lcra 69kV
	3
	$161.04
	 

	ESCONDID_GANSO_ESCOND_GANSO1_1
	SBRAPIN8
	ESCOND_GANSO1_1
	BRACKETTVILLE to BRACKETTVILLE LIN 1
	Escondido - Ganso 138kV
	3
	$18.91
	 



[bookmark: _Toc242710759][bookmark: _Hlk219801104]Generic Transmission Constraint Congestion
	GTC
	Days Congestion

	East Texas
	23

	Nelson Sharpe - Rio Hondo
	22

	South Texas Export Pawnee - Spruce
	21

	South Texas Export Pawnee - Tango
	20

	North Edinburg - Lobo
	17

	North - Houston
	10

	Panhandle
	8

	West Texas
	7

	South Texas Import Katoen - Lonhill
	4

	Zapata Starr
	4

	South Texas Import Pawnee - Spruce
	1



There was no activity on the remaining GTCs during the month.
Note: This is how many times a constraint has been activated to avoid exceeding a GTC limit, it does not imply an exceedance of the GTC occurred or that the GTC was binding.
[bookmark: _Toc242710760][bookmark: _Hlk164677736]Manual Overrides
· None
[bookmark: _Toc242710761]Congestion Costs for Calendar Year 2026
The following table represents the top twenty active constraints for the calendar year based on the estimated congestion rent attributed to the congestion. ERCOT updates this list on a monthly basis.

	Contingency Name
	Overloaded Element
	# of 5-min SCED
	Estimated
	Transmission

	BASE CASE
	WESTEX
	18295
	$102,325,256.76
	Permian Basin Relibility Plan (765-kV import paths) (The PUCT approved ,helps improve, but not fully exit, the GTC yet.)

	DWPWFWP5
	STPWAP39_1
	10746
	$70,943,942.51
	 

	MHCKRA25
	HCKSW_MR2L
	1363
	$51,703,803.38
	 

	DBAKCED5
	6965__A
	13081
	$50,101,641.18
	Oncor_FW_81268_Longshore – Consavvy 345 kV Double-Circuit Line Rebuild (MOD 81268)

	BASE CASE
	EASTEX
	12545
	$43,568,286.85
	 

	DWCSRAM5
	35100__A
	386
	$42,503,054.47
	Oncor Southern DFW Load Interconnection and General Grid Strengthening Project (25RPG004)

	SRGRMGS5
	6945__A
	7238
	$34,959,268.92
	West Texas 345-kV Infrastructure Rebuild Project (23RPG034)

	SVENFTS5
	35055__A
	5620
	$34,824,077.83
	Venus Switch to Sam Switch 345-kV Line Project (24RPG017)

	MRNKDHM5
	587__A
	6658
	$34,162,852.87
	 

	DMTSCOS5
	6437__F
	15526
	$33,605,304.01
	Oncor_FW_102849_Union 138 kV Switch (MOD 102849)

	SBWDDBM5
	LPLMK_LPLNE_1
	9938
	$32,285,434.20
	 

	DSALKLN5
	641__A
	2796
	$31,304,486.27
	ONCOR_SE_87703_Belton_Killeen_138 kV Line (via Nolanville) (MOD 87703, 24RPG001)

	DSALHUT5
	1715__B
	5468
	$27,476,036.48
	Temple Area Project (24RPG001). Note that Fryers Creek is named Boggy Creek in planning cases.

	DNAVOUT5
	50__A
	504
	$26,063,843.65
	ONCOR_SE_99622_PIN_OAK_SWITCH (MOD 99622, 25RPG004)

	SCNRFOR5
	FORSW_MR3H
	313
	$23,466,291.82
	Oncor Forney 345/138-kV Switch Rebuild Project (24RPG021)

	DBAKCED5
	HARGRO_TWINBU1_1
	5089
	$23,430,138.42
	 

	BASE CASE
	NE_LOB
	23716
	$23,315,082.42
	San Antonio South Reliability I Project (22RPG048)
LRGV Transmission Improvement Project (21RPG017)
San Antonio South Reliability II Project (23RPG032)

	BASE CASE
	E_PASP
	12724
	$22,524,624.61
	San Antonio South Reliability I Project (22RPG048)
LRGV Transmission Improvement Project (21RPG017)
San Antonio South Reliability II Project (23RPG032)

	BASE CASE
	HHGTOM_1
	9303
	$21,498,853.14
	 

	BASE CASE
	NELRIO
	27085
	$18,845,933.69
	The Lower Rio Grande Valley (LRGV) System Enhancement Project (21RPG017) 



[bookmark: _Toc242710762][bookmark: _Hlk219797360]System Events
[bookmark: _Toc242710763]ERCOT Peak Load
[bookmark: _Toc242710764]The unofficial ERCOT peak load for September 2026 was 86,647 MW and occurred on 9/12/2026 during hour ending 17:00, this is 6,698 MW greater than the September 2025 demand of 79,949 MW on 9/4/2025 during hour ending 18:00. Instantaneous peak for September 2026 was 86,777 MW. Actual instantaneous peak for the same month last year was 80,356 MW.
Load Shed Events
· None.
[bookmark: _Toc242710765]Stability Events
· None.
[bookmark: _Toc242710766]Notable PMU Events
ERCOT analyzes PMU data for any significant system disturbances that do not fall into the Frequency Events category reported in section 2.1. The results are summarized in this section once the analysis has been completed.
There were no PMU events outside of those reported in section 2.1.
[bookmark: _Toc242710767]DC Tie Curtailment
· None.
[bookmark: _Toc242710768][bookmark: _Hlk164863863][bookmark: _Hlk141082606][bookmark: _Hlk135641502]TRE/DOE Reportable Events
· [bookmark: _Toc13724670]Porter Solar submitted a DOE-417 for 09/05/2026 for Damage or destruction of a Facility.
· Oncor submitted an EOP-004-4 for 09/29/2026 for Complete loss of monitoring or control capability at its staffed Bulk Electric System control center for 30 continuous minutes or more.
· Oncor submitted a DOE-417 for 09/29/2026 for Complete loss of monitoring or control capability at its staffed Bulk Electric System control center for 30 continuous minutes or more. 
[bookmark: _Toc242710769]New/Updated Constraint Management Plans
MOD: MP_2025_13 REV4
[bookmark: _Toc242710770]New/Modified/Removed RAS
· None
[bookmark: _Toc242710771]New Procedures/Forms/Operating Bulletins
	[bookmark: _Hlk207973620]Date
	Subject
	Bulletin No.

	9/30/2026
	Shift Supervisor V2 Rev 5
	2040

	9/30/2026
	Reliability Unit Commitment V2 Rev 6
	2039



[bookmark: _Toc242710772][bookmark: _Hlk164863872]Emergency Conditions
[bookmark: _Toc242710773]OCNs
· None 
[bookmark: _Toc242710774]Advisories
	Date and Time
	Message

	September 15, 2026, 1:22 PM
	DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 09/16/2026 due to long run time.

	September 28, 2026, 1:25 PM
	DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 09/29/2026 due to long run time.

	September 29, 2026, 1:16 PM
	DAM Notice: ERCOT has postponed the deadline for the posting of the DAM solution for Operating Day 09/30/2026 due to long run time.



[bookmark: _Toc242710775]Watches
· None
[bookmark: _Toc242710776]Emergency Notices
· None

[bookmark: _Toc242710777]Application Performance
[bookmark: _Toc242710778]TSAT/VSAT Performance Issues
· None.
[bookmark: _Toc242710779]Communication Issues
· None.
[bookmark: _Toc242710780][bookmark: _Hlk164863883]Market System Issues
· None.

[bookmark: _Toc242710781]Model Updates
The Downstream Production Change (DPC) process allows ERCOT to make changes in the one-line Network Operations Model without loading a completely new model.  The purpose of this process is to allow for reliable grid operations as system conditions change between designated Network Operations Model database loads.  The DPC process is limited in scope to just those items listed below, with equipment ratings updates being the most common.  ERCOT has seen a rise in the use of the DPC process to make on-line updates to the Network Operations Model in recent years, instead of through the standard Network Operations Model Change Request process.
· Static Line ratings (Interim Update)
· Dynamic Line ratings (non-Interim Update)
· Autotransformer ratings (non-Interim Update)
· Breaker and Switch Normal status (Interim Update)
· Contingency Definitions (Interim Update)
· RAP and RAS changes or additions (Interim Update)
· Net Dependable and Reactive Capability (NDCRC) values (Interim Update)
· Impedance Updates (non-Interim)
[image: ]
A total of 39 DPCs were implemented in September 2026. 373 DPCs have been implemented year to date. DPCs submitted by TDSPs are mainly updates to transmission element ratings. DPCs submitted by ERCOT are mainly updates to manual contingency definitions. 
	Transmission Operator
	Number of DPCs

	AEP TEXAS COMPANY (TDSP)
	12

	BRAZOS ELECTRIC POWER CO OP INC (TDSP)
	0

	BROWNSVILLE PUBLIC UTILITIES BOARD (TDSP)
	0

	BRYAN TEXAS UTILITIES (TDSP)
	0

	CENTERPOINT ENERGY HOUSTON ELECTRIC LLC (TDSP)
	1

	CITY OF AUSTIN DBA AUSTIN ENERGY (TDSP)
	0

	CITY OF COLLEGE STATION (TDSP)
	0

	CITY OF GARLAND (TDSP)
	0

	CPS ENERGY (TDSP)
	1

	CROSS TEXAS TRANSMISSION LLC (TSP))
	0

	DENTON MUNICIPAL ELECTRIC (TDSP)
	0

	ELECTRIC TRANSMISSION TEXAS LLC (TDSP)
	0

	ERCOT
	0

	LCRA TRANSMISSION SERVICES CORPORATION (TDSP)
	11

	LONE STAR TRANSMISSION LLC (TSP)
	0

	ONCOR ELECTRIC DELIVERY COMPANY LLC (TDSP)
	10

	PEDERNALES ELECTRIC CO OP INC (TDSP)
	1

	RAYBURN COUNTRY CO OP DBA RAYBURN ELECTRIC (TDSP)
	0

	SHARYLAND UTILITIES LP (TDSP)
	0

	SOUTH TEXAS ELECTRIC CO OP INC (TDSP)
	3

	TEXAS MUNICIPAL POWER AGENCY (TDSP)
	0

	TEXAS-NEW MEXICO POWER CO (TDSP)
	0

	WIND ENERGY TRANSMISSION TEXAS LLC (TSP)
	0




[bookmark: _Toc242710782]Appendix A: Real-Time Constraints
The following is a complete list of constraints activated in SCED. Full contingency descriptions can be found in the Standard Contingencies List located on the MIS secure site at Grid  Generation  Reliability Unit Commitment.
	Year
	Month
	Contingency Name
	Overloaded Element
	From Station
	To Station
	Count of Days

	2026
	September
	SPRSPAR8
	1545__A
	FLTSW
	PRSSW
	27

	2026
	September
	SMDOPHR5
	138_ALV_NAL_1
	TNNALVIN
	ALVIN
	27

	2026
	September
	DSALHUT5
	1715__B
	TMPSW
	FRYSW
	24

	2026
	September
	DSALHUT5
	1710__A
	SALDS
	SONTERRA
	24

	2026
	September
	BASE CASE
	EASTEX
	n/a
	n/a
	23

	2026
	September
	SBENS_M8
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	23

	2026
	September
	BASE CASE
	NELRIO
	n/a
	n/a
	22

	2026
	September
	BASE CASE
	E_PASP
	n/a
	n/a
	21

	2026
	September
	BASE CASE
	E_PATA
	n/a
	n/a
	20

	2026
	September
	DWAP_OB5
	MDOPHR99_A
	MDO
	PHR
	19

	2026
	September
	SWCOWCO8
	G138_15_1
	ANGLETON
	WCOLLOCL
	19

	2026
	September
	DFRYBC58
	SEA_AAT1
	SEA
	SEA
	19

	2026
	September
	SWCOWCO8
	G138_15_1
	WCOLLOCL
	ANGLETON
	19

	2026
	September
	DMTSCOS5
	6437__F
	SCRCV
	KNAPP
	19

	2026
	September
	SFURVAN8
	MOURSUND_FUR_1
	MOURSUND
	FURHMAN
	18

	2026
	September
	SFURVAN8
	MOURSUND_FUR_1
	FURHMAN
	MOURSUND
	18

	2026
	September
	SBWDDBM5
	LPLMK_LPLNE_1
	LPLMK
	LPLNE
	18

	2026
	September
	DWO5_EU8
	DT_PK_91_A
	PK
	DT
	18

	2026
	September
	SBLURDH8
	1275__A
	WDBSW
	HLSBR
	18

	2026
	September
	DWPWFWP5
	STPWAP39_1
	STP
	WAP
	18

	2026
	September
	BASE CASE
	NE_LOB
	n/a
	n/a
	17

	2026
	September
	STARLEO8
	SOLSTICE_PST1
	SOLSTICE
	SOLSTICE
	17

	2026
	September
	SMDOOAS5
	GN_PZ_08_A
	GN
	PZ
	17

	2026
	September
	DELMSAN5
	PAWNEE_SPRUCE_1
	PAWNEE
	CALAVERS
	16

	2026
	September
	DBLW2JC5
	WAPWLY72_A
	WLY
	WAP
	16

	2026
	September
	SPEBTRU8
	940__A
	ENWSW
	TMPTN
	16

	2026
	September
	SLAQLOB8
	BRUNI_69_1
	BRUNI
	BRUNI
	15

	2026
	September
	SRGRMGS5
	6945__A
	MGSES
	CATSW
	15

	2026
	September
	MHARNED5
	WESLCO_HIDLBRG_1
	MV_HBRG4
	MV_WESL4
	15

	2026
	September
	MLOFOAV5
	ASHERT_CATARI1_1
	CATARINA
	ASHERTON
	14

	2026
	September
	SBLURDH8
	2270__B
	MEXTP
	ITALY
	14

	2026
	September
	SSTAWIC8
	138_IH2_COT_1
	IH20
	TNCOLIET
	14

	2026
	September
	MLOFOAV5
	ASHERT_CATARI1_1
	ASHERTON
	CATARINA
	14

	2026
	September
	SOBWAP5
	OB_WAP98_A
	WAP
	OB
	13

	2026
	September
	MSNDWCR5
	SNDSW_MR1H
	SNDSW
	SNDSW
	13

	2026
	September
	DTNFBCA8
	138_FTS_LNC_1
	FTST
	LEONCRK
	13

	2026
	September
	DELMSAN5
	POT_OAKS_1
	POTEETS
	OAKS9
	13

	2026
	September
	SBIGV_D8
	GREENL_WEAVER1_1
	WEAVERRD
	GREENLK
	12

	2026
	September
	MHARNED5
	HAINE__LA_PAL1_1
	LA_PALMA
	HAINE_DR
	12

	2026
	September
	MLOFOAV5
	NLARSW_PILONC1_1
	PILONCIL
	NLARSW
	12

	2026
	September
	BASE CASE
	138_FTS_LNC_1
	LEONCRK
	FTST
	12

	2026
	September
	SBCESN35
	455__A
	BGRSW
	SNDSW
	12

	2026
	September
	MLOFOAV5
	NLARSW_PILONC1_1
	NLARSW
	PILONCIL
	12

	2026
	September
	SCARFRI8
	ATSO_SONR1_1
	SONR
	ATSO
	12

	2026
	September
	DWAP_BI5
	BI_JN_64_A
	JN
	BI
	12

	2026
	September
	BASE CASE
	138_FTS_LNC_1
	FTST
	LEONCRK
	12

	2026
	September
	XASH89
	CARIZOSPG_BEVO_1
	BEVO
	CARIZOS
	12

	2026
	September
	SSHAFRO8
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	11

	2026
	September
	DFOAVLO5
	BRUNI_69_1
	BRUNI
	BRUNI
	11

	2026
	September
	SEBATH8
	FB_RS_60_A
	RS
	FB
	11

	2026
	September
	SSHAFRO8
	BENTS_FRTER_1B_1
	S_MISSIN
	FRONTERA
	11

	2026
	September
	DGRMGRS8
	6830__B
	CRDSW
	OLNEY
	11

	2026
	September
	DALASOA8
	138_FTS_LNC_1
	FTST
	LEONCRK
	10

	2026
	September
	BASE CASE
	N_TO_H
	n/a
	n/a
	10

	2026
	September
	SFMRRYS5
	400__A
	FMRVL
	RYSSW
	10

	2026
	September
	DSALHUT5
	CKT_1027_1
	DUNLAP
	DECKER
	10

	2026
	September
	DELMWWE8
	1020__A
	ELMOT
	MCTYE
	10

	2026
	September
	DCPSES12
	810__G
	RDHSW
	BLUMS
	9

	2026
	September
	SHLSWDB8
	810__G
	RDHSW
	BLUMS
	9

	2026
	September
	DRNS_TB5
	THWZEN98_A
	ZEN
	THW
	9

	2026
	September
	SDAFAUS8
	CKT_1027_1
	DUNLAP
	DECKER
	9

	2026
	September
	XVE2N58
	950__B
	SARDIS
	WXHNW
	9

	2026
	September
	DSNDBGR5
	36040__A
	KNBSW
	SALSW
	8

	2026
	September
	SSNDBGR5
	421__A
	BCESW
	SNDSW
	8

	2026
	September
	DFRYTM58
	SEA_AAT1
	SEA
	SEA
	8

	2026
	September
	DAUSLOS5
	196T171_1
	GIDEON
	SETTLE
	8

	2026
	September
	DFOAVLO5
	NLARSW_PILONC1_1
	NLARSW
	PILONCIL
	8

	2026
	September
	SFTLMES8
	PALOUS_WOLFCA1_1
	PALOUSE
	WOLFCAMP
	8

	2026
	September
	SJUNYEL9
	HEXT_MASONS1_1
	HEXT
	MASONSW
	8

	2026
	September
	DFOAVLO5
	NLARSW_PILONC1_1
	PILONCIL
	NLARSW
	8

	2026
	September
	BASE CASE
	PNHNDL
	n/a
	n/a
	8

	2026
	September
	DSTPSTA5
	BLESSING_1382
	BLESSING
	BLESSING
	8

	2026
	September
	MKNGSTE5
	LA_PALMA_XF1A
	LA_PALMA
	LA_PALMA
	8

	2026
	September
	XVIC89
	MAGRUD_VICTOR2_1
	VICTORIA
	MAGRUDER
	8

	2026
	September
	SL_4RAY8
	RAYBURN_69_2
	RAYBURN
	RAYBURN
	8

	2026
	September
	DCDHTVW5
	6200__F
	TYPRK
	PLYAM
	8

	2026
	September
	SCLCGTN8
	6635__G
	MRVLY
	ESTLD
	7

	2026
	September
	SJUNYEL9
	HEXT_YELWJC1_1
	YELWJCKT
	HEXT
	7

	2026
	September
	DFOAVLO5
	ASHERT_CATARI1_1
	CATARINA
	ASHERTON
	7

	2026
	September
	DZORHAY5
	BERGHE_AT1H
	BERGHE
	BERGHE
	7

	2026
	September
	DYETRJU8
	HEXT_YELWJC1_1
	YELWJCKT
	HEXT
	7

	2026
	September
	SZENTHW5
	THWZEN98_A
	ZEN
	THW
	7

	2026
	September
	SBRAHAM8
	ESCOND_GANSO1_1
	ESCONDID
	GANSO
	7

	2026
	September
	SMAYWHI8
	NUECES_WHITE_2_1
	NUECES_B
	WHITE_PT
	7

	2026
	September
	SP5CAG8
	D5_S1_1
	HOWARD
	LEON_CRK
	7

	2026
	September
	DMCDUPS8
	HECKER_RESNIK1_1
	HECKER
	RESNIK
	7

	2026
	September
	DBIGSCH5
	PALOUS_WOLFCA1_1
	PALOUSE
	WOLFCAMP
	7

	2026
	September
	SFURVAN8
	RAYBURN_69_2
	RAYBURN
	RAYBURN
	7

	2026
	September
	MLOFOAV5
	SND_ORAN_1
	ORNGROV
	SNDIEGS
	7

	2026
	September
	SALVTNN8
	138_FWP_MNL_1
	FRWYPARK
	MAINLAND
	7

	2026
	September
	BASE CASE
	WESTEX
	n/a
	n/a
	7

	2026
	September
	DFOAVLO5
	ASHERT_CATARI1_1
	ASHERTON
	CATARINA
	7

	2026
	September
	SRAYRI38
	HAINE__LA_PAL1_1
	LA_PALMA
	HAINE_DR
	6

	2026
	September
	SPALFRO8
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	6

	2026
	September
	DLEOPEA8
	D5_V4TP_1
	LEON_CRK
	V4_TAP
	6

	2026
	September
	SMOOPEA8
	POT_OAKS_1
	POTEETS
	OAKS9
	6

	2026
	September
	SBLURDH8
	1210__B
	HUBRD
	HAN1
	6

	2026
	September
	DLEOPEA8
	D5_V4TP_1
	V4_TAP
	LEON_CRK
	6

	2026
	September
	SCISPUT8
	LENSW_PUTN2_1
	LENSW
	PUTN
	6

	2026
	September
	DPRSHWK8
	1545__A
	FLTSW
	PRSSW
	6

	2026
	September
	BASE CASE
	138_ALV_NAL_1
	TNNALVIN
	ALVIN
	6

	2026
	September
	SPETSNU8
	AE_STR26_A
	AE
	STR
	6

	2026
	September
	SBRAPIN8
	ESCOND_GANSO1_1
	ESCONDID
	GANSO
	6

	2026
	September
	SBRAPIN8
	ESCOND_GANSO1_1
	GANSO
	ESCONDID
	6

	2026
	September
	SWOLPAL8
	LAKENA_SAMATH1_1
	LAKENASW
	SAMATHIS
	6

	2026
	September
	SCALBAN9
	SND_ORAN_1
	ORNGROV
	SNDIEGS
	6

	2026
	September
	SBUZHMP8
	6217__B
	MPPOI
	KEYSB
	5

	2026
	September
	SWOLPAL8
	CROSSO_PALOUS1_1
	PALOUSE
	CROSSOVE
	5

	2026
	September
	DFOWSMG5
	COTULL_REVEIL1_1
	REVEILLE
	COTULLA
	5

	2026
	September
	SCOLBAL8
	BALLINGE_FMRL
	BALLINGE
	BALLINGE
	5

	2026
	September
	STARLEO8
	138_FTS_LNC_1
	LEONCRK
	FTST
	5

	2026
	September
	DPPRTEC8
	610__B
	TMPSW
	TMPSE
	5

	2026
	September
	DSALKLN5
	KLNSW_MR1H
	KLNSW
	KLNSW
	5

	2026
	September
	DWCSRAM5
	35100__A
	PKRSW
	HCKSW
	5

	2026
	September
	SVEROK28
	SANDRO_VERS1_1
	VERS
	SANDROAD
	5

	2026
	September
	DSALHUT5
	GABRIE_AT1
	GABRIE
	GABRIE
	5

	2026
	September
	SDELLAR8
	NLARSW_UNITEC1_1
	NLARSW
	UNITEC
	5

	2026
	September
	DDL_KR_8
	SIEWAP05_A
	WAP
	SIE
	5

	2026
	September
	DBIGKEN5
	TREADW_YELWJC1_1
	TREADWEL
	YELWJCKT
	5

	2026
	September
	SGEOORN8
	ORNGROV_69_1
	ORNGROV
	ORNGROV
	5

	2026
	September
	SVENFTS5
	35055__A
	SAMSW
	VENSW
	5

	2026
	September
	DMGSRIC8
	6840__B
	NVKSW
	ANARN
	5

	2026
	September
	DWTRWLV5
	3170__B
	SMPST
	BNTDR
	4

	2026
	September
	BASE CASE
	I_KALO
	n/a
	n/a
	4

	2026
	September
	DVICDUP8
	BIGTRE_V_DUPS1_1
	V_DUPSW
	BIGTRE
	4

	2026
	September
	SHONMOO8
	BIG_FOOT_69A1
	BIG_FOOT
	BIG_FOOT
	4

	2026
	September
	DELMSAN5
	MAGRUD_VICTOR2_1
	VICTORIA
	MAGRUDER
	4

	2026
	September
	BASE CASE
	B4_V4_1
	V4
	B4
	4

	2026
	September
	BASE CASE
	ZAPSTR
	n/a
	n/a
	4

	2026
	September
	SABSBLU8
	ABINDU_MULBER1_1
	MULBERRY
	ABINDUST
	4

	2026
	September
	BASE CASE
	B4_V2_1
	B4
	V2
	4

	2026
	September
	SSNYCGR8
	SNYDR_FMR1
	SNYDR
	SNYDR
	4

	2026
	September
	SFMRRY25
	381__A
	FMRVL
	RYSSW
	4

	2026
	September
	BASE CASE
	D5_V4_1
	LEON_CRK
	V4
	4

	2026
	September
	DBCVPSA8
	LHMLY_08_A
	LHM
	LY
	4

	2026
	September
	SPAWCAL5
	MAGRUD_VICTOR2_1
	VICTORIA
	MAGRUDER
	4

	2026
	September
	SFTLMES8
	CROSSO_NORTMC1_1
	NORTMC
	CROSSOVE
	4

	2026
	September
	SFTCGAR8
	BALLINGE_FMRL
	BALLINGE
	BALLINGE
	4

	2026
	September
	SI_2RES8
	I_DUPS_RESNIK3_3
	I_DUPSW
	RESNIK
	4

	2026
	September
	SHLSWH28
	1210__B
	HUBRD
	HAN1
	3

	2026
	September
	SABSBLU8
	OAKC_PERSHI1_1
	OAKC
	PERSHING
	3

	2026
	September
	MBULNAV5
	35045__A
	SAMSW
	FVLSW
	3

	2026
	September
	SGRIRAP5
	REFUG_VICTO_1C_1
	VICTORIA
	OCONNOR
	3

	2026
	September
	SVLGLO8
	SN_STR26_A
	SN
	STR
	3

	2026
	September
	SMOOPEA8
	UVALDE_W_BATE1_1
	W_BATESV
	UVALDE
	3

	2026
	September
	SCMNCPS5
	651__B
	CMNSW
	CMNTP
	3

	2026
	September
	SGRMGRS8
	6830__B
	CRDSW
	OLNEY
	3

	2026
	September
	DGABGEA8
	GABRIE_AT1
	GABRIE
	GABRIE
	3

	2026
	September
	DLIMHOR5
	722T782_1
	CANYON
	ROHR
	3

	2026
	September
	SHONMOO8
	BIG_FO_PLEASA1_1
	BIG_FOOT
	PLEASANT
	3

	2026
	September
	XCMB58
	CRD_CRD2
	CRD
	CRD
	3

	2026
	September
	SANGSTA5
	BLESSING_1382
	BLESSING
	BLESSING
	3

	2026
	September
	SLARLAS8
	DEL_MA_UNIVER1_1
	DEL_MAR
	UNIVERSI
	3

	2026
	September
	DYETRJU8
	HEXT_MASONS1_1
	HEXT
	MASONSW
	3

	2026
	September
	DBLUBUF8
	OAKC_PERSHI1_1
	OAKC
	PERSHING
	3

	2026
	September
	SHLSWH28
	1210__B
	HAN1
	HUBRD
	3

	2026
	September
	DHLYTRC5
	ELKTN_MR3H
	ELKTN
	ELKTN
	3

	2026
	September
	DWPWFWP5
	155T217_1
	BELLSO
	PT
	3

	2026
	September
	DLONPK25
	6375__A
	GRSES
	GRMES
	3

	2026
	September
	DENWSTE8
	ROC_ROCK_1
	ROCKETT
	ROCKETSW
	3

	2026
	September
	DSALGA58
	GABRIE_AT1
	GABRIE
	GABRIE
	3

	2026
	September
	DBAKCED5
	LAKENA_SAMATH1_1
	LAKENASW
	SAMATHIS
	3

	2026
	September
	SBWDDBM5
	LPLNW_LPLMD_1
	LPLNW
	LPLMD
	3

	2026
	September
	SGIDLIN8
	215T215_1
	HIGH36
	BRENNO
	3

	2026
	September
	DPHRCTR5
	MDOPHR99_A
	MDO
	PHR
	2

	2026
	September
	DSCOTKW5
	6215__A
	BCKSW
	CGRSW
	2

	2026
	September
	DMTSCOS5
	6240__C
	SACRC
	DPCRK
	2

	2026
	September
	SECRDMT8
	6437__F
	SCRCV
	KNAPP
	2

	2026
	September
	SRICGRS8
	6840__A
	ANARN
	CRDSW
	2

	2026
	September
	DLYTZOR5
	722T782_1
	CANYON
	ROHR
	2

	2026
	September
	SANGSTA5
	BLESSI_PALACI1_1
	BLESSING
	PALACIOS
	2

	2026
	September
	DCHBJO25
	CBYCVN86_A
	CBY
	CVN
	2

	2026
	September
	DNP_PLA8
	HB_KW_66_A
	HB
	KW
	2

	2026
	September
	STNFTAR8
	138_FTS_LNC_1
	FTST
	LEONCRK
	2

	2026
	September
	SBTPBNT8
	2115__B
	TOWER
	BNTSW
	2

	2026
	September
	DEVRHLS8
	6293__C
	MARSW
	DEVIT
	2

	2026
	September
	XVE2N58
	951__A
	STERT
	SARDIS
	2

	2026
	September
	DFRYBC58
	BELCNTY_XFMR
	BELCNTY
	BELCNTY
	2

	2026
	September
	DBIGSCH5
	CROSSO_NORTMC1_1
	NORTMC
	CROSSOVE
	2

	2026
	September
	SBIGOR45
	FORTMA_YELWJC1_1
	FORTMA
	YELWJCKT
	2

	2026
	September
	SBIGOR45
	FORTMA_YELWJC1_1
	YELWJCKT
	FORTMA
	2

	2026
	September
	SGA2ROM8
	GARZA_XF1H
	GARZA
	GARZA
	2

	2026
	September
	DMCEBUT8
	MKLT_TRNT1_1
	TRNT
	MKLT
	2

	2026
	September
	SSPUASP8
	SPUR_69_1
	SPUR
	SPUR
	2

	2026
	September
	DCC1DUKE
	WESLCO_HIDLBRG_1
	MV_HBRG4
	MV_WESL4
	2

	2026
	September
	SDBLBN28
	12010__A
	GRSSW
	WTHSW
	2

	2026
	September
	DFORCN85
	1395__A
	MESQE
	OATES
	2

	2026
	September
	DPRSHWK8
	1535__B
	TNSKA
	TCOSW
	2

	2026
	September
	MNLFIWO8
	904T485_1
	GOODWIN
	FRONTERA
	2

	2026
	September
	SKITGEO9
	ARGENTA_AMATH_1
	MATHIS
	ARGENTA
	2

	2026
	September
	BASE CASE
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	2

	2026
	September
	SLARLAS8
	GATEET_UNIVER1_1
	UNIVERSI
	GATEETP
	2

	2026
	September
	SMCEESK8
	MKLT_TRNT1_1
	MKLT
	TRNT
	2

	2026
	September
	SRVRSLK5
	SLKSW_AX1L
	SLKSW
	SLKSW
	2

	2026
	September
	DWTRWLV5
	3610__G
	PGTP1
	PDSES
	2

	2026
	September
	MKNGSTE5
	BENTS_FRTER_1B_1
	FRONTERA
	S_MISSIN
	2

	2026
	September
	MKNGSTE5
	LA_PALMA_XF1B
	LA_PALMA
	LA_PALMA
	2

	2026
	September
	DBLBYWF5
	STPWAP39_1
	STP
	WAP
	2

	2026
	September
	DBAKCED5
	225T558_1
	BIGHIL
	OERSTED
	2

	2026
	September
	DROUCHI8
	228T333_1
	LAGOVI
	NAMELE
	2

	2026
	September
	SILLFTL8
	CARVER_TINSLE1_1
	CARVER
	TINSLEY
	2

	2026
	September
	DCMBCPS8
	CRD_CRD2
	CRD
	CRD
	2

	2026
	September
	SDELLAR8
	GATEWT_WORMSE1_1
	GATEWTP
	WORMSER
	2

	2026
	September
	SCROPAL8
	LAKENA_SAMATH1_1
	LAKENASW
	SAMATHIS
	2

	2026
	September
	DWO5_EU8
	MIDGT_90_A
	GT
	MID
	2

	2026
	September
	DDORELK5
	SCSES_MR1H
	SCSES
	SCSES
	2

	2026
	September
	SSAMTCR5
	505__B
	FBRSW
	THSES
	2

	2026
	September
	MTRYBRO8
	6217__B
	MPPOI
	KEYSB
	2

	2026
	September
	SCNRFOR5
	FORSW_MR3H
	FORSW
	FORSW
	2

	2026
	September
	BASE CASE
	HENWAP01_A
	WAP
	HEN
	2

	2026
	September
	DCBYJOR5
	HOPWRN84_A
	HOP
	WRN
	2

	2026
	September
	BASE CASE
	WESLCO_HIDLBRG_1
	MV_HBRG4
	MV_WESL4
	2

	2026
	September
	DMLSE123
	31__A
	RCHBR
	TRSES
	2

	2026
	September
	MNLFIWO8
	904T485_1
	FRONTERA
	GOODWIN
	2

	2026
	September
	DJCY_CC1
	BOW_FMR1
	BOW
	BOW
	2

	2026
	September
	SBRAPIN8
	HAMILT_MAVERI1_1
	HAMILTON
	MAVERICK
	2

	2026
	September
	SHONF38
	HON_DEVI_1
	HONDOCK
	DEVINESW
	2

	2026
	September
	SMCEESK8
	MKLT_TRNT1_1
	TRNT
	MKLT
	2

	2026
	September
	SRVRSLK5
	SLKSW_AX1H
	SLKSW
	SLKSW
	2

	2026
	September
	SWCOW2C8
	_WC_WCO_1
	WC
	WCOLMAIN
	2

	2026
	September
	DMTSCOS5
	6437__A
	KNAPP
	BCKSW
	2

	2026
	September
	DBLUBUF8
	ABINDU_MULBER1_1
	MULBERRY
	ABINDUST
	2

	2026
	September
	DKG_NB_5
	BCVPSA03_A
	PSA
	BCV
	2

	2026
	September
	SEL_ARR8
	BLESSING_69A1
	BLESSING
	BLESSING
	2

	2026
	September
	SA4LEO8
	D5_V4TP_1
	LEON_CRK
	V4_TAP
	2

	2026
	September
	BASE CASE
	FTST_SOLSTI1_1
	FTST
	SOLSTICE
	2

	2026
	September
	SDELLAR8
	GATEWT_UNITEC1_1
	UNITEC
	GATEWTP
	2

	2026
	September
	BASE CASE
	HAINE__LA_PAL1_1
	LA_PALMA
	HAINE_DR
	2

	2026
	September
	DTPCTHS5
	LCSES_MR1H
	LCSES
	LCSES
	2

	2026
	September
	SGEOHU48
	221T355_1
	CHIEBR
	GEORGE
	1

	2026
	September
	SHLSWH28
	2270__B
	MEXTP
	ITALY
	1

	2026
	September
	SBTPBNT8
	583__E
	KRMSW
	KRUMS
	1

	2026
	September
	DMBDRKC5
	651__B
	CMNSW
	CMNTP
	1

	2026
	September
	SRICGRS8
	6840__B
	NVKSW
	ANARN
	1

	2026
	September
	DBEANOR5
	6965__A
	LNGSW
	PRLSW
	1

	2026
	September
	DLIMHOR5
	7T246_1
	ZORN
	LYTTON_S
	1

	2026
	September
	SGRIRAP5
	BIGTRE_V_DUPS1_1
	V_DUPSW
	BIGTRE
	1

	2026
	September
	SMDOOAS5
	BI_KB_37_A
	BI
	KB
	1

	2026
	September
	BASE CASE
	BURNS_RIOHONDO_1
	RIOHONDO
	MV_BURNS
	1

	2026
	September
	BASE CASE
	HHGTOM_1
	HHGT
	OMEGA
	1

	2026
	September
	DHUTLIM5
	HUTTO_MR2H
	HUTTO
	HUTTO
	1

	2026
	September
	DDL_KR_8
	IM_WAP05_A
	WAP
	IM
	1

	2026
	September
	DLOBCEN5
	LON_HI_ORNGRO1_1
	LON_HILL
	ORNGROV
	1

	2026
	September
	SKITGEO9
	ORNGROV_69_1
	ORNGROV
	ORNGROV
	1

	2026
	September
	SMOOPEA8
	PALDRO_DILLEY_1
	PALODURO
	DILLEYSW
	1

	2026
	September
	SFORRAY8
	RAYBURN_69_2
	RAYBURN
	RAYBURN
	1

	2026
	September
	MDCQCLK5
	SANDRO_VERS1_1
	VERS
	SANDROAD
	1

	2026
	September
	DLOFOAV5
	SND_ORAN_1
	ORNGROV
	SNDIEGS
	1

	2026
	September
	XFOR58
	200__A
	FORSW
	RYSSW
	1

	2026
	September
	DCAGCO58
	583T583_1
	BANDER
	MASOCR
	1

	2026
	September
	SSPRVAL8
	595__A
	BNTSW
	DCATR
	1

	2026
	September
	SMGPBRN8
	650__B
	PNKNY
	BRNWD
	1

	2026
	September
	SCARLVO8
	ATSO_SONR1_1
	SONR
	ATSO
	1

	2026
	September
	SSTPSTA5
	BLESSING_1382
	BLESSING
	BLESSING
	1

	2026
	September
	DSTOGAR8
	CKT_943_1
	LYTTON_S
	PILOT
	1

	2026
	September
	DRAFOMI8
	E3_X2_1
	E3
	X2
	1

	2026
	September
	SCARFRI8
	FDR_OZNC_1
	OZNC
	FRIEND_R
	1

	2026
	September
	STARLEO8
	FTST_SOLSTI1_1
	FTST
	SOLSTICE
	1

	2026
	September
	SCT2CAR8
	HAMILT_MAXWEL1_1
	MAXWELL
	HAMILTON
	1

	2026
	September
	SMDOPHR5
	MDO_AT1
	MDO
	MDO
	1

	2026
	September
	DRNS_TB5
	NB_THW97_A
	THW
	NB
	1

	2026
	September
	SFTLMES8
	SANTAR_WOLFCA1_1
	WOLFCAMP
	SANTARIT
	1

	2026
	September
	BASE CASE
	SOLSTICE_PST1
	SOLSTICE
	SOLSTICE
	1

	2026
	September
	SPIGSOL8
	138_FTS_LNC_1
	FTST
	LEONCRK
	1

	2026
	September
	SBLAWDB8
	2270__B
	MEXTP
	ITALY
	1

	2026
	September
	SMYRSPR8
	583__D
	DCRSW
	ALISN
	1

	2026
	September
	DDHMLWS5
	595__A
	BNTSW
	DCATR
	1

	2026
	September
	DCMNFUL8
	660__B
	MGPSW
	ZEPHYR
	1

	2026
	September
	SABSBLU8
	6940__D
	CLCTY
	PLOWB
	1

	2026
	September
	SCITWEI8
	CLARK__LON_HI1_1
	LON_HILL
	CLARK_WD
	1

	2026
	September
	SGARBAL8
	CONCHO_HARI1_A
	CONCHO
	HARI
	1

	2026
	September
	XBAL89
	CONCHO_HARI1_A
	CONCHO
	HARI
	1

	2026
	September
	SPAUSAR8
	CONCHO_SAEM1_1
	CONCHO
	SAEM
	1

	2026
	September
	DNLPIMI8
	DEL_MA_UNIVER1_1
	DEL_MAR
	UNIVERSI
	1

	2026
	September
	SHELKEN8
	F2_11_1
	KENEDSW
	F2
	1

	2026
	September
	DBIGKEN5
	FORTMA_YELWJC1_1
	YELWJCKT
	FORTMA
	1

	2026
	September
	SABSBLU8
	LENSW_PUTN2_1
	LENSW
	PUTN
	1

	2026
	September
	SBOSWHT8
	LKW_WHT_1
	LKWHITNY
	WHTNY
	1

	2026
	September
	SANGSTA5
	MOURSUND_FUR_1
	FURHMAN
	MOURSUND
	1

	2026
	September
	XBLU58
	ORNT_REDCRE1_1
	REDCREEK
	ORNT
	1

	2026
	September
	SBIGOR45
	TREADW_YELWJC1_1
	TREADWEL
	YELWJCKT
	1

	2026
	September
	SFURMOU8
	VAN_VNDB_1
	VANBLTSS
	VANBLT69
	1

	2026
	September
	DHWKRCS8
	1545__A
	FLTSW
	PRSSW
	1

	2026
	September
	DTRSTRC5
	1852__A
	TRSES
	NPKTP
	1

	2026
	September
	DFRYBC58
	2395__B
	PGE
	TMPTV
	1

	2026
	September
	SODETES5
	6052__C
	QALSW
	TESSW
	1

	2026
	September
	DCDHTVW5
	6200__E
	PRKRW
	TYPRK
	1

	2026
	September
	DCRLCY28
	710__B
	CRLNW
	CYPSW
	1

	2026
	September
	SLYTZOR5
	722T782_1
	CANYON
	ROHR
	1

	2026
	September
	DHLYTRC5
	985__A
	FGLSW
	ATHNW
	1

	2026
	September
	SCARFRI8
	ATSO_OZNC1_1
	ATSO
	OZNC
	1

	2026
	September
	DWAP_JN5
	BI_WAP50_A
	WAP
	BI
	1

	2026
	September
	SANGSTA5
	BLESSING_69A1
	BLESSING
	BLESSING
	1

	2026
	September
	SLOLFOR8
	BROOKT_JOSLIN1_1
	JOSLIN
	BROOKTAP
	1

	2026
	September
	SWAATH8
	FB_RS_60_A
	RS
	FB
	1

	2026
	September
	DDNEDBP5
	FREER_LOBO1_1
	LOBO
	FREER
	1

	2026
	September
	SHASTNN8
	G138_8A_1
	PHR
	HDNLAKES
	1

	2026
	September
	SGA2ROM8
	GARZA_XF1L
	GARZA
	GARZA
	1

	2026
	September
	BASE CASE
	I_PASP
	n/a
	n/a
	1

	2026
	September
	DSALHUT5
	KLNSW_MR1H
	KLNSW
	KLNSW
	1

	2026
	September
	XBLU58
	ORNT_TENNYS1_1
	ORNT
	TENNYSON
	1

	2026
	September
	SANGSTA5
	REFUG_VICTO_1C_1
	VICTORIA
	OCONNOR
	1

	2026
	September
	BASE CASE
	RYSSW_FMR1
	RYSSW
	RYSSW
	1

	2026
	September
	DAE_AE_8
	RZ_WML26_A
	WML
	RZ
	1

	2026
	September
	MBONNED5
	WESLCO_HIDLBRG_1
	MV_HBRG4
	MV_WESL4
	1

	2026
	September
	SCOMKEN8
	115T123_1
	KENDAL
	KERRST
	1

	2026
	September
	SHWKLBL8
	1545__A
	FLTSW
	PRSSW
	1

	2026
	September
	SQALTES5
	6054__B
	ODEHV
	TESSW
	1

	2026
	September
	MDBHRSA5
	6085__E
	WFSSW
	NSTAR
	1

	2026
	September
	SCR2CRL8
	710__B
	CRLNW
	CYPSW
	1

	2026
	September
	SCRLHKB5
	710__B
	CRLNW
	CYPSW
	1

	2026
	September
	SBROCOC9
	ALPINE_BRONCO1_1
	BRONCO
	ALPINE
	1

	2026
	September
	DSALHUT5
	BALLIN_PAINTR1_1
	BALLINGE
	PAINTROC
	1

	2026
	September
	XBA2N89
	BANDER_AT2
	BANDER
	BANDER
	1

	2026
	September
	SPETSNU8
	BFPCAV82_A
	CAV
	BFP
	1

	2026
	September
	SV_DVI28
	BIGTRE_V_DUPS1_1
	V_DUPSW
	BIGTRE
	1

	2026
	September
	SDANBLE8
	BLESSING_69A1
	BLESSING
	BLESSING
	1

	2026
	September
	SOAKNIC8
	CEDRHI_SILT1_1
	SILT
	CEDRHILL
	1

	2026
	September
	DDECWAC8
	CKT_1021_1
	BERGSTRO
	KINGSBER
	1

	2026
	September
	XMDO58
	GN_PZ_08_A
	GN
	PZ
	1

	2026
	September
	SMDOOAS5
	GT_KB_37_A
	KB
	GT
	1

	2026
	September
	BASE CASE
	HI_LONE_TLINE_1
	HI_LONE
	CEDACA
	1

	2026
	September
	DHUNMED8
	J0_R1_1
	J0
	R1
	1

	2026
	September
	DBIGKEN5
	MADDUX_TREADW1_1
	MADDUX
	TREADWEL
	1

	2026
	September
	DWPWFCK5
	STPWAP39_1
	STP
	WAP
	1

	2026
	September
	DSNG_TB5
	THWZEN98_A
	ZEN
	THW
	1

	2026
	September
	BASE CASE
	X5_ALAMO1_1
	OCI_ALM1
	X5
	1

	2026
	September
	SWORBRD8
	138_WIC_STG_1
	WICKETT
	STAGHORN
	1

	2026
	September
	DCAGCI58
	255T279_1
	PIPECR
	MEDILA
	1

	2026
	September
	SGRIRAP5
	2992_1
	OCONNOR
	GRETA
	1

	2026
	September
	DCDHMCS8
	3150__A
	CDCSW
	OKCLS
	1

	2026
	September
	DBCEBGR5
	36040__A
	KNBSW
	SALSW
	1

	2026
	September
	DHILMAR5
	361T361_1
	SCHERT
	PARKWA
	1

	2026
	September
	SECRDMT8
	6215__A
	BCKSW
	CGRSW
	1

	2026
	September
	DBUCRGP5
	651__B
	CMNSW
	CMNTP
	1

	2026
	September
	DCPSST58
	651__B
	CMNSW
	CMNTP
	1

	2026
	September
	SSCLWF18
	6840__B
	NVKSW
	ANARN
	1

	2026
	September
	DCMBCLB8
	950__B
	SARDIS
	WXHNW
	1

	2026
	September
	DBAKCED5
	ATSO_SONR1_1
	SONR
	ATSO
	1

	2026
	September
	SA4LEO8
	B4_V4_1
	V4
	B4
	1

	2026
	September
	DSTEXP12
	BALLIN_PAINTR1_1
	BALLINGE
	PAINTROC
	1

	2026
	September
	XBAN89
	BANDER_AT3
	BANDER
	BANDER
	1

	2026
	September
	SA4LEO8
	D5_J0_1
	LEON_CRK
	J0
	1

	2026
	September
	DSKYNAC8
	FRA_PAR_1
	PARKWA
	S4
	1

	2026
	September
	DBLBYWF5
	JCKSTP18_A
	STP
	JCK
	1

	2026
	September
	DNOESGT5
	LAKENA_SAMATH1_1
	LAKENASW
	SAMATHIS
	1

	2026
	September
	SCARLVO8
	LAKENA_SAMATH1_1
	LAKENASW
	SAMATHIS
	1

	2026
	September
	BASE CASE
	LA_PALMA_XF1A
	LA_PALMA
	LA_PALMA
	1

	2026
	September
	SMOOPEA8
	NBA_S_BA_1
	S_BATES
	NBATSVS
	1

	2026
	September
	SAILAB48
	OILMIT_SAWGRA1_1
	SAWGRASS
	OILMITAP
	1

	2026
	September
	SP5CAG8
	R2_U4_1
	R2
	U4
	1

	2026
	September
	SFURMOU8
	RAYBURN_69_2
	RAYBURN
	RAYBURN
	1

	2026
	September
	DOASSEB5
	WAPWLY72_A
	WLY
	WAP
	1

	2026
	September
	MKNGSTE5
	WESLCO_HIDLBRG_1
	MV_HBRG4
	MV_WESL4
	1

	2026
	September
	SSOAHOL8
	138_FTS_LNC_1
	FTST
	LEONCRK
	1

	2026
	September
	DSALHUT5
	1710__B
	SONTERRA
	JREST
	1

	2026
	September
	DSTBELB5
	35045__A
	SAMSW
	FVLSW
	1

	2026
	September
	SSUNRGR8
	6240__C
	SACRC
	DPCRK
	1

	2026
	September
	DMTSCOS5
	6426__A
	DMTSW
	ECRSW
	1

	2026
	September
	DMGSBTR5
	6437__F
	SCRCV
	KNAPP
	1

	2026
	September
	SMGPBRN8
	650__A
	CMNSW
	PNKNY
	1

	2026
	September
	DPRSPAC5
	874__A
	CRSSW
	COMSW
	1

	2026
	September
	XVE2N58
	945__B
	GLNHT
	STERT
	1

	2026
	September
	SABSBLU8
	ABNTHW_SERDEV1_1
	ABNTHWST
	ABNTHWST
	1

	2026
	September
	SHAMMAX8
	ATSO_SONR1_1
	SONR
	ATSO
	1

	2026
	September
	SCOLBAL8
	BALLIN_HUMBLT1_1
	BALLINGE
	HUMBLTAP
	1

	2026
	September
	DGABGEA8
	BELCNTY_XFMR
	BELCNTY
	BELCNTY
	1

	2026
	September
	DCE_OB28
	BM_WD_73_A
	BM
	WD
	1

	2026
	September
	SABSBLU8
	CALLAH_PERSHI1_1
	PERSHING
	CALLAHAN
	1

	2026
	September
	SSACBUR9
	CEDRHI_SILT1_1
	CEDRHILL
	SILT
	1

	2026
	September
	BASE CASE
	DT_PK_91_A
	PK
	DT
	1

	2026
	September
	SMCEESK8
	ESKSW_TRNT1_1
	TRNT
	ESKSW
	1

	2026
	September
	SFURMOU8
	FURHMAN_VANDB_1
	FURHMAN
	VANBLTSS
	1

	2026
	September
	DBI_GT_8
	HT_TAP24_1
	HT
	HT
	1

	2026
	September
	XMDO58
	MDO_AT1
	MDO
	MDO
	1

	2026
	September
	DBWN_AM5
	ORNT_REDCRE1_1
	REDCREEK
	ORNT
	1

	2026
	September
	SFURVAN8
	RAY_MOURSUND_1
	MOURSUND
	RAYBURN
	1

	2026
	September
	SWALWLN8
	SWI_OLIN_1
	OLINGR
	SWINDELL
	1

	2026
	September
	DELMWWE8
	1210__A
	HAN1
	REVSW
	1

	2026
	September
	SBOSELM5
	1210__A
	HAN1
	REVSW
	1

	2026
	September
	DELMWWE8
	1210__B
	HUBRD
	HAN1
	1

	2026
	September
	SWORBRD8
	138_PYT_STG_1
	STAGHORN
	PYOTE
	1

	2026
	September
	SSTAPYO8
	138_WOR_HRT_1
	HARPOONT
	WORSHAM
	1

	2026
	September
	SMCCCNR5
	1395__A
	MESQE
	OATES
	1

	2026
	September
	SWDDMNS5
	403__A
	PRSSW
	VLYSO
	1

	2026
	September
	DDHMLWS5
	587__A
	ARGYL
	LWSVH
	1

	2026
	September
	DMTSCOS5
	6217__B
	MPPOI
	KEYSB
	1

	2026
	September
	DFRYTM58
	630__A
	BLTON
	BLTSW
	1

	2026
	September
	SHAYZO25
	6T227_1
	HAYSEN
	ZORN
	1

	2026
	September
	DBLUBUF8
	ABNTHW_SERDEV1_1
	ABNTHWST
	ABNTHWST
	1

	2026
	September
	DLEOPEA8
	B4_V4_1
	V4
	B4
	1

	2026
	September
	DYELHE89
	BALLIN_PAINTR1_1
	BALLINGE
	PAINTROC
	1

	2026
	September
	DLOBCEN5
	CALLIC_PORTIL1_1
	CALLICOA
	PORTILLA
	1

	2026
	September
	MLOFOAV5
	CATARI_PILONC1_1
	CATARINA
	PILONCIL
	1

	2026
	September
	SMCEESK8
	ESKSW_TRNT1_1
	ESKSW
	TRNT
	1

	2026
	September
	SGRSMNW8
	MIL_LIPAN_1
	LONG
	LIPAN
	1

	2026
	September
	DLOFOAV5
	NLARSW_PILONC1_1
	PILONCIL
	NLARSW
	1

	2026
	September
	DCAGPIN8
	P5_X1_1
	P5
	X1
	1

	2026
	September
	SFURVAN8
	RAY_L_46_1
	RAYBURN
	L_463S
	1
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___ 50C% Heatmap by Date and Hour Ending (Hourly Average SOC%) (2026-09-01 to 2026-09-30)
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