Summary of Nodal Operating Guide Revisions

Effective:  November 1, 2026
Section 2:
NOGRR226 – Addition of Supplemental UFLS Stages
This Nodal Operating Guide Revision Request (NOGRR) adds provisions for Transmission Operator (TO) “anti-stall” automatic firm Load shedding at 59.5 Hz in order to improve reliability by mitigating the risk of a total system-wide Blackout.
Revised Subsection:  2.6.1 [unboxed due to system implementation]
NOGRR247 – Change UFLS Stages and Load Relief Amounts
This Nodal Operating Guide Revision Request (NOGRR) modifies the ERCOT automatic Under-Frequency Load Shed (UFLS) program by increasing the number of Load shed stages from three to five and changing the Transmission Operator (TO) Load relief amounts to uniformly increment by 5% for each stage.  The NOGRR also adds a UFLS minimum time delay of six cycles (0.1 seconds), and adds 59.1 Hz to the list of UFLS stages in paragraph (3) of Section 2.6.1, Automatic Firm Load Shedding.  Additionally, this NOGRR revises the grey-boxed language from NOGRR226, Addition of Supplemental UFLS Stages, in Section 2.6.1 to provide that the TO Load value used to determine the TO Load at each frequency threshold in Table 1, Standard UFLS Stages, will be the value of TO Load at the time frequency reaches 59.5 Hz, rather than the value of TO Load at the time of reaching each successive frequency threshold, consistent with the current method for determining TO Load in Table 1.
Revised Subsection:  2.6.1 [unboxed due to system implementation]
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