TEXAS EV ALLIANCE | OCTOBER 26, 2026

Comments on ERCOT Phase 4
and bidirectional EV participation

Comments of Texas EV Alliance

To: Electric Reliability Council of Texas
Re: Aggregate Distributed Energy Resource Pilot Project Governing Document, Phase 4
October 12, 2026 clean draft

Support the aggregated storage direction

Texas EV Alliance supports advancing Phase 4 of the Electric Reliability Council of Texas (ERCOT) Aggregate Distributed Energy Resource (ADER) Pilot Project. The proposed Aggregate Distributed Energy Storage Resource (ADESR) option would give aggregated distribution-connected storage a more direct role in dispatch and allow evaluation of its effects on transmission congestion. Under the proposal, ADESRs would use nodal dispatch through Security-Constrained Economic Dispatch (SCED), retain load-zone energy settlement, and not initially provide ancillary services. [1, Sections 1, 5.b.3, 5.f.3 and 5.h]

The Alliance recommends technology-neutral eligibility based on demonstrated capability and performance, with implementation procedures that accommodate qualifying bidirectional electric vehicle (EV) systems. Vehicle-to-grid (V2G) participation warrants explicit evaluation because the storage device also serves transportation needs and may connect at different approved premises. Those characteristics should be addressed without presuming availability or relaxing reliability requirements.

Clarify eligibility in the ADESR definition

Texas EV Alliance recommends adding the following language directly to the introductory ADESR definition so subsequent references include qualifying storage without singling out a particular technology:

An ADESR may include energy storage devices regardless of technology, physical configuration, or primary end use, including devices that are not continuously connected, provided that the devices and associated interconnection and control equipment meet the applicable requirements of this Governing Document. Only approved devices connected at approved Premises and available to respond to ERCOT Dispatch Instructions may contribute to the ADESR's available capability.

This clarification would not waive applicable qualification, electrical-location, interconnection, utility-approval, protection, or export-limit requirements. For EV participation, review should address the configured vehicle, compatible bidirectional charging equipment, and associated controls rather than the vehicle in isolation.

1. Use planning data without replacing electrical mapping

Texas EV Alliance recommends exploring whether lawfully available, aggregated or de-identified vehicle-registration information from the Texas Department of Motor Vehicles (TxDMV) can assist participation planning. Any data-sharing arrangement should respect privacy and access restrictions. Registration information may help estimate potential participation; it does not establish where a vehicle is connected, its available capability, or its electrical mapping.

The Distribution Service Provider (DSP), in coordination with the Transmission Service Provider (TSP), should remain responsible for confirming each participating premise's Common Information Model (CIM) Load. Planning data should supplement, not replace, that utility-confirmed mapping or verification of the device's active connection point. [1, Section 2, item 8; Sections 5.c.2 and 5.c.7]

2. Accept validated equipment data without unnecessary duplication

Texas EV Alliance recommends allowing existing measurement and communications capabilities in compatible vehicles, charging equipment, storage systems, or aggregation systems to satisfy applicable requirements when validated. Acceptance should depend on data accuracy, timing, synchronization, device identity, and performance, not on whether the measurement equipment is integrated into the device or installed separately. Compliance should be demonstrated for the proposed equipment configuration, not presumed for all EVs or chargers.

The Qualified Scheduling Entity (QSE) should remain the interface with ERCOT for resource-level telemetry and market submissions. Validated equipment data should not replace required premises-level settlement metering or reduce device-level validation, data-retention, or reporting requirements. [1, Sections 5.d.1–5.d.3 and 5.d.6]

3. Clarify the transformer boundary and residential participation

Section 5.a requires an ADESR's devices to map to the same CIM Load, identified as the substation transformer, with the same Load Serving Entity (LSE) and DSP. Texas EV Alliance recommends expressly distinguishing that upstream substation transformer from the smaller downstream service transformers supplying individual customers. [1, Section 5.a]

Residential premises served through different service transformers should not be excluded solely for that reason when they map to the same substation transformer and meet all other requirements. Conversely, being served by the same substation is not sufficient when premises map to different substation transformers. The pilot should evaluate whether the common-transformer, common-LSE, and minimum-size requirements create practical residential-enrollment barriers. Any broader aggregation arrangement should be evaluated separately for reliability and accurate locational dispatch.

4. Reconcile voltage and frequency ride-through requirements

Voltage and frequency ride-through concerns equipment response to specified temporary grid disturbances, not the duration of stored energy. Section 5.b.3 would apply DSP-specified ride-through requirements to ADESR devices instead of the Nodal Operating Guide requirements otherwise applicable to a Distributed Energy Storage Resource. Section 5.c.2 also contains an equipment attestation referencing ERCOT ride-through provisions. Their interaction needs clarification. [1, Sections 5.b.3 and 5.c.2]

Texas EV Alliance recommends that ERCOT reconcile these provisions, identify the requirements applicable to each approved equipment configuration, and align related attestations and forms. This request seeks consistent safety requirements and review expectations, not an exemption from equipment protection or DSP approval.

5. Establish a workable process for movement between approved locations

Texas EV Alliance recommends distinguishing changes in the approved participant population from routine changes in the availability of already-approved devices. The current ADESR population-update process requires DSP review and ERCOT validation before added premises or devices may participate. Applying that entire process to every recurring connection or disconnection would create a practical barrier for mobile storage. [1, Section 5.c.7]

Implementation guidance should provide an approved process for recurring movement between qualified connection points, including a vehicle moving between home and work. Before the device contributes at the receiving location, its equipment configuration, premises, and required registrations must be approved; its actual electrical location must be verified; and its contribution to the prior aggregation must end. No capacity or energy may be double counted across aggregations.

Each receiving aggregation must independently satisfy the applicable CIM Load, LSE, and DSP requirements. New devices, premises, connection points, or material changes in capability or equipment should remain subject to the required review. Routine availability changes within an approved operating arrangement should not, by themselves, require a new interconnection study or population approval.

6. Report available capability and clarify update deadlines

Texas EV Alliance recommends distinguishing the proposed 1 megawatt (MW) aggregate nameplate threshold from the capability actually connected and available. Temporary reductions in availability, including below 1 MW or to zero, should not alone terminate qualification when approved registered capability remains sufficient and the QSE accurately reports availability. This would not waive qualification testing or performance obligations for capability offered or dispatched.

For each operating hour, the QSE should report charging and discharging limits consistent with expected connections, customer reserves, and equipment and site limits. Real-time capability must reflect connected, approved devices; disconnected devices contribute no available dispatch capacity. State of charge and deliverable duration must reflect actual operating conditions, not registered nameplate totals. [1, Sections 5.a, 5.c.7, 5.d and 5.f.3]

The draft's two-second resource-level telemetry requirement is not a complete notification schedule for every change in duration or availability. Texas EV Alliance recommends that ERCOT specify the required information, submission channel, and deadline for forecast changes, unexpected disconnections, changes in usable energy or delivery duration, and permanent registration changes. Guidance should also define the safe response to lost communications or unverified capability. [1, Section 5.d.2]

7. Distinguish scheduled departures from aggregate nonperformance

Texas EV Alliance recommends clarifying that a scheduled disconnection does not, by itself, constitute nonperformance when its effect is reflected timely and accurately in applicable operating plans, telemetry, and market submissions, and the aggregation continues to satisfy its dispatch and other obligations.

An expected departure should not retroactively excuse a dispatch shortfall or relieve the QSE of an existing commitment. The aggregation must manage device-level changes while continuing to meet the performance requirements applicable to the capability it offers and is dispatched to provide. [1, Sections 5.f.3 and 5.g; see proposed Section 5.f.4 in the redline]

8. Evaluate EV use cases within the technology-neutral framework

Texas EV Alliance recommends that Phase 4 evaluation and reporting address storage with variable connection schedules and movement between approved premises. Qualifying bidirectional EV systems should be an explicit use case within that broader evaluation, including residential, fleet, and depot configurations and recurring movement between approved locations.

Reports should distinguish registered capability from connected availability and document dispatch performance, electrical mapping, telemetry quality, customer operating constraints, participation costs, and barriers to enrollment. Findings should identify practical changes needed for a durable market pathway. Future ancillary-service eligibility or settlement changes should be evaluated separately; these recommendations do not assume those changes are authorized by the proposed ADESR option. [1, Sections 5.b.3, 5.i and 5.k]

Protect owners and support practical implementation

Participation should remain voluntary and based on clear owner consent. Program terms should explain compensation, battery use, and withdrawal procedures and permit owners to establish minimum state of charge, departure needs, and backup reserves. Aggregators should translate those limits into the capability offered before accepting dispatch obligations. These customer arrangements should not alter ERCOT's wholesale settlement provisions.

The Alliance would welcome a technical working session with ERCOT, DSPs, QSEs, and prospective participants to map the process from equipment approval and connection through availability reporting, dispatch, disconnection, and settlement. We recommend incorporating the clarifications above into the governing document and implementation guidance so qualified resources can participate without unnecessary administrative barriers or weakened reliability safeguards.

Respectfully submitted,
Mario Bravo
Executive Director
Texas EV Alliance
mario.bravo@txev.org

Source documents and proposed revisions

[1] ERCOT, Aggregate Distributed Energy Resource Pilot Project Governing Document, Phase 4, clean draft dated October 12, 2026. Section references above identify provisions addressed by these proposed comments.

ERCOT meeting page - October 19, 2026

ERCOT clean Phase 4 draft - October 12, 2026

ERCOT Phase 4 redline - October 12, 2026

The following governing-document copy contains Texas EV Alliance's proposed revisions in Word tracked changes, aligned with these comments. ERCOT's own Phase 4 redline, linked above, is a separate source comparison. The Alliance amendments are proposed changes to the October 12 draft; the ride-through provisions are flagged for clarification rather than substantively changed.

2705 West Lake Drive

Taylor, Texas 76574

(512) 248-6800

ercot.com

#### Aggregate Distributed Energy Resource

#### Pilot Project Governing Document

Phase 4

Proposed for consideration at the December 7, 2026 meeting of the ERCOT Board of Directors [PLACEHOLDER: update after final Board action.]

Texas EV Alliance proposed amendments | October 26, 2026

# Table of Contents

1.	Introduction	3

2.	Purpose of the Pilot Project Phase 4	5

3.	Phase 4 Pilot Project Timeline and Duration	6

4.	Policy Questions to be Considered in Phase 4	7

5.	Phase 4 of the Multi-phase Pilot Project	7

a.	Basic Program Parameters	7

b.	Exceptions to ERCOT Rules	10

c.	Eligibility and Qualification	13

d.	Metering, Telemetry, and Market Submissions	23

e.	Additional Data from the QSE Representing the ADER	32

f.	Procurement and Deployment	32

g.	Performance Evaluation and Compliance Metrics	33

h.	Settlement and Cost Allocation	33

i.	Evaluation and Analysis of Different ADER Participation Models for Phase 4	33

j.	Program Costs	34

k.	Reports	35

l.	Construction	35

Appendix A	36

Appendix B	37

Appendix C	38

# Introduction

On October 18, 2022, as authorized by 16 Texas Administrative Code (TAC) § 25.361(k), and as directed by the Public Utility Commission of Texas (PUCT), the ERCOT Board of Directors (Board) established a pilot project to evaluate the participation of Aggregate Distributed Energy Resources (ADERs) in the ERCOT wholesale market (Pilot Project). An ADER is a Resource consisting of multiple Premises or devices connected at the distribution system level that has the ability in aggregate to respond to ERCOT Dispatch Instructions. As described by the Commissioner Memorandum filed on July 13, 2022, in Project No. 51603, the Pilot Project is intended to answer, “questions related to how ADERs can support reliability, enhance the wholesale market, incentivize investment, potentially reduce transmission and distribution investments, and support better load management during emergencies.” The “Phase 1” Governing Document laid out the framework for the first phase of the Pilot Project and envisioned a multi-phase Pilot Project in which future revisions to this Governing Document would establish the details for the additional phases, with lessons learned from the early phases considered when designing additional phases for the Pilot Project. These additional phases would be intended to create opportunity to expand overall participation while maintaining the reliable operation of the transmission and distribution grid. Commission updates regarding the Pilot Project have been filed in Project No. 53911.

At the February 13, 2025 PUCT Open Meeting, the Commissioners approved a PUCT Staff recommendation for the Commission to dissolve the ADER Task Force at the Commission and officially transfer the ADER pilot program over to the ERCOT stakeholder process under the Technical Advisory Committee (TAC). The Pilot Project was transferred and first discussed by the ERCOT Technical Advisory Committee (TAC) members at its February 27, 2025 meeting.

The table below summarizes how the Pilot Project has progressed through each phase, and the participation limits in effect during that phase.

| Phase | Description of Changes | Participation Limits |
| --- | --- | --- |
| Phase 1 Approved October 18, 2022 Participation began August 22, 2023 | Established the Pilot Project. ADERs register and participate as Aggregate Load Resources modeled as Controllable Load Resources; eligible for energy and Ancillary Services (Non-Spin) in SCED. System-wide and QSE limits (20%) established. | 80 MW energy 40 MW Non-Spin ECRS not available |
| Phase 2 Approved February 27, 2024 | Added ECRS eligibility and refined the telemetry validation requirements to account for very small injections and withdrawals of energy. Followed the Phase 1 Report filed with the Commission on February 27, 2024. | 80 MW energy 40 MW Non-Spin 40 MW ECRS |
| Phase 3.1 Approved June 23, 2025 | Added the non-Controllable Load Resource (NCLR) participation option for aggregations that cannot incrementally follow SCED Set Points. Clarified the DOTA review process and the interaction with ERS and TDU Load Management programs, and updated Premise-level validation. Followed the Phase 2 Report filed with the Commission on June 20, 2025. | 160 MW energy 80 MW Non-Spin 80 MW ECRS |
| Phase 3.2 Approved February 27, 2026 | Increased the system-wide participation limits and the limit applicable to a single QSE (to 90%), at ERCOT's discretion and in consultation with TAC. | 500 MW energy 100 MW Non-Spin 100 MW ECRS |
| Phase 3.3 Approved June 2, 2026 | Removed the requirement that the response capability of all ADERs assigned to a single CIM Load be capped at 100% of the CIM Load rating, and reflected the practice of posting participation numbers on the ERCOT website. | Unchanged |
| NEW: Phase 4 Approved ___, 2026 | Adds the Aggregate Distributed Energy Storage Resource (ADESR) participation option, dispatched through SCED using nodal shift factors. | ALRs and NCLRs: limits unchanged ADESRs: not subject to the system/QSE participation limits, but remain subject to DSP approval. Not currently eligible to provide Ancillary Services. |

The ADER Pilot has grown rapidly, driven in significant part by residential battery installations. The existing ALR participation option has been successful insofar as it has demonstrated the ability of aggregate resources to be dispatched in SCED and provide Ancillary Services.  The existing frameworks do have some limitations.  For instance, these Resources are modelled using Load Zone shift factors and the ALR framework does not provide ERCOT with the State of Charge visibility or the representation of charging and discharging capability of the aggregate Resource.

ERCOT and stakeholders have identified a new opportunity within the Pilot to:

- Improve modelling of Resources by exploring a new participation option; and

- Explore and evaluate the impact of nodal dispatch for aggregated distribution-connected energy storage.  This effectively would expand the ability of ADERs beyond the provision of energy and Ancillary Services to evaluate whether ADERs can meaningfully help manage transmission congestion.

The Phase 4 Governing Document revises the Phase 3 Governing Document to add the ADESR as an additional participation option:

- An ADESR is an aggregation of distribution-connected energy storage that is registered, modeled, and dispatched substantially in the same manner as a Distributed Energy Storage Resource (DESR), including dispatch through Security-Constrained Economic Dispatch (SCED) using nodal shift factors.  ERCOT has proposed some targeted exceptions for ADESRs described in this Governing Document. An ADESR may include energy storage devices regardless of technology, physical configuration, or primary end use, including devices that are not continuously connected, provided that the devices and associated interconnection and control equipment meet the applicable requirements of this Governing Document. Only approved devices connected at approved Premises and available to respond to ERCOT Dispatch Instructions may contribute to the ADESR's available capability. This inclusion does not waive applicable qualification requirements, the common CIM Load, LSE, and DSP requirements, DSP approval, studies, interconnection requirements, protection settings, or export limits.

- Since an ADESR would be dispatched based on its nodal shift factor, this approach will provide a better way to study the effects on transmission congestion while continuing the Pilot Project's learning-by-doing approach; it will minimize near-term changes to ERCOT systems and will not require changes to DSP systems.

- The ADESR option is additive to the existing ALR and NCLR participation options and does not create a new Resource type in the ERCOT Protocols.

ERCOT is not proposing that any system-wide and/or QSE limits would be applicable to ADESRs; however, the requisite study, approvals, and individual, localized, or newly established participation limits where necessary from DSPs for any DOTA submissions will continue to apply for any and all ADERs irrespective of participation type.

# Purpose of the Pilot Project Phase 4

Phase 4 of the Pilot Project is intended to continue the work from the prior phases and make additional improvements and account for lessons learned from Phases 1 through 3. The purpose of this phase of the Pilot Project is to:

- Assess the operational benefits and challenges of heterogeneous Distributed Energy Resource (DER) aggregations that are net generation or net load and address those challenges to allow meaningful use of DER aggregation.

- Understand the impact of having Ancillary Services and energy delivered by ADERs and assess how ADERs can best be used to support reliability.

- Assess challenges to incentivizing competition and attract broad DER participation through Load Serving Entities (LSEs), while ensuring adequate customer protections are in place.

- Allow Distribution Service Providers (DSPs), the Commission, and others to study distribution system impacts of ADERs that inject to the grid.

- Evaluate the impacts to transmission system congestion management associated with the dispatch and Settlement of ADERs that participate as ALRs or NCLRs at a zonal level.

- Evaluate the dispatch of ADESRs at a nodal level using nodal shift factors, including an evaluation of the effects on transmission congestion. Zonal Settlement will be retained during Phase 4.

- Develop and evaluate options of metering approaches and nodal Settlement processes for ADESR while ensuring customers are protected.

- The DSPs, in coordination with ERCOT, will evaluate how routine changes to distribution system connectivity that are implicit in the operation of the distribution system impact the capability and “mapping” of ADESRs.  If necessary, ERCOT will investigate how the capability of the ADESRs can be represented considering the changes in distribution system connectivity that routinely occur.  Any recommendations addressing this issue will not create a safety or reliability risk to DSP operations.  ERCOT and participating DSPs may evaluate lawfully available, aggregated or de-identified ownership or registration information to support participation planning, subject to applicable privacy and access restrictions. Such planning information shall not substitute for DSP- and TSP-confirmed electrical mapping, verification of the active connection point, or measurement of available capability.

- Identify potential Pilot Project enhancements; study the need for and benefit of transitioning distribution-level aggregations to different levels of more granular dispatch and Settlement; and evaluate more complex use-cases and business models.

Phase 4 expands the participation options established in prior phases by adding the ADESR participation option for aggregations of distribution-connected energy storage.  Phases 1 through 3,provided a means for Premises with any combination of generation, energy storage technologies, or controllable load with the capability of 1 MW or less to participate in the ERCOT wholesale markets. This Pilot Project is not intended to investigate or propose changes to existing participation models, such as those for Distributed Generation Resources (DGRs), Distributed Energy Storage Resources (DESRs), Aggregate Load Resources (ALRs), or Settlement Only Distribution Generators (SODGs) greater than 1 MW. For the first two phases of the Pilot Project, which were designed to make use of the ALR participation model, aggregations of multiple Premises that included only Load were not able to participate as there is already a pathway for their participation in the Protocols if the aggregation is “controllable.” However, that changed with Phase 3, under which an ADER became able to participate in the market similar to a non-Controllable Load Resource (NCLR).

Phase 4 introduces the ADESR participation option for aggregations of distribution-connected energy storage.  The ADESR will participate in a manner substantially equivalent to a DESR. An ADESR is sized at the aggregate Resource level, with a minimum aggregate capability of 1 MW.  System-wide capacity and QSE limits will not be applied to ADERs participating at ADESRs; however, a DSP may establish its own location-based participation limits and all proposed aggregations (in the form of DOTA submissions) will continue to need to be reviewed, studied and approved by the DSPs before being submitted to ERCOT.

# Phase 4 Pilot Project Timeline and Duration

The Pilot Project will continue under Phase 4 until implementation of ERCOT market rules and systems are in place to accommodate participation by ADERs, considering any direction from the PUCT, or until ERCOT, following PUCT consultation, or the PUCT deems the Pilot Project unnecessary. ERCOT expects that the Pilot Project will need to continue for a minimum of one additional year from the formal adoption of the Phase 4 Governing Document, including any future phases, to allow for any incorporation of ERCOT system upgrades, testing of customer migration, and qualifying Resources for multiple ERCOT services, as determined to be allowable while maintaining grid reliability.

This Phase 4 Governing Document provides the necessary details for a fourth phase of the Pilot Project to continue the implementation of an ADER program with minimal changes to ERCOT and DSP systems.  Potential future phases may introduce additional design elements to help expand participation opportunities while still maintaining distribution and transmission grid reliability.

Phase 4 adds the ADESR participation option, enabling nodal dispatch of aggregated distribution-connected energy storage as described in this Governing Document. Phase 4 of the Pilot Project is planned to proceed according to the following timeline:

- Following a period of at least six months after ERCOT Board approval of Phase 4, ERCOT shall prepare a recommendation on whether Phase 4 should continue in order to gain more data.  This recommendation will be based on regular stakeholder discussions, which shall take place at the Wholesale Market Subcommittee.

- ERCOT will continue to update the PUCT every six months on the status of the Pilot Project.

# Policy Questions to be Considered in Phase 4

During Phase 4, ERCOT  may consider the following issues:

- Device-level sub-meter data, power quality metering, or methods for independent certification of QSE-provided data: This Pilot Project will need to evaluate the need for and methods for collecting data from individual Premises or devices that can be used to validate ADER performance and compliance of ADERs, including for the provision of additional Ancillary Services. This may include requiring data recorders located on individual DERs and on the distribution system in the future. If that is needed, ERCOT will need to evaluate who installs/owns these data recorders and the accuracy of data provided for performance and compliance.

- Provision of additional Ancillary Services: During Phase 4 of the Pilot Project, ERCOT will continue to study the provision of ECRS by ADERs and will continue to work with the PUCT and stakeholders regarding the provision of additional Ancillary Services by Resources connected to the distribution system. The approach taken for ADERs will be linked to broader discussions on this topic as it relates to all distribution-connected Resources.

- ADER modeling with alternative dispatch and pricing schemes: As part of this Pilot Project, ERCOT will evaluate a Logical Resource Node (LRN) concept and other alternative dispatch and pricing schemes. Specific to the LRN concept, implementation of this model approach will require the Settlement Meter location for each Premise to be identical to the Premise’s telemetry location. If a Premise has only one Settlement Meter, then the telemetry location will be required to correspond to the Settlement Meter location. This implies that all native load behind the Settlement Meter will be settled at an LRN price. Among other issues, this scheme will require consideration of the consistency with 16 TAC § 25.501(h), which requires load to be settled at a zonal price. While this issue may be resolved by both placing a Settlement Meter that measures only the ADER dispatchable component at the Premise and having the telemetry correspond to the dispatchable (device-level) component at the Premise, this will also raise the question of who would be responsible for installing, maintaining, and reading this separate Settlement Meter.

- Alternative telemetry requirements for QSEs may be considered.

- Potential rule or rule changes regarding interoperability standards and their application to devices participating in the ADER Pilot Project.

- Potential future nodal Settlement for ADESRs: ERCOT may develop a concept paper on the challenges and possible approaches to implementing nodal Settlement for ADESRs, informed by discussions with DSPs and Market Participants that may install ADESRs. ERCOT may also conduct a proof of concept with one or more DSPs and Market Participants to test metering and data gathering options.

# Phase 4 of the Multi-phase Pilot Project

# Basic Program Parameters

The fourth phase of the Pilot Project design will continue to build on Phases 1–3 and, as with prior phases, aims to minimize ERCOT and DSP required system changes and expedite an expanded Pilot Project. ERCOT expects to use lessons learned from this phase to evaluate possible further phases for the Pilot Project that could expand overall participation while ensuring the reliable operation of the electric grid. During the fourth phase of the Pilot Project:

- A registered ADER (not participating as a ADESR) must always be seen as an ALR or NCLR in aggregate as a net consumer of energy by ERCOT, in terms of telemetry and other market submissions to ERCOT. However, it will be acceptable if individual Premises that are components of the aggregation are net injectors of energy and an ADER may provide a net injection on an aggregated basis.  This net-Load representation does not apply to an ADER participating as an ADESR.

  - Continuing in Phase 4, an ADER participating as an ALR will be modeled as a Load Resource and is an aggregation of Premises, where all the Premises are located within a single Load Zone and have the same LSE and DSP.

  - An ADER participating as an NCLR will be modeled as a Load Resource and is an aggregation of Premises, where all the Premises are located within a single Load Zone and have the same DSP. For ADERs participating as an NCLR, where the individual Premises associated with the aggregation have electric consumption exceeding 100kW, those Premises are not required to have the same LSE provided that ERCOT has received “LSE’s QSE Acknowledgment for NCLR-Type Participation” forms (hereinafter, “LSE Acknowledgment”) (See Appendix A) for the QSEs of all the active LSEs associated with the Premises in that aggregation. Also, ADERs participating as an NCLR may be an aggregation of load-only Premises.

  - An ADER participating as an ADESR is an aggregation of distribution-connected energy storage devices that map to the same CIM Load (substation transformer).  ADESRs will be modeled in substantially the same manner as a DESR. All of the Premises within an ADESR must be served by the same substation transformer and have the same LSE and DSP. The ADESR is assigned a Resource Node and is dispatched by ERCOT through SCED using nodal shift factors. Where a Resource Node does not already exist at the applicable electrical bus, the Resource Node created for the ADESR will be non-biddable in the DAM and CRR markets; where a Resource Node already exists, the ADESR will be mapped to that existing Resource Node. Multiple Resources may be mapped to the same Resource Node.  For an ADER participating as an ALR or NCLR, each Premise within the ADER may be net load or net generation. The aggregation must have the capability to provide at least 100 kW of response (Demand response capability plus injection capability), and each Premise must provide 1 MW or less of response (Demand response capability plus injection capability). Premises or aggregations that are otherwise able to participate in the ERCOT market (e.g., as a DGR, DESR, SODG larger than 1 MW, or ALR) should not be included as part of an ALR- or NCLR-type ADER. The ADER’s performance should always be represented as a net Load for purposes of telemetry and other market submissions to ERCOT.

For the ADESR requirements, the substation transformer is the transformer associated with the applicable CIM Load, not a downstream customer-service transformer. Premises supplied through different customer-service transformers may participate in the same ADESR if the DSP, in coordination with the TSP, confirms that they map to the same CIM Load and all other requirements are satisfied. Premises served by the same substation but mapped to different substation transformers shall not be combined in one ADESR.

  - For an ADER participating as an ADESR, the nameplate capacity must have a minimum aggregate injection capability of 1 MW, with no cap on aggregate injection capability imposed by this Governing Document, unless such a cap (individual or aggregate) has been established by the DSP or TSP. An aggregation with an injection capability of 10 MW or greater may be subject to the applicable large generator interconnection process.

  - For an ADESR, the minimum aggregate nameplate injection capability of 1 MW is a registration and qualification threshold, not a requirement that at least 1 MW remain connected and available at all times. The qualifying capability shall reflect the registered devices' simultaneous injection capability, limited by the associated power-conversion equipment and approved site export limits. Temporary reductions in connected availability below 1 MW, including to zero, shall not alone terminate qualification, provided the approved registered capability continues to meet the threshold and the QSE accurately reports available capability. Disconnected or otherwise unavailable devices shall contribute no available dispatch capability. This provision does not waive qualification testing or performance obligations for capability offered or dispatched.

  - Continuing in Phase 4 of the Pilot Project, the total registered MW capacity of ADERs participating as ALRs or NCLRs must be no greater than 500 MW system wide. ADERs participating as ALRs or NCLRs will be limited to providing no more than 100 MW of Non-Spinning Reserve (Non-Spin) system-wide and no more than 100 MW of ERCOT Contingency Reserve Service (ECRS) system-wide. As part of the DOTA provided to ERCOT, the QSE shall indicate the anticipated MW capacity that is intended to be registered as well as an amount of Non-Spin and ECRS for which the QSE is intending to qualify the ADER. These ADER MW quantities will be evaluated against these ERCOT Pilot Project participation limits. Additionally, no QSE will be allowed to register more than 90% of these system-wide limits.

  - , There are no ERCOT-level participation limits for ADERs participating as ADESRs.  The above registration requirements and limitations concerning the Pilot Program’s energy, Non-Spin and ECRS limits therefore do not apply to ADESRs. There may be TSP or DSP existing or newly established location-based limits, either individual or in the aggregate.

- The ADER Pilot Project participation limits, which apply only to ADERs participating as ALRs or NCLRs, will be enforced as part of ERCOT’s review of a QSE’s submission for participation.  Updates showing remaining availability under the participation limits are posted on the ADER Pilot Projects page of the ERCOT website.

- When participation by ADERs participating as ALRS or NCLRs exceeds 80% of the limits described above, including the limit on a QSE’s ability to register more than 90% of the system-wide cap, ERCOT shall review any reliability concerns with potential increases in the ERCOT Pilot Project participation limits. ERCOT may increase any of the imposed participation limits, at its sole discretion and in consultation with TAC, after evaluating performance during the Pilot Project. If ADER participation is approaching either the system-wide limits or QSE limits in the Governing Document, ERCOT will exercise its discretion to make incremental upward adjustments to either or both of these limits to continue to support growth in participation while managing administrative burden ahead of transitioning the pilot to ERCOT Nodal Protocols. Such increases will not be considered amendments to this Governing Document and therefore will not require approval by the ERCOT Board. ADESR participation is excluded from these calculations.

- The above program parameters are not exhaustive.  There may be other limitations on ADERs established by ERCOT and/or DSPs due to reliability concerns that will also be evaluated and addressed as the ADER details are submitted to DSPs for their acknowledgement.  TSPs and DSPs may establish limits and restrictions on individual or aggregate participants as they deem necessary to maintain reliable and safe operation of their systems.

The table below summarizes the three participation options available under Phase 4.

| Parameter | ALR | NCLR | ADESR |
| --- | --- | --- | --- |
| Underlying Resource model | Controllable Load Resource | Non-Controllable Load Resource | Distributed Energy Storage Resource |
| What is aggregated | Devices at Premises | Devices at Premises | Distribution-connected energy storage devices at Premises |
| Energy dispatch | SCED Set Points using Load Zone shift factors | Not dispatched by SCED | SCED Set Points using nodal shift factors |
| Settlement | Load Zone price | Load Zone price | Load Zone price |
| Ancillary Services | Non-Spin and ECRS if qualified | Non-Spin and ECRS if qualified | Not eligible |
| Participation limits | DSP, system-wide and QSE | DSP, system-wide and QSE | DSP |
| Single-QSE limit | 90% of the system-wide limits | 90% of the system-wide limits | Not applicable |
| Minimum aggregation size | 100 kW of response | 100 kW of response | 1 MW aggregate injection capability |
| Size of each participating unit | Each Premise provides 1 MW or less of response | Each Premise provides 1 MW or less of response | No prescribed limit; injection capability of 10 MW or greater may be subject to the applicable large generator interconnection process |
| Telemetry basis | Device-level or Premise-level, or a combination | Device-level or Premise-level, or a combination | Device-level, aggregated to the Resource |
| Resource meter | TDSP Settlement meter at each Premise | TDSP Settlement meter at each Premise | TDSP Settlement meter at each Premise |
| Net-Load representation | Must always appear as a net consumer; MW offset may be used | Must always appear as a net consumer; MW offset may be used | Represented as a Resource; no MW offset |
| Resource Node | Not applicable | Not applicable | Assigned a Resource Node, non-biddable in DAM and CRR where newly created |
| Participation Requirements/Eligibility | All Premises must be within a single load zone and have the same LSE and DSP. ADER QSE must also be the same entity that represents the LSE. | All Premises must be withing a single load zone and have the same LSE and DSP. ADER QSE must also be the same entity that represents the LSE. Third Party QSE may represent loads greater than 100 KW with written consent from LSE | All Premises must be fed by the same substation transformer and have the same LSE and DSP. ADER QSE must also be the same entity that represents the LSE. |
| Performance evaluation | ALR performance processes | NCLR performance processes | DESR performance processes |

# Exceptions to ERCOT Rules

During the fourth phase of this Pilot Project, ADERs will have the option to participate as ALRs,  NCLRs, or ADESRs and will be treated as ALRs, NCLRs, or DESRs respectively for all purposes under the ERCOT Protocols, Operating Guides, or any Other Binding Document,, except as otherwise described in this Governing Document.

- ADERs opting to register as an ALR must participate as ALRs in accordance with all Protocol, Operating Guide and/or Other Binding Document requirements applicable to non-ADER ALRs, except with respect to the following Pilot Project-specific requirements, which shall apply in addition to or in lieu of any corresponding requirements in the Protocols, Operating Guides and/or Other Binding Documents as set forth below:

  - An ADER may have Premises that can inject energy into the distribution system, and an ADER may provide a net injection on an aggregated basis. A net injection from an ADER in response to an ERCOT Dispatch Instruction will be considered Demand response under the Protocols and other ERCOT rules. Any Premise with the potential to export energy beyond its Premise meter must have the correct load profile ID set, for meters in service territories where that is applicable, such that both the import and export channels of its Premise meter are provided to ERCOT.

  - ADER withdrawal telemetry values must represent the sum of the consumption and export of each of the member Premises or devices plus any necessary MW offsets, as described in this Governing Document. Maximum Power Consumption and Low Power Consumption values must be modified to accommodate ADERs, as further provided in this Governing Document. An ADER using device-level telemetry must comply with the validation process for device-level telemetry provided in this document instead of existing validation rules.

  - An ADER is not permitted to present statistical sampling for performance evaluation.

  - The Resource Entity and QSE for the ADER are jointly responsible for maintaining ADER population information, as further described in subsections 5.c.4 and 5.c.5.

  - ADERs will have Pilot Project-specific modeling and ERCOT Pilot Project participation limits.

  - ERCOT will not use baseline evaluation for either qualification or performance validation purposes during the Pilot Project. Qualification and performance validation specific to the Pilot Project is described in subsection 5.c.8.

  - Scheduled Power Consumption (SPC) +2 information will not be required to be provided for an ADER, as it is for an ALR.

  - The telemetry validation procedures and metrics for ADERs are distinct from those for ALRs and are described in subsection 5.d.

  - For Phase 4 of the Pilot Project, ADERs are allowed to, but will not be required to, provide Primary Frequency Response (PFR), as is required for ALRs. To encourage ADERs to provide frequency response, ERCOT will consider opportunities for ADERs with that capability to provide Responsive Reserve (RRS), subject to a system-wide cap. The system-wide cap will be sufficiently high to allow ERCOT to assess the adequacy of ADERs to provide frequency response from the distribution system without posing a threat to the reliability of the system. This opportunity is designed to create a path to a frequency response provision from all ADERs should the current exception, which is specific to Phases 1 through 4, not be granted in the future. To foster an inclusive Pilot Project, ERCOT may develop different alternative participation models in the future that will not require frequency response capability, such as a participation model in which the aggregation may provide some Ancillary Services but is not dispatchable by Security-Constrained Economic Dispatch (SCED). ERCOT may also consider ADERs providing PFR without the ability to be SCED-dispatchable. Similarly, ADERs participating as NCLRs that are capable of interrupting consumption for a frequency event (like traditional NCLRs) may be considered as part of the ADER pilot.

- ADERs opting to register as an NCLR must participate as NCLRs in accordance with all Protocol, Operating Guide and/or Other Binding Document requirements applicable to non-ADER NCLRs, except with respect to the following Pilot Project-specific requirements, which shall apply in addition to or in lieu of any corresponding requirements in the Protocols, Operating Guides and/or Other Binding Documents as set forth below:

- An ADER may have Premises that can inject energy into the distribution system, and an ADER may provide a net injection on an aggregated basis. A net injection from an ADER in response to an ERCOT Dispatch Instruction will be considered Demand Response under the Protocols and other ERCOT rules. Any Premise with the potential to export energy beyond its Premise meter must have the correct load profile ID set, for meters in service territories where that is applicable, such that both the import and export channels of its Premise meter are provided to ERCOT.

- ADER withdrawal telemetry values must represent the sum of the consumption and export of each of the member Premises or devices plus any necessary MW offsets, as described in this Governing Document. Maximum Power Consumption and Low Power Consumption values must be modified to accommodate ADERs, as further provided in this Governing Document. An ADER using device-level telemetry must comply with the validation process for device-level telemetry provided in this document instead of existing validation rules.

- An ADER is not permitted to present statistical sampling for performance evaluation.

- The Resource Entity and QSE for the ADER are jointly responsible for maintaining ADER population information, as further described in subsections 5.c.4 and 5.c.5. This baseline involves meter readings prior to deployment and similar readings during the sustained response period for performance measurement. Qualification and performance validation specific to the Pilot Project is described in subsection 5.c.8.

- The telemetry validation procedures and metrics for ADERs are distinct from other Resources participating in the ERCOT Ancillary Service markets and are described in subsection 5.d.

- An ADER acting as an NCLR to provide RRS must be capable of capturing and storing load data and frequency data for dispatchable events in a manner acceptable to ERCOT and allows for performance verification comparable to that of traditional NCLRs providing RRS, should that type of participation be allowed in Phase 4.

- ADERs opting to register as an ADESR must participate as DESRs in accordance with all Protocol, Operating Guide and/or Other Binding Document requirements applicable to DESRs, except with respect to the following Pilot Project-specific requirements, which shall apply in addition to or in lieu of any corresponding requirements in the Protocols, Operating Guides and/or Other Binding Documents as set forth below:

- Where a Resource Node is created for the ADESR (i.e., there is no existing Resource Node at the applicable electrical bus), the Resource Node associated with an ADESR will be  non-biddable in the DAM and CRR markets. ERCOT will not create a biddable Resource Node mapped only to an ADESR.

- An ADESR does not have a single physical meter at a Point of Interconnection; instead, device-level metered data is aggregated to represent the Resource, as described in subsection 5.d.

- An ADESR is settled at the applicable Load Zone price, as described in the Settlement and Cost Allocation section.

- An ADESR is not currently eligible to provide Ancillary Services.

- An ADESR will be identified as an aggregation at the time of registration. Pending any associated RIOO system changes, which may follow a separate release schedule, ERCOT may identify and prioritize ADESR registrations through an interim manual process.  Until the RIOO system changes are implemented there may be a manual process in place to note that a DESR is an ADESR.

- An ADESR is not permitted to present statistical sampling for performance evaluation.

- The DOTA for an ADESR will be submitted using an ADESR-specific form. This form will cover one CIM Load per form.

- ADESRs participating in this Pilot Project are not currently subject to the requirements of Protocols § 3.8.6, Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs).

- ADESRs participating in this Pilot Project are not currently subject to the voltage ride-through and frequency ride-through requirements in Nodal Operating Guide Sections 2.6 and 2.9 that would otherwise apply to a DESR. An ADESR must instead meet the voltage ride-through and frequency ride-through requirements specified by the DSP for the devices participating in the aggregation.

# Eligibility and Qualification

As a condition for participation in Phase 4 of the Pilot Project, a QSE must meet the conditions described in this section. Note that the QSE associated with a proposed ADER must submit the information identified in c.1 (if applicable), c.2, and c.3 below, while the Resource Entity for the proposed ADER must submit the registration and qualification information in c.4 through c.8 below. The information contained in a DOTA form submitted under this Section is Protected Information

- ADERs participating as an NCLR must provide written consent from all LSEs representing the Premises in each aggregation. (See Appendix A) (ADERs participating as ALRs or ADESRs should skip to c.2 below)

  - Where the individual Premises associated with the aggregation have electric consumption exceeding 100 kW and the Premises are associated with one or more LSEs that are not associated with the QSE, the QSE must provide written consent from each of the LSEs’ QSEs (See Appendix A).  Because an individual ADER may be made of customers represented by multiple different LSEs, written consent is required from each of the LSEs’ QSEs.

  - No LSE or LSE’s QSE is required to participate in this Pilot Program.

  - A QSE must provide the following information to the applicable LSE’s QSE that serves each of the Premises that make up the aggregation. The information should be submitted to the LSEs’ QSE on the “Details of the Aggregation” (DOTA) form posted on the ADER Pilot Projects page of the ERCOT website:

    - Premise unique identifier (name/ID);

    - An indication of whether the ADER telemetry contribution from the Premise is at its TDSP-read meter location or device location;

    - ESI ID (or unique meter identifier, if the ADER is in a NOIE territory) of the TDSP-read meter that measures consumed energy from the grid and/or injected energy into the grid at the Premise;

    - LSE associated with ESI ID or unique meter identifier;

    - DUNS+4 of the QSE associated with the LSE; and

    - For each controllable device at a Premise that is part of the ADER:

  - The type of device (battery, rooftop solar, pool pump, synchronous generator, etc.);

  - The rated dispatchable range (kW) of the individual ADER components at this Premise (for example, the rated dispatchable range of the battery may be +/-5kW maximum discharge/charge; or 3kW maximum consumption for a pool pump);

  - For a Premise that has a battery as part of the ADER, maximum rated operating State of Charge (kWh) and the minimum rated operating State of Charge (kWh); and

  - Which, if any, communication standards the devices are certified to meet.

- If an ADER is made up of customers represented by multiple different LSEs, only the portion of the DOTA containing customers of a given LSE should be sent to that LSE. In accordance with the confidentiality requirements set forth in ERCOT Protocols §§ 1.3.1 and 1.3.1.1(1)(r), an LSE should not receive customer information regarding customers they do not represent.

  - Upon receiving the DOTA form containing only a given LSE’s customer information, an LSE’s QSE that has elected to participate in the Pilot Project shall review the DOTA form for feasibility of participation of the Premises in the proposed Resource on the distribution network. If the LSE’s QSE has concerns with all or a portion of the ESI IDs (or, for NOIEs, unique meter identifiers) listed in the DOTA form, the LSE’s QSE will notify the QSE. The LSE’s QSE may, on a non-discriminatory basis, reject all or a portion of the ESI IDs or unique meter identifiers listed in the DOTA.

  - The LSE’s QSE may consent to the participation of the Premises identified in the DOTA form only by executing the “LSE Acknowledgment” included in Appendix A to this Governing Document and available on the ADER Pilot Projects page of the ERCOT website.

  - The LSE’s QSE’s execution of the LSE Acknowledgment shall be taken as the LSE’s QSE’s confirmation that the LSE provides retail electric service to each of the Premises that are the subject of the request.

  - Any Premises for which an LSE has rejected for participation in the ADER should be removed from the DOTA form sent to the DSP in section 5.c.2 below.

  - If any additions or removals have occurred for the aggregation, the QSE will submit  updates to the applicable LSE’s QSE, as further described in subsections 5.c.4 and 5.c.5, which the LSE’s QSE will review in the same manner as above.

- QSEs must provide written consent from DSP (See Appendix B), consistent with the requirements set forth below:

  - No DSP is required to participate in this Pilot Program.

  - To be eligible to participate in the ADER Pilot Project, a QSE must provide the following information to the applicable DSP that serves each of the Premises that make up the aggregation. The information should be submitted to the DSP on the DOTA form posted on the ADER Pilot Projects page of the ERCOT website:

    - Premise unique identifier (name/ID);

    - An indication of whether the ADER telemetry contribution from the Premise is at its TDSP-read meter location or device location;

    - ESI ID (or unique meter identifier, if the ADER is in a NOIE territory) of the TDSP-read meter that measures consumed energy from the grid and/or injected energy into the grid at the Premise;

    - LSE associated with ESI ID or unique meter identifier; and

    - For each controllable device at a Premise that is part of the ADER:

  - The type of device (battery, rooftop solar, pool pump, synchronous generator, etc.);

  - The rated dispatchable range (kW) of the individual ADER components at this Premise (for example, the rated dispatchable range of the battery may be +/-5kW maximum discharge/charge; or 3kW maximum consumption for a pool pump);

  - For a Premise that has a battery as part of the ADER, maximum rated operating State of Charge (kWh) and the minimum rated operating State of Charge (kWh); and

  - Which, if any, communication standards the devices are certified to meet.

    - An attestation provided by the Resource Entity which includes:

    - that any inverter-based device is either certified to UL1741-SB or complies with the requirements of UL1741-SA and that the inverter settings are programmed to ride through frequency and voltage excursions in a manner consistent with requirements for DGRs and DESRs in ERCOT Nodal Operating Guide sections 2.6.2.1(2) and 2.9.2(3); and

    - that any synchronous generator relays are programmed to ride through frequency and voltage excursions in a manner consistent with requirements for DGRs in ERCOT Nodal Operating Guide sections 2.6.2.1(2) and 2.9.2(2).

  - The MW capacity that is intended to be registered with ERCOT as an ADER and the amount of Non-Spin and ECRS which the QSE is intending to qualify the ADER. An ADER may include additional customer Premises or devices as long as the capacity registered and Non-Spin and ECRS qualification amounts remain lower than these values.

  - For ADERs participating as ALRs, the DOTA form should indicate whether or not the ADER is able to provide PFR.

  - For an NCLR, the DOTA form received by the DSP should only contain Premises that the applicable LSE QSE has agreed to include.

  - Upon request by a QSE that is developing ADERs, a participating DSP must provide any relevant non-confidential information to support the commencement of the enrollment process for the Pilot Project and the addition of new metered Premises on an ongoing basis for the duration of the Pilot Project.

  - Upon receiving the DOTA form, a DSP that has elected to participate in the Pilot Project shall review the DOTA for feasibility of participation of the Premises in the proposed Resource on the distribution network. If the DSP has concerns with all or a portion of the ESI IDs (or, for NOIEs, unique meter identifiers) listed in the DOTA, the DSP will notify the QSE. The DSP may, on a non-discriminatory basis, for reasons of safety, reliability, or regulatory impediments, reject all or a portion of the ESI IDs or unique meter identifiers listed in the DOTA. If the DSP chooses to reject all or a portion of the ESI IDs or unique meter identifiers listed in the DOTA, the DSP shall notify the QSE managing that ADER and provide the QSE the reason for the rejection.

  - As part of its review of an ADER, the DSP, in conjunction with the TSP, shall map each of the Premises that make up the ADER to their respective Common Information Model (CIM) Loads and add this information to the DOTA form as part of the DSP’s response to the submission.

  - The DSP must also verify whether any of the ESI IDs are already participating in a TDSP Load Management Program.

  - DSPs must respond to QSE DOTA submissions within 45 days of receipt.  If the DSP determines that additional time is needed to evaluate the ADER, and/or that DSP studies will need to be performed, the DSP will notify the QSE as soon as reasonably practicable.

  - The DSP may consent to the participation of the Premises identified in the DOTA form only by executing the “Distribution Service Provider Acknowledgment” (DSP Acknowledgment) included in Appendix B to this Governing Document and available on the ADER Pilot Projects page of the ERCOT website.

  - The DSP’s execution of the DSP Acknowledgment shall be taken as the DSP’s confirmation that the DSP provides delivery service to each of the Premises that are the subject of the request.

  - If any Premises or devices are proposed to be added to or removed from an aggregation, the QSE must submit an updated DOTA, together with any required accompanying attestations, to ERCOT and the DSP documenting those changes. Such updates are submitted, as further described in subsections 5.c.5, 5.c.6, and 5.c.7, which the DSP will review in the same manner as above. Routine connection or disconnection within the approved registered population of an ADESR is treated as provided in subsection 5.c.7.

  - If ERCOT is processing an approved DOTA form that requires registration and modeling updates, the QSE cannot submit another DOTA update for the same ADER until the pending changes have been added to the RIOO database and the network model. If the QSE does submit an updated DOTA before the pending changes are complete, neither the DSP nor ERCOT will evaluate that update.

- QSEs must execute a supplement to the Standard Form Market Participant Agreement for Pilot Project participation (See Appendix C), consistent with the requirements set forth below:

- In addition to obtaining the DSP’s consent, the QSE representing a proposed ADER must execute a supplement to its Standard Form Market Participant Agreement and submit it to ERCOT for counter-signature. The “Supplement to the Standard Form Market Participant Agreement” (QSE Supplement) is included in Appendix C to this document and is available on the ADER Pilot Projects page of the ERCOT website.

- QSEs must submit all required documentation to ERCOT, and ERCOT will review such documentation, as follows:

- The DSP Acknowledgment, QSE Supplement, DOTA form, and the LSE Acknowledgment (if applicable), as described above, shall be submitted as a package to ERCOT via e-mail to pilotprojects@ercot.com.  That e-mail submission must copy the applicable DSP and Resource Entity. QSEs may request that a secure email account be created with ERCOT if using standard email is of concern.  ERCOT will review the documents after it receives them.

- ERCOT may reject the submission for the following reasons:

  - Accepting the submission would cause the program to exceed any ERCOT Pilot Project participation limits, as defined in subsection 5.a;

  - ESI IDs or unique meter identifiers included in the submission (evaluated at the time of submission):

    - Are already part of an accepted submission from a different QSE;

    - Are not associated with the submitting LSE (not applicable to ADERs intending to participate as NCLRs, provided the individual premise associated with the participating ESIID has electricity consumption that is greater than 100 kW);

    - Have a status of not active in the ERCOT database;

    - Do not have an interval data recorder meter type;

    - Are not in the ERCOT region;

    - Are participating in the most current ERS Standard Contract Term;

      - Once a DOTA has been approved by ERCOT any conflicts with Premises participating in subsequent ERS Standard Contract Terms will be resolved through the ERS procurement process and will not require the DOTA to be edited for those conflicts.

    - Are duplicated within the QSE’s submission; or

    - Are a Generation Resource.

  - The Load Zone information is incorrect;

  - The Premises included in the ADER are otherwise able to participate in the ERCOT market in a similar manner using existing participation models;

    - ERCOT determines that the ADER would otherwise not comply with the Protocols or this Governing Document; and/or

    - ERCOT has not received all applicable LSE Acknowledgments.

- Within ten Business Days of receipt of a complete ADER submission package, ERCOT shall accept or reject the submission and  shall notify the QSE accordingly via email, copying the DSP and Resource Entity.

- Upon receiving ERCOT’s acceptance, the QSE shall, within 20 Business Days, initiate registration of the ADER under the applicable participation option.  The registration-to-participation timeline for an ADESR is described in subsection 5.c.7.

- Registration of ADERs opting to register as ALRs:

  - Following ERCOT’s acceptance of the QSE’s submission for a given ADER opting to register as an ALR:

    - ERCOT shall provide the MW offset to be used to register as a CLR and operate as a net load under all circumstances, in terms of telemetry and other market submissions to ERCOT.

    - The Resource Entity must register the ADER as a CLR with ERCOT using the Resource Integration & Ongoing Operations (RIOO) application.

    - The location of an ADER in the Network Model will be identified by its Resource Dispatch Asset Code and the associated CIM Load in the model. The DSP, in collaboration with the interconnecting TSP if necessary, will populate the CIM Load for each individual premise identified by the QSE in its completed DOTA form. ERCOT will assign each ADER to a single CIM Load.

  - The telemetry and other market submissions for a registered ADER must always show the ADER as a net consumer of energy. This may require use of an offset, which will be a static MW value provided by ERCOT, as earlier described. Regardless of use of the MW offset, it will be acceptable if individual Premises that are components of the aggregation are net injectors of energy, based on TDSP metering at the Premises.

  - Known limitations relevant to the DSP, such as Premise injection limitations, must be reflected in the registration of the ADER. Identified limitations on the distribution system will not explicitly be enforced by ERCOT’s systems in awarding or dispatching the ADER.

  - The ADER shall be registered and associated with a QSE.

  - If an individual Premise that is part of the ADER can inject into the distribution system, the loadID for the TDSP read meter at the Premise must be updated such that any exports at the Premise will be treated as negative load. For ADERs in a NOIE Load Zone, a similar process needs to be done in coordination with the NOIE DSP and, if applicable, the TSP serving that NOIE.

  - Changes to the population of the ADER must be managed as follows:

  - The Resource Entity and the QSE are jointly responsible for maintaining ADER population information using the active DOTA form for the specific type of ADER.

  - ADER parameters will be established in the Network Model by the ADER’s Resource Entity using the approved Resource Registration process. ADERs that are subject to dynamically changing populations may need to set their Resource Registration data parameters at levels that will accommodate potential growth so as to reduce the need for frequent Resource Registration updates. This accounting for potential growth during registration should be done in consultation with ERCOT staff.

  - The QSE may add or remove Premises from an ADER at any time so long as the aggregation is still operating within the participation caps established by this Governing Document and the TSP or DSP. The QSE shall provide notice to each affected DSP of any changes to an ADER population by providing an updated DOTA form, which must be reviewed and confirmed by the relevant DSP prior to being included by the QSE in the ADER population. The following requirements apply to the addition and/or removal of Premises:

    - On the first day of each month following the first month of having an active approved ADER, the QSE shall provide notice to each affected DSP any and all changes to the DOTA form by providing an updated DOTA form. This updated DOTA form must include any Premises that are proposed to be added to or removed from the ADER and must also retain the Premises that are unchanged from the last update.  The updated DOTA form must clearly note the Premises that are proposed to be added or removed.

    - Consistent with the timelines and requirements in subsection 5.c.2 above, the DSP may accept or reject any proposed additions of Premises to a QSE’s ADER. The DSP may reject any proposed additions for the same reasons described in subsection 5.c.2, and shall provide the reasons for any rejection as also described in that subsection.

    - The DSP’s consent to the addition of any Premises to an ADER shall be documented by an email from a DSP employee to the submitting QSE. For each new Premise to which it consents, the DSP should add the appropriate Common Information Model (CIM) Load information to the DOTA form (as described in subsection 5.c.2), and return the DOTA form to the QSE. When the DSP returns the approved form to the QSE, it shall constitute a confirmation that the DSP serves each added Premise, and consents to the additional participation of these Premises in the Pilot Project. The QSE shall forward the DSP’s email consenting to the changes to ERCOT, and email the updated DOTA form approved by the DSP to ERCOT. The affected DSP and Resource Entity (RE) must be copied on both of these emails from the QSE to ERCOT. QSEs may request that a secure email account be created with ERCOT if using standard email is of concern.

    - Within five Business Days of receipt of both the required DSP consent and completed updated DOTA form, ERCOT will process the changes request by the QSE, subject to the participation caps outlined in this Governing Document. ERCOT shall notify the QSE of the time and date the updated “Details of Aggregation” list has been validated by ERCOT.

  - The QSE shall update appropriate telemetry values and market submissions when a change is made to the ADER population. All Premises included in the list provided should be currently enrolled with the REP. Any future switches should be accounted for in the  update based on start and stop dates.

  - Any ADER population updates shall include start and stop dates for new Premises in the ADER and/or Premises that have left the ADER. If a Premise is vacated or the customer has/is being switched to a different REP, the stop date should reflect that date; and if a new customer later moves into that Premise and joins the ADER (or joins with a different REP), a new start date should be used.

  - In competitive choice areas, QSEs will manage the ADER population by ESI ID, which ERCOT will then cross-reference to its internal systems. In the NOIE territories, QSEs shall provide unique meter identifiers consistent with the requirements detailed elsewhere in this document.

- Registration of ADERs opting to register as NCLRs:

  - Following ERCOT’s acceptance of the QSE’s submission for a given ADER opting to register as an NCLR:

    - ERCOT shall provide the MW offset to be used to register as a NCLR and operate as a net load under all circumstances, in terms of telemetry and other market submissions to ERCOT.

    - The Resource Entity must register the ADER as an NCLR with ERCOT using the Resource Integration & Ongoing Operations (RIOO) application.

    - The location of an ADER in the Network Model will be identified by its Resource Dispatch Asset Code and the associated CIM Load in the model. The DSP, in collaboration with the interconnecting TSP if necessary, will populate the CIM Load for each individual premise identified by the QSE in its completed DOTA form. ERCOT will assign each ADER to a single CIM Load.

  - The telemetry and other market submissions for a registered ADER must always show the ADER as a net consumer of energy. This may require use of an offset, which will be a static MW value provided by ERCOT, as earlier described. Regardless of use of the MW offset, it will be acceptable if individual Premises that are components of the aggregation are net injectors of energy, based on TDSP metering at the Premises.

  - Known limitations relevant to the DSP, such as Premise injection limitations, must be reflected in the registration of the ADER. Identified limitations on the distribution system will not explicitly be enforced by ERCOT’s systems in awarding or dispatching the ADER.

  - The ADER shall be registered and associated with a QSE.

  - If an individual Premise that is part of the ADER can inject into the distribution system, the load profile ID for the TDSP read meter at the Premise must be updated such that any exports at the Premise will be treated as negative load. For ADERs in a NOIE Load Zone, a similar process needs to be done in coordination with the NOIE DSP and, if applicable, the TSP serving that NOIE.

  - Changes to the population of the ADER must be managed as follows:

  - The Resource Entity and the QSE are jointly responsible for maintaining ADER population information using the active DOTA form for the specific type of ADER.

  - ADER parameters will be established in the Network Model by the ADER’s Resource Entity using the approved Resource Registration process. ADERs that are subject to dynamically changing populations may need to set their Resource Registration data parameters at levels that will accommodate potential growth so as to reduce the need for frequent Resource Registration updates. This accounting for potential growth during registration should be done in consultation with ERCOT staff.

  - The QSE may add or remove Premises from an ADER at any time so long as the aggregation is still operating within the participation caps established by this Governing Document. The QSE shall provide notice to each affected DSP of any changes to an ADER population by providing an updated DOTA form, which must be reviewed and confirmed by the relevant DSP prior to being included by the QSE in the ADER population. The following requirements apply to the addition and/or removal of Premises:

    - On the first day of each month following the first month of having an active approved ADER, the QSE shall provide notice to each affected DSP any and all changes to the DOTA form by providing an updated DOTA form. This updated DOTA form must include any Premises that are proposed to be added to or removed from the ADER and must also retain the Premises that are unchanged from the last update.  The updated DOTA form must clearly note the Premises that are proposed to be added or removed.

    - Consistent with the timelines and requirements in subsection 5.c.2 above, the DSP may accept or reject any proposed additions of Premises to a QSE’s ADER. The DSP may reject any proposed additions for the same reasons described in subsection 5.c.2, and shall provide the reasons for any rejection as also described in that subsection.

    - The DSP’s consent to the addition of any Premises to an ADER shall be documented by an email from a DSP employee to the submitting QSE. For each new Premise to which it consents, the DSP should add the appropriate Common Information Model (CIM) Load information to the DOTA form (as described in subsection 5.c.2), and return the DOTA form to the QSE. When the DSP returns the approved form to the QSE, it shall constitute a confirmation that the DSP serves each added Premise, and consents to the additional participation of these Premises in the Pilot Project. The QSE shall forward the DSP’s email consenting to the changes to ERCOT, and email the updated DOTA form approved by the DSP to ERCOT. The affected DSP and Resource Entity  must be copied on  these emails from the QSE to ERCOT. QSEs may request that a secure email account be created with ERCOT if using standard email is of concern.

    - Within five Business Days of receipt of both the required DSP consent and completed updated DOTA form, ERCOT will process the changes request by the QSE, subject to the participation caps outlined in this Governing Document. ERCOT shall notify the QSE of the time and date the updated DOTA list has been validated by ERCOT.

  - The QSE shall update appropriate telemetry values and market submissions when a change is made to the population. All Premises included in the list provided should be currently enrolled with the REP. Any future switches should be accounted for in the  update based on start and stop dates.

  - Any ADER population updates shall include start and stop dates for new Premises in the ADER and/or Premises that have left the ADER. If a Premise is vacated or the customer has/is being switched to a different REP, the stop date should reflect that date; and if a new customer later moves into that Premise and joins the ADER (or joins with a different REP), a new start date should be used.

  - In competitive choice areas, QSEs will manage the ADER population by ESI ID, which ERCOT will then cross-reference to its internal systems. In the NOIE territories, QSEs shall provide unique meter identifiers consistent with the requirements detailed elsewhere in this document.

- Registration of ADERs opting to register as ADESRs:

  - Following ERCOT's acceptance of the QSE's submission for a proposed ADESR:

    - The Resource Entity must register the Resource through the RIOO application using the process designated by ERCOT for an ADESR. The registration must identify the Resource as an aggregation. Pending implementation of any associated RIOO changes, ERCOT may use an interim manual process to identify and prioritize ADESR registrations.

    - The ADESR-specific DOTA form must cover only one CIM Load and must identify the participating Premises and devices, the applicable DSP, the aggregate charging and discharging capability in MW, the aggregate energy capability in MWh, and the other information required by ERCOT. The DSP, in coordination with the interconnecting TSP as necessary, must verify that all participating Premises and devices map to the same CIM Load and must provide the associated substation and CIM Load information.

    - The Resource Entity and QSE for an ADESR shall maintain registration information identifying each approved storage device, associated interconnection and control equipment, Premise, and connection point, and the association of those devices with the applicable CIM Load. This information shall be maintained through the ADESR-specific DOTA form and any supporting device register designated by ERCOT. Multiple storage devices may participate at one approved Premise or at multiple approved Premises only where the aggregation satisfies subsection 5.a and the applicable eligibility requirements.

    - The ADESR will be modeled in substantially the same manner as a DESR. ERCOT will assign the ADESR to a Resource Node at the applicable electrical bus. If a Resource Node does not already exist, the Resource Node created for the ADESR will be non-biddable in the DAM and CRR markets. If a Resource Node already exists at that electrical bus, ERCOT will map the ADESR to that existing Resource Node. Multiple Resources may be mapped to the same Resource Node.

    - The ADESR will be registered with its aggregate power and energy capabilities and must provide Current Operating Plan submittals, telemetry, and other Resource data applicable to a DESR, except as otherwise provided in this Governing Document. An ADESR is represented and dispatched as a Resource and does not use the MW offset or net-Load representation applicable to ADERs participating as ALRs or NCLRs.

    - Existing TSP and/or DSP studies and other registration reviews applicable to a DESR will apply to an ADESR.

  - Known limitations relevant to the DSP, such as Premise or device injection limitations, must be reflected in the registration of the ADESR. Identified limitations on the distribution system will not explicitly be enforced by ERCOT's systems in dispatching the ADESR.

  - The ADESR shall be registered and associated with a QSE.

  - Before including a storage device in an ADESR, the Resource Entity shall obtain or ensure documented, voluntary owner consent through the applicable participation agreement. The agreement shall explain compensation terms, device use, and withdrawal procedures and shall allow owners to establish minimum State of Charge, availability schedules, and a backup reserve. The QSE shall receive the operating constraints necessary to reflect these terms in market submissions and dispatchable capability. These customer terms do not alter the wholesale Settlement provisions of subsection 5.h.

  - Changes to the population of the ADESR must be managed as follows:

  - The Resource Entity and the QSE are jointly responsible for maintaining the ADESR population information using the active DOTA form for the specific type of ADER.

  - ADESR parameters will be established in the Network Model by the ADESR's Resource Entity using the approved Resource Registration process.

  - Routine connection or disconnection of an already-approved storage device at an approved connection point within its registered aggregation shall be treated as a change in operating availability rather than, by itself, a change in the registered population requiring a DOTA update. A new storage device, Premise, connection point, or material change in equipment, registered capability, or electrical location remains subject to the applicable population-update, DSP review, registration, and revalidation requirements. Review of an equipment substitution shall be proportionate to the change in electrical characteristics and risk without eliminating required approvals.

  - ERCOT, in coordination with affected DSPs and QSEs, shall establish an approved process for recurring movement of already-approved storage devices between qualified connection points. The process shall distinguish active contribution from registration of approved devices and locations and specify device identification, location verification, and coordination among QSEs. Before a device contributes at a receiving location, all required equipment, Premise, connection-point, and registration approvals must be complete; its actual electrical location must be verified; and its contribution to the prior aggregation must end. Each receiving aggregation must independently satisfy the applicable CIM Load, LSE, and DSP requirements. No device capability or energy may be double counted across aggregations. Routine movement within an approved operating arrangement shall not, by itself, require a new interconnection study or population approval. New devices, Premises, connection points, and material equipment or capability changes remain subject to applicable review. Devices connected at unapproved locations shall contribute no available capability.

  - The QSE may add or remove Premises or devices from an ADESR so long as the aggregation continues to meet the minimum aggregate injection capability established by this Governing Document, and all additions remain within the same DSP, the same LSE, and the same CIM Load. The QSE shall provide notice to the affected DSP of any changes to an ADESR population by providing an updated ADESR-specific DOTA form, which must be reviewed and confirmed by the DSP prior to being included by the QSE in the ADESR population. The following requirements apply to the addition and/or removal of Premises or devices:

    - If any Premises or devices are proposed to be added to or removed from the aggregation, the QSE shall provide an updated ADESR-specific DOTA form to the affected DSP, together with any required accompanying attestations. The updated form must include any Premises or devices that are proposed to be added to or removed from the ADESR and must also retain those that are unchanged from the last update. The updated DOTA form must clearly note the Premises or devices proposed to be added or removed.

    - In accordance with the timelines and requirements in subsection 5.c.2 above, the DSP may accept or reject any proposed additions of Premises or devices to a QSE's ADESR. The DSP may reject any proposed additions for the same reasons described in subsection 5.c.2, and shall provide the reasons for any rejection as also described in that subsection. The DSP must also verify that any added Premises or devices map to the same CIM Load.

    - The DSP's consent to the addition of any Premises or devices to an ADESR shall be documented by an email from a DSP employee to the submitting QSE. For each addition to which it consents, the DSP should add the appropriate Common Information Model (CIM) Load information to the ADESR-specific DOTA form and return the form to the QSE. When the DSP returns the approved form to the QSE, it shall constitute a confirmation that the DSP serves each added Premise or device and consents to its participation in the Pilot Project. The QSE shall forward the DSP's email consenting to the changes to ERCOT, and email the updated ADESR-specific DOTA form approved by the DSP to ERCOT. The affected DSP and Resource Entity must be copied on these emails from the QSE to ERCOT.

    - Within five Business Days of receipt of both the required DSP consent and the completed updated ADESR-specific DOTA form, ERCOT will process the changes requested by the QSE. ERCOT shall notify the QSE of the time and date the updated ADESR population has been validated by ERCOT. A Premise or device may not participate in the ADESR until ERCOT has completed that validation.

  - The QSE shall update appropriate telemetry values and market submissions when a change is made to the population or to the connected availability of approved storage devices. All Premises included in the list provided should be currently enrolled with the REP. Any future switches should be accounted for in the  update based on start and stop dates.

  - Any ADESR population update shall include start and stop dates for Premises or devices joining or leaving the aggregation. If a Premise is vacated or the customer has been or is being switched to a different REP, the stop date should reflect that date; and if a new customer later moves into that Premise and joins the ADESR, a new start date should be used.

  - In competitive choice areas, QSEs will manage the ADESR population by ESI ID, which ERCOT will then cross-reference to its internal systems. In NOIE territories, QSEs shall provide unique meter identifiers consistent with the requirements detailed elsewhere in this Governing Document.

- Qualification of ADERs

Irrespective of the participation model, an ADER wishing to participate in this Pilot Project must have its Resource and associated QSE qualify to provide the specific services available under the participation model chosen. ADERs participating as an ALR must also qualify to participate in SCED, per Nodal Protocols Section 3.6.1., Load Resource Participation.

# Metering, Telemetry, and Market Submissions

  - Terminology: For purposes of this Governing Document, the following terms shall have the meanings set forth below whenever used in this Section:

  - Telemetry: Refers to the ADER bi-directional, Inter-Control Center Communications Protocol (ICCP) telemetry between QSE and ERCOT systems for the ADER as an aggregate.

  - Metering: Refers to the 15-minute Settlement Quality TDSP read meters at the individual Premises that make up the ADER.

  - Market Submissions: Refers to the ADER-related XML submissions that the QSE submits to and receives from ERCOT.

  - ADER telemetry: ADER telemetry for ADERs opting to register as ALRs, as NCLRs, or as ADESRs must meet the following requirements:

  - ADERs opting to register as ALRs are considered ALRs for the purposes of this Pilot Project and must therefore comply with ALR metering and telemetry requirements.

  - ADERs opting to register as NCLRs are considered NCLRs for the purposes of this Pilot Project and must therefore comply with NCLR metering and telemetry requirements.

  - ADERs opting to register as ADESRs are considered DESRs for the purposes of this Pilot Project and must comply with DESR telemetry requirements.  An ADESR does not have a single physical meter at a Point of Interconnection. Instead, the ADESR's meter data is derived from device-level data aggregated to the Resource level to represent the behavior of the aggregation. Telemetry validation for an ADESR is performed under the ADESR-specific process described below.

  - A QSE representing an ADER must send Resource-level Real-Time telemetry to ERCOT every two seconds in accordance with Protocols Section 6.5.5.2, Operational Data Requirements; Nodal Operating Guide, Section 7, Telemetry and Communication; and the ERCOT Nodal ICCP Communication Handbook available on the ERCOT User Guides webpage. Telemetered data points are specific to the service being provided and are listed in detail in Protocols Section 6.5.5.2(6).

  - The QSE representing an ADESR shall report the aggregation's charging and discharging capability limits for each Operating Hour through the applicable ERCOT market-submission processes and shall update those limits in accordance with applicable requirements as availability changes. Forward-looking submissions shall account for expected device connections and disconnections, charging needs, owner-established reserves, and approved equipment and site limits. Registered nameplate capability shall not be substituted for the capability reasonably expected to be available for the applicable Operating Hour.

ERCOT shall publish implementation guidance identifying the required information, submission channel, and applicable deadline for forecast changes, unexpected device disconnections, changes in usable energy or delivery duration, and permanent registration changes. The guidance shall distinguish operating-availability updates from changes requiring registration or DOTA approval and shall be consistent with applicable Protocol and Operating Guide requirements. The Resource-level two-second telemetry requirement remains unchanged.

  - Real-Time capability, operating limits, and available energy for an ADESR shall reflect only approved, connected devices whose availability can be verified. The QSE shall exclude disconnected or otherwise unavailable devices from available capability and shall reduce reported capability when an owner reserve, availability limit, equipment limit, or distribution-system constraint restricts delivery. State of Charge reporting shall use the applicable ERCOT methodology and accurately represent the connected, participating devices. Anticipated future device connections shall not be reported as currently available capability.

  - The ADESR qualification process shall establish a documented response to disconnection, loss of communications, and invalid or stale device data. The response shall remove unverified capability from the reported available Resource capability, update market submissions as required, and apply safe device-level operating controls consistent with equipment protections and DSP requirements. The QSE shall not continue to represent unavailable or unverified capability as dispatchable.

  - For an ADER participating as an ALR or NCLR, the ADER’s telemetry must be an accurate representation of the aggregate values of all Premises in the Resource. Those values may be based on device-level or Premise-level conditions or a combination of both. An offset value will be added to the aggregate values, if needed, to ensure the telemetry is always communicated to ERCOT as a net load. That offset value will be established between the QSE and ERCOT as part of the qualification process at a static level that will allow for some growth in the ADER. The offset may be adjusted over time but only with the mutual agreement between the QSE and ERCOT.

  - For an ADER participating as an ALR or NCLR, telemetry values to ERCOT (Low Power Consumption (LPC), Maximum Power Consumption (MPC), Net Power Flow, etc.) must represent the sum of the corresponding values at the individual Premises or devices based on the approved DOTA form submitted to ERCOT by the Pilot Project participant, and must include any MW offset values provided by ERCOT. The difference between the value of the telemetered MPC and the value of the telemetered LPC for the ADER must equal the difference between the greatest possible injection quantity and the greatest possible withdrawal quantity.

  - For an ADER participating as an ALR or NCLR, ADER ramp rate telemetry to ERCOT must represent the weighted average of the ramp rates at the individual Premise or device based on the approved DOTA form submitted to ERCOT by the Pilot Project participant. As part of the validation of ADER telemetry, QSEs participating in the Pilot Project shall provide time series data of the net MW at the Premise level and/or device level.

  - If the ADER includes energy storage devices, time series data on State of Charge for the device will also be required.

  - The above data must be provided to ERCOT when requested, within a reasonable storage requirement timeframe. The data storage requirements and the mechanism of delivering this data to ERCOT will be determined later.

  - ADER Metering: ADER metering must meet the following requirements:

  - Premises in an ADER are required to have 15-minute interval meter data, whether ESI ID data from the competitive choice areas of ERCOT, or revenue-quality meter data within a NOIE territory. ERCOT will use this Premise-level interval meter data as the primary foundation of the telemetry validation process and as a secondary tool for event performance measurement and verification. For any Premises that export power to the distribution system, both the consumption data and export data must be provided to ERCOT.

  - Interval meter data must be time-stamped within appropriate standards in correlation with ERCOT 15-minute Settlement clock intervals, and shall be provided to ERCOT for Premises within the ADER through one of the following methods:

  - For ADERs in competitive choice areas of ERCOT, investor-owned TDSPs submit ESI ID-level Interval Data Recorder (IDR) or Advanced Metering System (AMS) data via the Texas Standard Electronic Transaction (TX SET) process (for IDR metering) or via the approved file format defined in Retail Market Guide, Section 9, Appendix G, ERCOT Specified File Format for Submission of Interval Data for AMS metering.

  - For ADERs in a NOIE service area, the NOIE shall submit IDR, AMS, or equivalent Premise-level meter data if associated with a non-Settlement ESI ID or a designated unique meter identifier. Such meters shall be maintained and read by the NOIE meter-reading entity. The data shall be submitted to ERCOT no later than 35 days after each corresponding Operating Day either via TX SET or in a format and transport method defined by ERCOT. NOIE Premise-level unique meter identifiers must use ESI ID-style nomenclature, in which the NOIE TDSP Department of Energy (DOE) code comprises the first digits of the identifier. The unique meter identifier must remain constant in perpetuity at the Premise.

  - A NOIE meter-reading entity shall validate Premise-level interval meter data; however, periods of time (intervals) with missing data should not be edited or estimated. For those Premises with missing interval data, those intervals will not be included in the aggregate values and may result in failed telemetry validation. Ongoing telemetry validation and performance measurement and verification are dependent upon a NOIE making timely and accurate Premise-level meter data submissions. Failure to meet the data submission requirements may result in suspension of the ADER’s qualification to participate in the Pilot Project. An ADER that has been suspended for this reason may be reinstated only upon successful restoration of accurate and timely meter data submissions.

  - NOIEs shall archive Premise-level data sufficient to meet these requirements.

  - ALR Telemetry Validation: Telemetry validation for ADERs opting to register as ALRs must meet the following requirements:

  - The objective of ADER telemetry validation is to create an acceptable standard that provides ERCOT operations with assurance that the telemetered values from the QSE provide a reasonable representation of the physical characteristics of the ADER. This section describes the processes ERCOT will use to conduct validation for QSE telemetry, with the goal of ensuring that an ADER’s telemetered data points provide a representation of ADER performance that meets reasonableness criteria consistent with good utility practice. With the submission of the DOTA form the QSE must indicate whether the ADER telemetry contribution from each Premise in the aggregation is at the TDSP read meter location or device location.

  - Premise-Level Telemetry:

  - The ADER telemetry values are to be a reasonable representation of the aggregate sum of the import and export values of the ADER member Premises plus the established offset. ERCOT will aggregate the Premise-level 15-minute interval Settlement meter data to the ADER level and will compare this data to the QSE telemetry values for net real power consumption (NPC) less the Resource specific assigned offset, averaged over each 15-minute interval during the period being evaluated.

  - ERCOT will conduct this telemetry validation as part of the ADER qualification process and periodically during the term of the Pilot Project, with each test encompassing all 15-minute Settlement Intervals during the evaluation period. The telemetry must validate to meet all of the following conditions:

    - Condition 1: Only intervals where the aggregate Premise-level 15-minute Settlement Interval meter data meets one of the following will be evaluated:

      - When the aggregate Premise-level 15-minute interval Settlement meter data shows as net withdrawing, the Resource’s metered withdrawals must equal or exceed 0.1 MW; or

      - When the aggregate Premise-level 15-minute interval Settlement meter data shows as net injecting (negative value in the meter data), the Resource’s metered injections must equal or exceed -0.1 MW.

    - Condition 2: Of these intervals being evaluated, the telemetered NPC value minus the Resource specific assigned offset must be within 10% of the aggregate Premise-level 15-minute interval Settlement meter data.

    - Condition 3: During the 8-hour evaluation period, at least 50% of the intervals must meet Condition 1 above.

  - Device-Level Telemetry:

  - If the ADER telemetry values represent the sum of the devices under control, the QSE will be required to provide device-level sub-meter (data recorder) data for each Premise in the aggregation contributing to the device-level telemetry to ERCOT upon request. This device-level sub-meter (data recorder) data must meet the minimum specifications established by ERCOT. As part of the qualification process, ERCOT will use the following two-step validation process for the QSEs device-level telemetry.

  - Step 1: The ADER NPC telemetered values minus offset averaged over each 15-minute interval must be within 10% of the aggregate of the device-level sub-meter (data recorder) data, averaged over each 15-minute interval during the period being evaluated.

    - All of the following conditions must be met for Step 1:

      - Condition 1: Only intervals where the aggregate device-level data, averaged over each 15-minute Settlement window are greater than 10% of the Resource’s requested energy capability will be evaluated as follows:

        - When the aggregate device-level data shows as net injecting, the Resource’s injections must exceed 10% of the Maximum Injection Capability (column E on the DOTA ADER Summary tab);or

        - When the aggregate device-level data shows as net withdrawing, the Resource’s withdrawals must exceed 10% of the Maximum Withdrawal Capability (column D on the DOTA ADER Summary tab).

      - Condition 2: Of these intervals being evaluated, the telemetered NPC value less the Resource specific assigned offset must be within 50% of the aggregate device-level data averaged over each 15-minute Settlement Interval when the Total Expected Registered Capacity (column I on the DOTA ADER Summary tab) is less than or equal to 1 MW, or within 10% of the aggregate device-level data averaged over each 15-minute Settlement Interval when the Total Expected Registered Capacity is greater than 1 MW.

      - Condition 3: During the 8-hour evaluation period, at least 50% of the intervals must meet Condition 1 above.

  - Step 2: ERCOT will instruct the QSE to deploy the ADER to a mutually agreed value that represents a significant portion of the ADER’s capability. This instruction will last for at least one full 15-minute Settlement Interval. The change in the telemetered NPC in response to the instruction must be within 10% of the total response observed in the aggregate Premise-level 15-minute interval meter data during each interval in the sustained response period. For Step 2 a SCED Set Point instruction may be used in lieu of an ERCOT initiated instruction.

  - In addition to the telemetry validation as part of the qualification, ERCOT may also perform additional periodic validation of the telemetry during the term of the Pilot Project. For Step 2 a SCED Set Point instruction may be used in lieu of an ERCOT initiated instruction.

  - Telemetry composed of both Premise and Device-level data:

  - If the ADER telemetry values represent a composition of both Premise-level and device-level data, ERCOT will perform the following:

  - Step 1: All of the following conditions must be met for Step 1:

    - Condition 1: Only intervals where telemetered NPC is greater than 10% of the registered Resource’s HRL will be evaluated.

    - Condition 2: Of the intervals being evaluated, the telemetered NPC value less the Resource specific assigned offset must be within 10% of the sum of (i) the aggregate Premise-level Settlement meter data for those Premises choosing Premise-level telemetry and (ii) the aggregate of the device-level data for those Premises choosing device-level telemetry, both averaged over each 15-minute Settlement Interval.

    - Condition 3: During the 8-hour evaluation period, at least 50% of the intervals must meet Condition 1 above.

  - Step 2: ERCOT will instruct the QSE to deploy the ADER to a mutually agreed value that represents a significant portion of the ADER’s capability. This instruction will last for at least one full 15-minute Settlement Interval. The change in the telemetered NPC in response to the instruction must be within 10% of the total response observed in the aggregate Premise-level 15-minute interval meter data during each interval in the sustained response period.

  - NCLR Telemetry Validation: Telemetry validation for ADERs opting to register as NCLRs  must meet the following requirements:

  - The objective of ADER telemetry validation is to create an acceptable standard that provides ERCOT operations with assurance that the telemetered values from the QSE provide a reasonable representation of the physical characteristics of the ADER. This section describes the processes ERCOT will use to conduct validation for QSE telemetry, with the goal of ensuring that an ADER’s telemetered data points provide a representation of ADER performance that meets reasonableness criteria consistent with good utility practice. With the submission of the DOTA form the QSE must indicate whether the ADER telemetry contribution from each Premise in the aggregation is at the TDSP read meter location or device location.

  - Premise-Level Telemetry:

    - The ADER telemetry values are to be a reasonable representation of the aggregate sum of the import and export values of the ADER member Premises plus the established offset. ERCOT will aggregate the Premise-level 15-minute interval meter data to the ADER level plus the assigned Resource offset and will compare this data to the QSE telemetry values for NPC averaged over each 15-minute interval during the period being evaluated.

    - ERCOT will conduct this telemetry validation as part of the ADER qualification process and periodically during the term of the Pilot Project, with each test encompassing all 15-minute Settlement Intervals during the evaluation period. The telemetry must validate to meet all of the following conditions:

      - Condition 1: Only intervals where the aggregate Premise-level 15-minute interval meter data meets one of the following will be evaluated:

        - When the aggregate Premise-level 15-minute interval Settlement meter data shows as net withdrawing, the Resource’s metered withdrawals must equal or exceed 0.1 MW; or

        - When the aggregate Premise-level 15-minute interval Settlement meter data shows as net injecting (negative value in the meter data), the Resource’s metered injections must equal or exceed -0.1 MW.

      - Condition 2: Of these intervals being evaluated, the telemetered NPC value minus the Resource specific assigned offset must be within 10% of the aggregate Premise-level 15-minute interval Settlement meter data.

      - Condition 3: During the 8-hour evaluation period, at least 50% of the intervals must meet Condition 1 above.

  - Device-Level Telemetry:

    - If the ADER telemetry values represent the sum of the devices under control, the QSE will be required to provide device-level sub-meter (data recorder) data for each Premise in the aggregation contributing to the device-level telemetry to ERCOT upon request. This device-level sub-meter (data recorder) data must meet the minimum specifications established by ERCOT. As part of the qualification process, ERCOT will use the following two-step validation process for the QSEs device-level telemetry.

    - Step 1: The ADER NPC telemetered values minus offset averaged over each 15-minute interval must be within 10% of the aggregate of the device-level sub-meter (data recorder) data, averaged over each 15-minute interval during the period being evaluated.

      - All of the following conditions must be met for Step 1:

        - Condition 1: Only intervals where the aggregate device-level data, averaged over each 15-minute Settlement window are greater than 10% of the Resource’s requested energy capability will be evaluated as follows:

          - When the aggregate device-level data shows as net injecting, the Resource’s injections must exceed 10% of the Maximum Injection Capability (column E on the DOTA ADER Summary tab); or

          - When the aggregate device-level data shows as net withdrawing, the Resource’s withdrawals must exceed 10% of the Maximum Withdrawal Capability (column D on the DOTA ADER Summary tab).

        - Condition 2: Of these intervals being evaluated, the telemetered NPC value less the Resource specific assigned offset must be within 50% of the aggregate device-level data averaged over each 15-minute Settlement Interval when the Total Expected Registered Capacity is less than or equal to 1 MW, or 10% of the aggregate device-level data averaged over each 15-minute Settlement Interval when the Total Expected Registered Capacity is greater than 1 MW.

        - Condition 3: During the 8-hour evaluation period, at least 50% of the intervals must meet Condition 1 above.

    - Step 2: ERCOT will instruct the QSE to deploy the ADER to a mutually agreed value that represents a significant portion of the ADER’s capability. This instruction will last for at least one full 15-minute Settlement Interval. The change in the telemetered NPC in response to the instruction must be within 10% of the total response observed in the aggregate Premise-level 15-minute interval meter data during each interval in the sustained response period.

    - In addition to the telemetry validation as part of the qualification, ERCOT may also perform additional periodic validation of the telemetry during the term of the Pilot Project.

  - Telemetry composed of both Premise and Device-level data:

    - If the ADER telemetry values represent a composition of both Premise-level and device-level data, ERCOT will perform the following:

    - Step 1: All of the following conditions must be met for Step 1:

      - Condition 1: Only intervals where telemetered NPC is greater than 10% of the registered Resource’s HRL will be evaluated.

      - Condition 2: Of the intervals being evaluated, the telemetered NPC value less the Resource specific assigned offset must be within 10% of the sum of (i) the aggregate Premise-level Settlement meter data for those Premises choosing Premise-level telemetry and (ii) the aggregate of the device-level data for those Premises choosing device level telemetry, both averaged over each 15-minute Settlement Interval.

      - Condition 3: During the 8-hour evaluation period, at least 50% of the intervals must meet condition 1 above.

    - Step 2: ERCOT will instruct the QSE to deploy the ADER to a mutually agreed value that represents a significant portion of the ADER’s capability. This instruction will last for at least one full 15-minute Settlement Interval. The change in the telemetered NPC in response to the instruction must be within 10% of the total response observed in the aggregate Premise-level 15-minute interval meter data during each interval in the sustained response period.

  - ADESR Telemetry Validation: Telemetry validation for ADERs opting to register as ADESRs must meet the following requirements:

  - The objective of ADESR telemetry validation is to provide ERCOT operations with assurance that the Resource-level telemetry, including State of Charge, provides a reasonable and time-synchronized representation of the aggregate behavior and capability of the devices in the ADESR.

  - Device-Level Telemetry:

    - ADESR telemetry must be derived from device-level data for all approved devices identified in the ADESR-specific DOTA form. Premise-level Settlement meter data does not substitute for the device-level data used to represent the Resource.

    - The QSE must retain and, upon request, provide time-series device-level real-power and State of Charge data for each participating device, in a format and at a frequency specified by ERCOT, with information sufficient to reconcile the data to the approved DOTA.

    - For an ADESR, device records shall identify the contributing devices and connection status and associate them with their approved electrical location. Validated data from compatible storage devices, associated interconnection and control equipment, or aggregation systems may satisfy the device-level requirements where the data meet ERCOT's applicable accuracy, timing, time-synchronization, identification, validation, and sub-meter or data-recorder specifications. Additional duplicative hardware shall not be required solely because a qualifying data source is integrated into a storage device or associated equipment. These provisions do not replace required Premise-level Settlement metering or change Settlement.

    - During initial qualification, ERCOT will conduct telemetry validation by comparing the Resource-level telemetry and State of Charge to the aggregate device-level data for the same period. The comparison must demonstrate that the telemetry reasonably represents the approved ADESR population during charging, discharging, and other operating conditions included in the evaluation.

    - As part of the qualification process, ERCOT will use the following two-step validation process for the QSEs device-level telemetry:

    - Step 1: The ADESR NPF MW telemetered values averaged over each 15-minute interval must be within 10% of the aggregate of the device-level sub-meter (data recorder) data, averaged over each 15-minute interval during the period being evaluated.

    - All of the following conditions must be met for Step 1:

        - Condition 1: Only intervals where the aggregate device-level data, averaged over each 15-minute Settlement window, are greater than 10% of the Resource’s requested energy capability will be evaluated as follows:

          - When the aggregate device-level data shows as net injecting, the Resource’s injections must exceed 10% of the Maximum Injection Capability (column D on the DOTA ADER Summary tab); or

          - When the aggregate device-level data shows as net withdrawing, the Resource’s withdrawals must exceed 10% of the Maximum Withdrawal Capability (column C on the DOTA ADER Summary tab).

        - Condition 2: Of these intervals being evaluated, the telemetered NPF MW value must be within 10% of the aggregate device-level data averaged over each 15-minute Settlement Interval.

        - Condition 3: During the 4-hour evaluation period, 100% of the intervals must meet Condition 1 above.

    - Step 2: ERCOT will instruct the QSE to deploy the ADESR to a mutually agreed value that represents a significant portion of the ADESR’s capability. This instruction will last for at least one full 15-minute Settlement Interval. The change in the telemetered NPC in response to the instruction must be within 10% of the total response observed in the aggregate Premise-level 15-minute interval meter data during each interval in the sustained response period. For Step 2 a SCED Set Point instruction may be used in lieu of an ERCOT initiated instruction.

    - ERCOT will conduct a SCED qualification test in which the ADESR is dispatched to mutually agreed Set Points that represent a meaningful portion of the ADESR’s charging and discharging capability. The QSE must demonstrate that the ADESR follows ERCOT-issued Set Points and provides State of Charge and other telemetry in a manner consistent with the requirements applicable to a DESR. The demonstration shall also address, as applicable, representative changes in device connection and availability, owner-imposed operating limits, and loss of communications or valid device data, using the performance criteria applicable to ADESRs. Planned availability schedules alone shall not establish dispatch capability.

    - ERCOT may conduct periodic telemetry validation during the term of the Pilot Project and may require additional validation following a material change to the ADESR population or registered capability. Failure to provide accurate telemetry or the supporting device-level data may result in suspension of the ADESR's qualification until the issue is corrected and the telemetry is successfully revalidated.

  - ADERs Providing Ancillary Services: Regarding telemetry and other market submissions, an ADER providing Non-Spin or ECRS may not have an Ancillary Service Offer  that exceeds the Non-Spin and ECRS MW amounts in the QSE submission signed by ERCOT.

# Additional Data from the QSE Representing the ADER

- The QSE shall provide allocation factors to ERCOT representing the fraction of the ERCOT-issued instruction to the ADER that is being provided by each particular metered Premise that is part of the aggregation. For Phase 4 of the Pilot Project, this information may be static and does not need to be provided in Real-Time or for the entire period of participation in the Pilot Project. Data that is provided will be used in off-line simulations to simulate different dispatch and pricing schemes. This data must be provided to ERCOT when requested, within a reasonable storage requirement timeframe. The data storage requirements and the mechanism of delivering this data to ERCOT will be determined later.

# Procurement and Deployment

ADER participation must comply with existing ALR, NCLR, and DESR requirements under the ERCOT Protocols and Other Binding Documents, subject to the exceptions described in this Governing Document. With respect to the procurement and deployment of ADERS for energy, Non-Spin and/or ECRS:

- ADERs qualified for Non-Spin and/or ECRS may be offered to provide Non-Spin and/or ECRS, as applicable, and will be cleared with other participating Resources, in accordance with existing ERCOT Protocols. Additionally, self-arranged or traded Non-Spin or ECRS may be provided by qualified ADERs. This Pilot Project is not intended to directly impact ERCOT’s determination of Ancillary Service quantities to be procured. However, ERCOT, at its sole discretion, may consider increases to Non-Spin and ECRS quantities, if deemed necessary, due to concerns regarding ADER performance.

- The deployment of an ADER participating as an ALR for Non-Spin, ECRS, or energy through SCED, will be in accordance with ALR requirements and other ERCOT rules. This includes dispatch using Load Zone shift factors.

- The deployment of an ADER participating as an NCLR for Non-Spin or ECRS will be via an XML deployment instruction. The deployment of an ADER participating as an ADESR for energy will be through SCED using nodal shift factors. The QSE must submit the Energy Bid/Offer Curves, Current Operating Plan data, State of Charge telemetry, and other market information applicable to a DESR, and the ADESR must follow ERCOT-issued Set Points in the same manner as a DESR. An ADESR is not currently eligible to provide Ancillary Services.

- For an ADESR, the QSE shall remain the interface with ERCOT for offers, applicable market submissions, and Resource-level dispatch. The QSE, directly or through its aggregation control provider, shall translate ERCOT Dispatch Instructions into device-level charging and discharging commands within reported operating limits. The QSE shall manage device availability and owner constraints before offering capability or accepting dispatch obligations and shall comply with applicable instructions and performance requirements. A scheduled disconnection of an approved device shall not, by itself, constitute nonperformance when its effect is reflected timely and accurately in applicable Current Operating Plan data, telemetry, and market submissions and the ADESR continues to satisfy its dispatch and other obligations. An expected disconnection shall not retroactively excuse a dispatch shortfall or relieve the QSE of an existing commitment. These provisions do not make an ADESR eligible for Ancillary Services or modify the Settlement provisions of subsection 5.h.

# Performance Evaluation and Compliance Metrics

ADERs will be registered as ALRs. NCLRs, or ADESRs in ERCOT’s systems.  Pending implementation of any associated RIOO changes, ERCOT may identify ADESRs through the interim manual process described in subsection 5.c.7.

ADERs registered as ALRs will have their performance evaluated using the existing CLREDP and Set Point Deviation processes for ALRs. The performance analysis results will be included in the monthly performance reports for CLRs. ERCOT may revoke an ADER’s qualification to provide Non-Spin or ECRS if the ADER demonstrates a continuing failure to perform. As part of Phase 4, ERCOT staff, along with stakeholders, may consider whether the existing performance tolerances for measuring performance when dispatched are appropriate for Resources whose rated capacity may be less than the current 2 MW compliance deadband.

ADERs registered as NCLRs will have their performance evaluated using the meter-before/meter-after baseline model as described in the Demand Response Baseline Methodologies document posted to (https://www.ercot.com/files/docs/2024/09/09/demand_response_baseline_methodologies_sep-9-2024.docx)

ADERs registered as ADESRs will have their performance evaluated using the existing ESREDP performance and compliance processes, including applicable Set Point Deviation processes, except as otherwise provided in this Governing Document. ERCOT will evaluate the ADESR's response to SCED Set Points and the accuracy of its Resource-level telemetry and State of Charge data. ERCOT may suspend or revoke the ADESR's SCED qualification if it demonstrates a continuing failure to perform or to provide accurate telemetry. Because ADESRs are not currently eligible to provide Ancillary Services, Ancillary Service performance metrics do not apply to ADESRs.

# Settlement and Cost Allocation

Energy from ADERs participating as ALRs will be settled in accordance with the ERCOT Nodal Protocols regarding ALR energy Settlement, and the Load Zone price will be used for Settlement of energy. There is no SCED participation for ADERs participating as NCLRs. In the event there are Premises within the ADER that inject into the distribution system, that injection will be treated as negative Load and the ERCOT energy Settlement will value it as negative Load in the Settlement for the QSE. The ADERs participating in the Pilot Project will be subject to other ERCOT Settlement calculations for Resources as described in the ERCOT Nodal Protocols, including the Ancillary Service Imbalance Settlement calculations.

Energy from ADERs participating as ADESRs will likewise be settled at the applicable Load Zone price, notwithstanding that ADESRs are dispatched at a nodal level using nodal shift factors.

# Evaluation and Analysis of Different ADER Participation Models for Phase 4

This section outlines some of the studies that ERCOT will be conducting during Phase 4 of the Pilot Project:

- ERCOT will evaluate the nodal dispatch of ADESRs using nodal shift factors and the corresponding effects on transmission congestion the potential transition of ADESRs from zonal to nodal Settlement, and the treatment of ADESRs in ERCOT planning models to inform which participation approaches should be carried forward into the Protocols at the conclusion of the Pilot Project.

- Phase 4 evaluation shall assess ADESR configurations that qualify and participate, including configurations with variable connection schedules and recurring movement between approved Premises. Qualifying bidirectional electric vehicle systems shall be an explicit use case within this technology-neutral evaluation, including residential, fleet, and depot configurations. ERCOT, in coordination with participating QSEs and DSPs, shall distinguish registered capability from connected availability and evaluate electrical mapping, dispatch performance, telemetry quality, customer operating constraints, participation costs, and barriers to enrollment. The evaluation shall address the practical effects of common-CIM-Load, common-LSE, and minimum-size requirements; any broader aggregation arrangement shall be evaluated separately for reliability and accurate locational dispatch. Findings shall identify practical changes needed for a durable market pathway. Future Ancillary Service eligibility and changes to metering or Settlement shall be evaluated separately and are not authorized by these participation provisions.

- ERCOT will continue to conduct off-line studies using archived production data to analyze different dispatch and pricing schemes and their comparative effectiveness in managing congestion. These include dispatch and Settlement using:

  - Logical Resource Nodes (LRNs):

    - Dispatch with static allocation factors used to determine the LRN shift factor and pricing; and

    - Dispatch with dynamic allocation factors used to determine the LRN shift factor and pricing.

    - The process by which allocation factor data will be provided to ERCOT for each ADER will be determined later.

  - Smaller Load Zones.

These different ADER modeling approaches will be compared and trade-offs between accuracy and complexity will be evaluated.

- ERCOT will continue to evaluate the ability of ADERs to provide Primary Frequency Response (PFR), identify processes for verifying any PFR response from ADER, and understand how the provision of PFR by ADERs may impact, or be limited by, the distribution system. While ADERs are not explicitly required to provide PFR in Phase 4, ADERs that can provide PFR are requested to do so, as this participation will allow this needed analysis during Phase 4 of the Pilot Project to occur.

- ERCOT will continue to work with the PUCT and stakeholders regarding the provision of Ancillary Services by Resources connected to the electric distribution system. The approach taken for ADERs will be linked to broader discussions on this topic as it relates to all distribution-connected Resources.

- Pilot Project participants will collaborate with ERCOT to provide relevant data relating to these studies upon request. ERCOT will report back on the progress of these studies and availability of data from Pilot Project participants to the TAC or a designated working group.

# Program Costs

ERCOT does not anticipate any cost impacts attributable to Phase 4 of the Pilot Project. ERCOT anticipates that the approach discussed in this document will not require major changes to its existing software systems, although limited registration, modeling, or process changes may be required to identify and administer ADESRs, and that it will be able to absorb staffing impacts in its current Operations and Maintenance budget.

# Reports

Based on Phase 4 evaluations, ERCOT will continue to review and report on the following:

- For storage devices with variable connection schedules or recurring movement between approved Premises, registered capability and connected availability; electrical mapping, telemetry quality, dispatch performance, customer operating constraints, participation costs, enrollment barriers, and recommended changes needed for durable participation.

- Recommendations for performance and compliance verification and metrics for ADERs, including additional data recorder requirements;

- Recommendations regarding alternative dispatch and pricing schemes for consideration in the future, such as recommendations on the LRN concept;

- Recommendations for processes, Protocol language, or changes necessary to address feedback from TDSPs and Aggregators on the program;

- Size of participation in aggregate and by Load Zone; and

- How many devices are reported to have communication standards, and of those that do, what those standards are.

These reports and other information related to this Pilot Project will be stored on the ADER Pilot Projects page on ERCOT’s website.

# Construction

This Governing Document and its appendices shall be liberally construed to achieve the purposes of the Pilot Project. Unless otherwise defined herein, , capitalized terms used in this Governing Document shall have the meanings ascribed to them under the ERCOT Protocols;, provided, however, that such terms shall be construed and applied in a manner consistently with the requirements of this Governing Document for the purposes of the ADER Pilot Project. In the event of any conflict between this Governing Document and the ERCOT Protocols, Operating Guides, or any Other Binding Document, the ERCOT Protocols, Operating Guides, or Other Binding Document shall control; provided, however, that with respect to any conflict or inconsistency relating to the scope or administration of this Pilot Project, the terms of this Governing Document shall control, but only to the extent of such conflict.

# Appendix A

Load Serving Entity’s Qualified Scheduling Entity Acknowledgment for NCLR-Type Participation

ERCOT Aggregate Distributed Energy Resource Pilot Project

*This form is only required for ADERs opting to register as NCLRs

This Acknowledgment is signed by an officer of the Qualified Scheduling Entity (“QSE”) of the Load Serving Entity (“LSE”) (“LSE QSE”) identified below.

By my signature, I confirm that the below-identified LSE QSE has received from [QSE PARTICIPANT’s NAME], a QSE in the ERCOT Region, an initial “Details of the Aggregation” submittal as that term is defined in the “Aggregate Distributed Energy Resource Pilot Project Governing Document,” and that the LSE QSE represents the LSE of the Premises identified in the initial “Details of Aggregation,” and that the LSE QSE consents to the NCLR-type participation of those Premises in this Pilot Project through [QSE PARTICIPANT’s NAME]. For any subsequent updates to the ADER population, the below-identified LSE QSE confirms that it will verify that the LSE represented by the LSE QSE provides retail electric service to the of the Premises identified, and will consent to or exclude each such Premise’s participation in this Pilot Project. The LSE QSE acknowledges that it understands the potential for impacts to its ERCOT settlements and financial positions related to the Premises’ load as a consequence of that participation.

I understand that the below-identified LSE QSE may rescind this acknowledgment by providing 30 days’ notice to [QSE PARTICIPANT’s NAME] and ERCOT, but that no termination of this acknowledgment will be effective before the end of any period for which ERCOT has already issued an award notification to [QSE PARTICIPANT’s NAME].

LSE QSE:___________________________________________________

LSE QSE DUNS+4:___________________________________________________

Officer Signature: _____________________________________________________

Printed Name:____________________________________________

Title: ___________________________________________________

Date: ___________________________________________________

# Appendix B

Distribution Service Provider Acknowledgment

ERCOT Aggregate Distributed Energy Resource Pilot Project

This Acknowledgment is signed by an officer of the Distribution Service Provider (DSP) identified below.

By my signature, I confirm that the below-identified DSP has received from [QSE PARTICIPANT’s NAME], a Qualified Scheduling Entity in the ERCOT Region (“QSE”), an initial “Details of the Aggregation” submittal as that term is defined in the “Aggregate Distributed Energy Resource Pilot Project Governing Document,” and that the DSP provides delivery service to each of the Premises identified in the initial “Details of Aggregation,” and that the DSP consents to the participation of those Premises in this Pilot Project. For any subsequent updates to the ADER population, the below-identified DSP confirms that it will verify that it provides delivery service to each of the Premises identified, and will consent to or exclude each Premise’s participation in this Pilot Project. The DSP acknowledges that it understands the potential for simultaneous injection of power from each Premise into the DSP’s system as a consequence of that participation.

I understand that the below-identified DSP may rescind this acknowledgment by providing 30 days’ notice to the QSE and ERCOT, but that no termination of this acknowledgment will be effective before the end of any period for which ERCOT has already issued an award notification to QSE Participant.

DSP:___________________________________________________

Officer Signature: _____________________________________________________

Printed Name:____________________________________________

Title: ___________________________________________________

Date: ___________________________________________________

# Appendix C

Supplement to the Standard Form Market Participant Agreement

Between

[Name of QSE]

and

Electric Reliability Council of Texas, Inc.

This Supplement to the Standard Form Market Participant Agreement (“Supplement”), effective as of [START DATE TO BE ENTERED BY ERCOT] (“Start Date”), is entered into by and between [PARTICIPANT’s NAME], a Qualified Scheduling Entity in the ERCOT Region (“QSE” or “QSE Participant”), and Electric Reliability Council of Texas, Inc., a Texas non-profit corporation (“ERCOT”).

Recitals

WHEREAS:

- The Public Utility Commission of Texas (“PUCT”) has authorized ERCOT to conduct pilot projects in 16 Texas Administrative Code § 25.361(k);

- The ERCOT Board has approved an Aggregate Distributed Energy Resource (ADER) pilot project (“Pilot Project”), as described in the Governing Document for Aggregate Distributed Energy Resource Pilot Project (“Governing Document”);

- Specific terms used in this Supplement that are defined in the Governing Document have the meanings assigned to them in that document;

- QSE Participant is a QSE in the ERCOT Region and has executed a Standard Form Market Participant Agreement (“Market Participant Agreement”) with ERCOT;

- QSE Participant wishes to submit bids and/or offers from ADERs; and

- The Parties enter into this Supplement in order to establish the terms and conditions by which ERCOT and QSE Participant will discharge their respective duties and responsibilities with respect to the ADER Pilot Project.

Agreements

NOW, THEREFORE, in consideration of the mutual covenants and promises contained herein, ERCOT and QSE Participant (the “Parties”) hereby agree as follows:

- All terms and conditions of the Market Participant Agreement between QSE Participant and ERCOT remain in full force and effect.

- QSE Participant and ERCOT will abide by and comply with the rules of the ADER Pilot Project set out in the Governing Document.

- Any Party may terminate this Supplement to the Market Participant Agreement by providing 30 days’ notice to the other Parties; however, no termination of this Supplement will be effective before the end of any period for which ERCOT has already issued an award notification to Participant.

- Otherwise, this Supplement to the Market Participant Agreement will terminate upon the completion of all obligations incurred under the terms of the Governing Document.

- This Supplement to the Market Participant Agreement may be executed in two or more counterparts, each of which is deemed an original, but all constitute one and the same instrument.

SIGNED, ACCEPTED, AND AGREED TO by each undersigned signatory who, by signature hereto, represents and warrants that he or she has full power and authority to execute this Supplement.

Electric Reliability Council of Texas, Inc.:

By: ____________________________________________________

Printed Name: ___________________________________________

Title: ___________________________________________________

Date: ___________________________________________________

QSE Participant:

By: _____________________________________________________

Printed Name:____________________________________________

Title: ___________________________________________________

Date: ___________________________________________________

Attached to this Agreement, QSE Participant shall include the “Details of the Aggregation,” as that term is defined in the “Aggregate Distributed Energy Resource Pilot Project Governing Document.”

All capitalized terms used herein and not otherwise defined have the meanings ascribed to them under the ERCOT Protocols.

Unless otherwise indicated, capitalized terms in this Supplement have the meanings ascribed to them in the ERCOT Protocols.