# ERCOT Operations Bulletin 153

ERCOT has revised the Frequency Control Desk section of the Operating Procedure Manual.

Changes include updating section 2.5.2 regarding NERC Recover Criteria after a NERC Reportable DCS Event.

| ### 2.5.2 Use of LAARs to Arrest a Reportable Low Frequency Disturbance |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | To meet NERC Recovery Criteria after a potential NERC Reportable DCS Event: |
| NOTES: | NERC Recovery Criteria Within 15 minutes ERCOT shall: - Return system frequency to 60 Hz if it was greater than or equal to 60 Hz prior to the disturbance, OR - Return system frequency to its pre-disturbance value if it is was less than 60 Hz prior the disturbance. A potential NERC Reportable DCS Event - Single contingencies – one event characterized by the sudden, unanticipated loss of generation greater than or equal to 1000 MWs , OR - Multiple contingencies – the loss of multiple units within one minute or less if the combined magnitude exceeds 1000 MWs. It is anticipated that the deployment of LAARs will occur in stages. LAARs UFRs are set at 59.7 Hz. If ERCOT declares an “Emergency Notice”, the text message may be sent as time permits so as not to impede system operations. |
| 1 | When a disturbance occurs due to a loss of generation, DETERMINE immediately if the event is potentially a NERC Reportable DCS Event. |
| 2 | IF the event is not a NERC Reportable DCS Event, proceed with normal operation. |
| 3 | IF the event is a potentially NERC Reportable DCS Event and the Frequency is above 59.7 Hz, - immediately place a hotline call to the QSEs and issue a VDI to deploy ALL un-deployed LAARs and hydro generation that are providing Responsive Reserve service. - ISSUE one VDI to all QSEs Typical Script: “ERCOT has experienced a potential DCS Event and all QSEs are required to deploy any un-deployed LAARs and hydro supplying Responsive Reserve.” |
| 4 | As soon as possible, REQUEST that the Transmission & Security Desk use the Hotline to notify the Transmission Operators. Typical script: “Due to a NERC DCS Event, ERCOT is deploying LAARs that are supplying Responsive Reserve.” |
| 5 | Restore LAARs incrementally as system conditions permit. |
| 6 | REQUEST that the Transmission & Security Desk notify the TOs that LAARs are being restored. Typical script: “LAARs that were supplying Responsive Reserve are being restored incrementally.” |