# ERCOT Operations Bulletin #71

ERCOT has revised the Transmission & Security Desk section of the Operating Procedure Manual.

Provided clarification for section 2.2.4, changed VDI to OOME.

| ### 2.2.4 Managing the Wind Powered Generation Resources (WPGR) in the McCamey Area |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | If the Total Transmission Capacity in the McCamey area is greater than the total amount of Tradable Generation Rights (TGR) allocated to Slow Response Wind Farms (SRWF) and Rapid Response Wind Farms (RRWF), THEN RRWF may be issued instructions to operate at the maximum output allowed by system conditions. |
| 2 | If the Total Transmission Capacity in the McCamey area is less than the total amount of TGR allocated to both SRWF and RRWF, THEN: 2.1 Instruct the RRWFs to reduce output such that the congestion is relieved. This instruction should be for one (1) hour duration. 2.2 Issue OOME to each SRWF to reduce its output by 10 Mw for a minimum of 3 hours. The reduction is to commence one hour after the RRWF instruction is issued. 2.3 After each SRWF has reduced its output by 10 MW, and system conditions permit, the RRWF OOME can be released. |
| NOTE: | SRWF can respond to ERCOT Dispatch Instructions no more often than one instruction per three consecutive hours. |
| 3 | At least three hours after performing Step 2.2 above, and if system conditions permit, perform step 3.1, otherwise perform 3.2 3.1 Resume operation up to an output level that will allow RRWF to operate at or above their TGR ownership levels. OR 3.2 Dispatch both SRWF and RRWF to levels that will allow them both to operate to the maximum allowed based on capacity-ratio-share. |

A copy of the procedure, Transmission & Security Desk V2R19, is attached.