# ERCOT Operations Bulletin #78

ERCOT has revised the Shift Supervisor section of the Operating Procedure Manual.

Changes to this procedure update include:  Added section 2.1.7 Coordinating Line Limit Changes and added section 2.1.8 Monitoring CSC Limits.

V2R6

| ### 2.1.7 Coordinating Line Rating Changes |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | When notified by the Transmission and Security Desk operator that a Transmission Operator has provided changes to a line’s ratings, NOTIFY the engineer on-call and provide the following information: - Equipment ID Name - MVA ratings (Continuous, Emergency and 15 Minute) - Name of Operator on duty - Name of Transmission Operator - Name of Transmission Operator’s authorizing Engineer - Authorizing Engineer’s contact phone number. |
| 2 | Log this communication in the Shift Supervisor’s Log, using the “Line Rating Changes” log type |
| 3 | Log the response of the ERCOT Operations Engineer in the Shift Supervisor’s Log, using the “Line Rating Changes” log type. |
| NOTE | If the rating received is a dynamic rating, the Transmission Operator must send it by e-mail or fax. |
| 4 | Forward related correspondence (email or fax) to Ricson Chai. |

| ### Monitoring CSC Limits |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE | NERC Policy 2 requires that NERC be notified when Interconnection Reliability Operating Limits (IROL) have been exceeded that could expose ERCOT to instability, cascading outages, or uncontrolled separation over a widespread area. |
| 1 | Near the end of each shift, verify that the CSC Limits have not been exceeded during the shift. - Open PI Process Book - Select Transmission Limit & Flow Summary for the ERCOT Top Page tab. - Check each CSC flow during the desired date range - Select Calendar to change the date range (The display will graph the CSC limit and line flow for that date range) - Deselect first flow and check next flow - Repeat until all flows have been selected and all data has been collected. |
| 2 | If any CSC exceeds the limit for more than 30 consecutive minutes, LOG it under log type “Exceeding Limits”. Include the date and time of the violation and the system conditions that caused the violation. |
| 3 | Notify by email the Chief System Operator and the on-call Operations Support Engineer. Include the data from Step 2. |