# Power Operations Bulletin #86

ERCOT has revised the Frequency Control section of the Operating Procedure Manual.

Changes include clarifying section 2.5.3 “Operator Instructions for High Frequency.”

CN 122 5/12/2004

JEB  AL

| ### Operator Instructions for High Frequency |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
|  | The following steps are to be taken in the event of High system frequency of unknown cause. If the cause of High System Frequency is known and system response or other actions are expected to correct it, then the following steps are optional. |
| NOTE: | For all frequency deviation events the Frequency Control Desk Operator must consult with the Transmission and Security desk to confirm that no OOMs from that desk could be affecting frequency. |
|  | Frequency above 60.05 and continuing to climb or over 60.05 > five minutes. |
| 1 | If regulation down capacity remains and is deploying: - Observe to see if the trend is reversing, if not then increase “Requested ACE Percentage” and observe frequency response. - Call QSE’s with positive SCE and direct them to reduce generation to return their SCE to zero as soon as possible. - Remove SCE feedback from QSEs with high SCE and monitor frequency response. |
| NOTE: | Typically a 300 MW dispatch instruction during the winter months would be expected to have a 0.1 Hz influence, while during the summer months this would require ~700 MW of reduction. |
|  | Frequency above 60.10 and continuing to climb |
| 2 | If the non-compliant QSE’s inform you that they cannot restore zero (0) SCE within five (5) minutes or no QSE appears to be hanging out, then: Issue Verbal Dispatch instructions to one or more QSE’s (other than those failing to maintain 0 SCE) to reduce generation. |
| 3 | Remove SCE feedback from QSEs with high SCE and monitor frequency response. |
| 4 | If no physical regulation down is available, call QSE with most positive SCE (over generating the most) and direct them to take offline a unit or units with over 300 MW immediately. Notify the QSE that this is an emergency instruction. |
| 5 | Log Actions taken under Steps 2, 3, and 4. |

A copy of the procedure, Frequency Control Desk V2R13, is attached.