###### Power Operations Bulletin #170

###### CN#223 – Modified Non-Spin Procurement Methodology

Effective Date:  June 1, 2005

Expiration Date:  June 30, 2005

The following methodology is to be used in place of Appendix 4 of this procedure.

###### Methodology for Determining Non-Spin Procurement

Use the following in determining the amount of NSRS needed:

- IF the current month is April, May, or October, then purchase NSRS in amounts equal to the largest unit online for the hours projected within 85% of peak hour.

- For other months of the year,

- IF today’s and tomorrow’s ERCOT high temperature is projected above 95 degrees in Dallas/Ft. Worth or Houston, THEN PURCHASE NSRS in amounts equal to the largest unit online for the hours projected warmer than 95 degrees.

OR

- If tomorrow’s low temperature forecast is projected below 30 degrees in Dallas/Ft. Worth or Houston, THEN PURCHASE NSRS in amounts equal to the largest unit online for

  - the projected morning load pickup hours and

  - hours projected within 85% of peak hour.

OR

NOTE:  Calculate “Spinning Reserve Online” as follows:

In MAI, “Max Cap Room + RRS = spinning reserve online”

- IF the current day generation plan shows <4600MW of spinning reserve online for any hour, THEN for the next day, PURCHASE amounts of NSRS equal to the largest unit online for hours in which the Day Ahead operator estimates spinning reserves online will drop lower than 4600 MW.

  - The shift supervisor may choose to ignore (not to procure non-spin) for single hours of deficiency in off-peak hours.

  - If such a decision is made, log it in the Shift Supervisor’s log.

Reference:

www.ercot.com  “ERCOT Methodologies for Determining Ancillary Service Requirements – Current”