# ERCOT Operations Bulletin 178

ERCOT has revised the Transmission & Security Desk section of the Operating Procedure Manual.

Changes include updating section 2.2.5 “Remedial Action Plans.”

| ### 2.2.5 Remedial Action Plans |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | A Remedial Action Plan (RAP) is to relieve the loading on the Transmission Facility within 15 minutes. ERCOT shall enforce pre-contingency System Operating Limit(s) to control the post contingency loading of the facility to levels below the 15-Minute Rating. The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Emergency Rating within 15 minutes. The “15-Minute Rating” and “LDSH” refer to the same thing. |
| CAUTION: | Remedial Action Plans are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions. |
| 1 | When RTCA shows a post-contingency overload and a Remedial Action Plan exists resolve it, - REVIEW the Remedial Action Plan with the associated Transmission Operator - Notify the Shift Supervisor of the anticipated actions. |
| 2 | If a Remedial Action Plan does not exist for this contingency and the Outage Notes do not provide a plan, REQUEST that Operations Engineering investigate development of a Remedial Action Plan for the anticipated insecure state. |
| 3 | If the contingency anticipated by the Remedial Action Plan takes place, - DIRECT implementation of the Remedial Action Plan - RESPOND as quickly as possible to requests made by the Transmission Operator in accordance with the Remedial Action Plan. |
| 4 | If Post-Contingency loading approached the “15-Minute Rating,” utilize pre-contingency congestion management methods to keep the Post-contingency loading below the “15-Minute Rating.” |
| 5 | If congestion management techniques will not control the post contingency loading below the “15 Minute Rating,” ISSUE a transmission alert. |
|  | Between 0000 and 0300 each day, the Transmission & Security Desk Operator should review the logs and verify that no RAPs remain in effect from the preceding day. IF any RAPs are still in use, evaluate system conditions to determine if: - The RAPs should remain in effect, OR - The system Action plan should be returned to a normal status. |
| 6 | IF the ERCOT System Operator and Shift Supervisor agree that the RAP is no longer needed, the Transmission and Security Desk Operator shall direct the TO to: - Return the system to its’ normal status, OR - Return the system to its’ status prior to implementation of the RAP Which ever state is applicable. |

A copy of Bulletin #178 is available at http://www.ercot.com/Participants/MarketBulletins.htm.