# ERCOT Operations Bulletin 180

ERCOT has revised the Transmission & Security Desk section of the Operating Procedure Manual.

Changes include incorporating new section 2.1.2 “OOME – VDI Guidelines.”

| ### OOME – VDI Guidelines |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions necessary to ensure system security. |
| 1 | If an OOME Dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that resource), then: - The duration of the OOME Dispatch instruction should end at the next scheduled off-line time according to the Resource Plan, OR the end of the operating day, whichever is shortest. - If the QSE representing the resource expresses a need for that resource to be returned on-line, and there is no negative impact on system reliability, then issue a VDI to the QSE to disregard the OOME instruction for the appropriate intervals. |
| 2 | When system conditions require one CT of a Combined Cycle Plant to be OOMEd off line, use the following steps: - Contact the QSE and determine which CT should receive the OOME - Obtain from the QSE the MW output impact the CT’s OOME will have on the steam unit. - OOME the required CT off line - Send an OOME equal to the amount the steam unit will produce when the CT is shut down. The intervals for both OOMEs should be the same. |
| 3 | When issuing a unit specific dispatch instruction (s) to a plant to change the output, but where all units will remain on line: - Determine what the net plant output should be. - Determine the unit (s) and MW amount per unit to be dispatched. - Send the dispatch instruction. |
| 4 | When a Dispatch Instruction prevents a QSE from performing their Ancillary Service obligation, the system operator may chose to exercise one of the two following options: - Upon a QSE’s request, issue a VDI to relieve the QSE from their Ancillary obligation. Should system conditions warrant, a second market may be necessary to procure additional Ancillary Services. Inform the Shift Supervisor that it may be necessary to open a second market. - Release the QSE from the dispatch instruction so they can come back into compliance. In this case, an element may exceed first contingency criteria. |
| 5 | If a VDI is issued to a QSE to relieve them from their Ancillary Service obligation, fax a copy of the VDI to ERCOT Compliance at 225-7165. |
| 6 | If a first contingency criterion is being exceeded, ISSUE a Transmission Alert and REQUEST the Operations Support Engineers develop a Mitigation Plan. |

A copy of the updated procedure, Transmission & Security Desk V3R46, is available at http://www.ercot.com/AboutERCOT/PublicDisclosure/ERCOTProcedures.htm.