# ERCOT Operations Bulletin 190

ERCOT has revised the Transmission & Security Desk section of the Operating Procedure Manual.

Changes include incorporating new section 2.4.3 “DFW Reactive Reserves” and new

Appendix 8 “DFW Reactive Reserves.”

| ### 2.4.3 DFW Reactive Reserves |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | It is necessary to have 1400 MVAR of reactive reserve in the DFW area at all times to avoid voltage collapse and maintain the system in a secure state. The table in Appendix 8 is a list of the units in the DFW area. The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. |
| 1 | If the spreadsheet indicates that reactive reserves have fallen below 1400 MVAR, direct the TOs to do the following: - Place all capacitors in the DFW area in service - Take all the reactors in the DFW area out of service |
| 2 | Using Appendix 8, increase generation on the available units. |
| 3 | Bring additional DFW generation online. Units should be chosen from the table below based on response time and system requirements. |
| 4 | If none of the above actions help in getting the reactive reserve to 1400 MVAR, issue a “Voltage Collapse” alert in the DFW area and call on Operations Support Engineers for assistance. |

## Appendix 8:  DFW Reactive Reserves

| Unit Name | Number | Most recent lagging test date | Lagging result |
| --- | --- | --- | --- |
| Northlake | 1 | 6/23/2003 | 118 |
|  | 2 | 7/7/2003 | 122 |
|  | 3 | 7/6/2001 | 200 |
| Handley | 1 | 8/25/2000 | 11 |
|  | 2 | 7/20/2001 | 53 |
|  | 3 | 7/21/2003 | 100 |
|  | 4 | 7/22/2003 | 90 |
|  | 5 | 7/24/2003 | 180 |
| Mountain Creek | 2 | 8/24/2001 | 8.3 |
|  | 3 | 6/27/2000 | 27 |
|  | 6 | 9/15/2003 | 60 |
|  | 7 | 9/16/2003 | 80 |
|  | 8 | 7/15/2003 | 289 |
| Lake Hubbard | 1 | 8/30/2001 | 170 |
|  | 2 | 6/16/2003 | 300 |
| CPSES | 1 | 8/3/2003 | 430 |
|  | 2 | 8/3/2003 | 400 |
| MELP | 1 | 7/25/2001 | 216.3 |

A copy of the updated procedure, Transmission & Security Desk V3R51, is available at http://www.ercot.com/AboutERCOT/PublicDisclosure/ERCOTProcedures.htm.